4.25
Annunciators
4.25.1
Enclosure
4.25.1.1
General

Both annunciators ANN-1E and ANN-2E shall be mounted on the door of an indoor free standing NEMA 12 enclosure.  72" H X 36" W X 24" D.  The enclosure shall be the "Hoffman" Cat. #A-723624FS, with a regular 60" X 32" panel, Cat. #A-72P32F1.  The annunciators shall have identical components except for the window nameplates.  The annunciators and all components shall be the standard current products of an approved, reputable manufacturer.  Each annunciator cabinet shall be baked black enamel, #16 gauge steel, flush mounted, NEMA 1 ventilated enclosure accommodating 4 high X 5 across (Totally 20) dual point windows.  Dimensions of each window shall be approximately 3" H X 3 5/16" W.  Dimensions of the cabinet shall be approximately 15 1/2" H X 18 1/2" W.

4.25.1.2
Nameplates

Nameplates shall be snapped onto the lightbox.  The color of the nameplate shall be white, red, or yellow as shown on the "Annunciator Schedule" on the drawing.  Each nameplate shall have two "Alarm Descriptions" for two points as described on the schematic diagram.

4.25.2
Modules
4.25.2.1
General

Each annunciator sequence module shall have a Tri-Flash-First-Out sequence single point module which houses cards, terminals and bus wiring.  The lightbox housing shall be mounted to the front of the module.  Each module shall have an integral "Electronic Output" to activate a common auxiliary relay of its group.  Forty eight modules are required and will be classified into two groups by two external grouping jumpers in the field.  In addition, four modules require an integral auxiliary dry contact output which is a "field-contact follower, no test, Form A type.

4.25.2.2
Ratings

All modules shall be operated with 24VDC input power and 24VDC field contact voltage, consuming approximately 1.3W.  The operating temperature range shall be 32°F to 122°F.  Lamps shall be a 28V nominal, 40 mA #85 subminiature wedge base, (T 1-3/4) bulb.

4.25.2.3
Sequence Card Mounting

The sequence card shall be mounted either in slot A or slot C of each window forming two points per window.

4.25.3
Power Supply

The annunciator shall have an external 450 W power supply mounted on the door of the enclosure.  Input power will be 120VAC, and output power shall be 24VDC.  Power supply module shall have a white power ON indication.

4.25.4
Components
4.25.4.1
Integral Flusher

Annunciator shall have an integral flusher located in the slot D of window 44, one window to the left of the power supply.

4.25.4.2
Three Pushbutton Module

A Three-push-button module, TEST-ACK-FIRST RESET, shall be inserted in the slot D of window #45.

4.25.4.3
Audible Signal Speakers

The audible signal speakers shall be remotely mounted properly on the door of the enclosure.

4.25.4.4
Terminals

The Terminal blocks shall be medium duty, channel mounting, dove tail base terminals for crimp-on-wire lugs, with a plain marking area, 'Agast' CAT. #0511.  Terminals shall be mounted on the channel and shall be arranged on the main panel in the enclosure as shown on the wiring drawings.

4.25.5
Catalog Number Reference

The two annunciator assemblies shall be the 'PANALARM' Series 90 product, requiring the following components:


Component
Catalog Number
Quantity

Cabinet
94CA45
2 Units


Light Box
92LA1WH
16 pcs


Light Box
92LA1YL
20 pcs


Light Box
92LA1YL
4 pcs


Flasher Module
90 FIX
2 pcs


Sequence Module
91TF1T24DC2FTD4EC
68 pcs


Sequence Module
91TFIT24DC2FTD4A4EC
8 pcs


Power Supply
90P2X12OAC24FC450W
1 Unit


Push Button/PWR LTG
90PB33F1P
pcs


Remote Horn
NT2-24D
2 pcs

STD SPEC
4.25 - 2

