5.6
FIELD MOUNTED INSTRUMENTS

Field-mounted instruments shall be located such that indicating instruments are readable from normal standing positions.  Gauges and thermometers which would be otherwise obstructed shall have the required length of capillary to permit placing the indicator in a viewable location or on a local panel, as indicated on the contract drawings. 


Instruments sensing temperature or other conditions at insulated points shall have lagging extensions to permit removal of the sensor without breaking or removing of insulation.


Instruments on local panels shall be identified by instrument number and function.  Nameplates shall be laminated plastic as further described under Section 5.5.6 of these specifications.


All field-mounted instruments, including hand valves and control valves, shall be identified by attaching a stamped, 1-1/2 inch diameter, stainless steel tag to each device with a Monel meter seal.  Tags shall be "Seton Style #250-SNAT", and meter seals shall be "Seton Model MSM-8".  Tag inscriptions shall reflect the designation assigned to each device on the P&ID's.


Connection of any instrument to a vessel, tank, pipe, etc. shall conform to the designated line class specification under Section 3.1.15 of the Piping specifications.


All field-mounted instruments shall be installed according to the manufacturer's instructions and the contract drawings.


All field-mounted instrument support structures shall be hot-dipped galvanized steel unless otherwise indicated on the contract drawings.


All instrumentation taps off of main process pipes shall be insulated in accordance with Section 3.7 of this specification.

STD SPEC
5.6 - 1

