Copyright 2003 and 2005 AIA
MASTERSPEC Full Length
08/03 (R 05/06)

Copyright 2003 and 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 072100 - THERMAL INSULATION
Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following:

Adjust list below to suit Project.  Delete applications, such as cavity wall, that are specified in other Sections.

1. Perimeter insulation under slabs-on-grade.

2. Perimeter wall insulation (supporting backfill).

3. Cavity-wall insulation.

4. Concealed building insulation.

5. Exposed building insulation.

6. Loose-fill building insulation.

7. Self-supported, spray-applied cellulosic insulation.

8. Radiant barriers.

Retain first subparagraph below only if retaining vapor retarders that are separate from vapor-retarder facings on insulation.

9. Vapor retarders.

10. Sound attenuation insulation.

B. Related Sections include the following:

List below only products, construction, and equipment that the reader might expect to find in this Section but are specified elsewhere.

1. Division 04 Section "Unit Masonry" for insulation installed in cavity walls and masonry cells.

2. Division 06 Section "Sheathing" for foam-plastic board sheathing over wood framing.

3. Division 07 Section "[Self-Adhering Sheet Waterproofing] [Elastomeric Sheet Waterproofing] [Thermoplastic Sheet Waterproofing] [Cold Fluid-Applied Waterproofing] [Hot Fluid-Applied Rubberized Asphalt Waterproofing]" for insulation and insulated drainage panels installed with waterproofing.

4. Division 07 Section "[Polymer-Based Exterior Insulation and Finish System (EIFS)] [Water-Drainage Exterior Insulation and Finish System (EIFS)]" for insulation specified as part of these systems.

5. Division 07 Section[s] "[Built-up Asphalt Roofing] [Built-up Coal Tar Roofing] [Ethylene-Propylene-Diene-Monomer (EPDM) Roofing] [Chlorosulfonate-Polyethylene (CSPE) Roofing] [Thermoplastic Membrane Roofing] [Atactic-Polypropylene (APP) Modified Bituminous Membrane Roofing] [Styrene-Butadiene-Styrene (SBS) Modified Bituminous Membrane Roofing] [Self-Adhering Modified Bituminous Membrane Roofing]" [and] ["Coated Foamed Roofing"] for insulation specified as part of roofing construction.

6. Division 07 Section "Fire-Resistive Joint Systems" for insulation installed as part of a perimeter fire-resistive joint system.

7. Division 09 Section[s] ["Gypsum Plastering"] ["Gypsum Veneer Plastering"] ["Portland Cement Plastering"] ["Gypsum Board"] [and] ["Gypsum Board Shaft-Wall Assemblies"] for installation in metal-framed assemblies of insulation specified by referencing this Section.

8. Division 21 Section "Fire-Suppression Systems Insulation."

9. Division 22 Section "Plumbing Insulation."

10. Division 23 Section "HVAC Insulation."

11. Division 33 Section "Subdrainage" for insulated drainage panels.

1.3 DEFINITIONS

A. Mineral-Fiber Insulation:  Insulation composed of rock-wool fibers, slag-wool fibers, or glass fibers; produced in boards and blanket with latter formed into batts (flat-cut lengths) or rolls.

1.4 PERFORMANCE REQUIREMENTS

Delete this Article if no mineral-fiber insulation in ceiling plenums.  If retaining, indicate, on Drawings or in the Insulation Schedule at the end of Part 3, locations where mineral-fiber insulation is installed in ceiling plenums.

A. Plenum Rating:  Provide [glass] [slag-wool-fiber/rock-wool]-fiber insulation where indicated in ceiling plenums whose test performance is rated as follows for use in plenums as determined by testing identical products per "Erosion Test" and "Mold Growth and Humidity Test" described in UL 181, or on comparable tests from another standard acceptable to authorities having jurisdiction.

1. Erosion Test Results:  Insulation shows no visible evidence of cracking, flaking, peeling, or delamination of interior surface of duct assembly, after testing for 4 hours at 2500-fpm (13-m/s) air velocity.

2. Mold Growth and Humidity Test Results:  Insulation shows no evidence of mold growth, delamination, or other deterioration due to the effects of high humidity, after inoculation with Chaetomium globosium on all surfaces and storing for 60 days at 100 percent relative humidity in the dark.

1.5 SUBMITTALS

A. Product Data:  For each type of product indicated.

Delete paragraph below if no exposed insulation or if no Samples are required.

B. Samples for Verification:  Full-size units for each type of exposed insulation indicated.

Retain paragraph and subparagraphs below if recycled content is required for LEED-NC or LEED-CI Credits MR 4.1 and MR 4.2.

C. LEED Submittal:

1. Product Data for Credit MR 4.1[ and MR 4.2]:  For products having recycled content, documentation indicating percentages by weight of postconsumer and preconsumer recycled content.

a. Include statement indicating costs for each product having recycled content.

Delete paragraph below if this Section has been edited to retain only products with well-known unvarying values.

D. Product Test Reports:  Based on evaluation of comprehensive tests performed by a qualified testing agency for insulation products.

Insert specific model code organization in paragraph below or revise if report must be from another source.

E. Research/Evaluation Reports:  For foam-plastic insulation.

1.6 QUALITY ASSURANCE

A. Source Limitations:  Obtain each type of building insulation through one source from a single manufacturer.

B. Fire-Test-Response Characteristics:  Provide insulation and related materials with the fire-test-response characteristics indicated, as determined by testing identical products per test method indicated below by UL or another testing and inspecting agency acceptable to authorities having jurisdiction.  Identify materials with appropriate markings of applicable testing and inspecting agency.

Retain subparagraph below if test results are indicated with other product requirements in Part 2.  Retain only test methods applicable to types of characteristics specified.

1. Surface-Burning Characteristics:  ASTM E 84.

Retain subparagraph below only if products specified in Part 2 are part of a fire-resistance-rated assembly.

2. Fire-Resistance Ratings:  ASTM E 119.

Pass-fail test in subparagraph below is for measuring combustibility and is referenced in codes to determine if elementary products are noncombustible.  Only selected unfaced mineral-fiber insulation and unfaced cellular-glass insulation pass this test.  Delete if not required.  See Evaluations.

3. Combustion Characteristics:  ASTM E 136.

Retain paragraph below to specify recycled content if required for LEED-NC or LEED-CI Credits MR 4.1 and MR 4.2.  An alternative method of complying with Credits MR 4.1 and MR 4.2 requirements is to retain requirement in Division 01 Section "Sustainable Design Requirements" that gives Contractor the option and responsibility for determining how Credits MR 4.1 and MR 4.2 requirements will be met.

C. Recycled Content:  Provide [glass] [and] [slag-wool-fiber/rock-wool]-fiber insulation with recycled content so postconsumer recycled content plus one-half of preconsumer recycled content is not less than <Insert number> percent.

1.7 DELIVERY, STORAGE, AND HANDLING

A. Protect insulation materials from physical damage and from deterioration by moisture, soiling, and other sources.  Store inside and in a dry location.  Comply with manufacturer's written instructions for handling, storing, and protecting during installation.

Delete paragraph and subparagraphs below if no plastic insulation.

B. Protect plastic insulation as follows:

1. Do not expose to sunlight, except to extent necessary for period of installation and concealment.

2. Protect against ignition at all times.  Do not deliver plastic insulating materials to Project site before installation time.

3. Complete installation and concealment of plastic materials as rapidly as possible in each area of construction.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

Edit this Article with other Part 2 articles in which manufacturers and products, or manufacturers only, are named.  See Division 01 Section "Product Requirements" for an explanation of the terms "Available Products," "Products," "Available Manufacturers," and "Manufacturers" and the effect these terms have on "Comparable Product" and "Product Substitution" requirements.

A. In other Part 2 articles where titles below introduce lists, the following requirements apply to product selection:

1. Available Products:  Subject to compliance with requirements, products that may be incorporated into the Work include, but are not limited to, products specified.

2. Products:  Subject to compliance with requirements, provide one of the products specified.

3. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, manufacturers specified.

4. Manufacturers:  Subject to compliance with requirements, provide products by one of the manufacturers specified.

Delete types of insulation not required from articles below that specify insulation.  Coordinate selections with thicknesses indicated on Drawings and with HVAC design and energy program.  Where insulation is exposed or open to air spaces in plenums, cavities, or similar voids, include only products that comply with building codes for fire-test-response characteristics.  Surface-burning indexes indicated for foam-plastic insulation are examples only and generally represent maximums allowed by model building codes for foam-plastic insulation.  Revise to suit products required and code in effect for Project.  See Evaluations.

In articles below specifying insulation products, coordinate subparagraphs that introduce a list of manufacturers or manufacturers and products with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

2.2 FOAM-PLASTIC BOARD INSULATION

A. Extruded-Polystyrene Board Insulation:  ASTM C 578, of type and density indicated below, with maximum flame-spread and smoke-developed indexes of 75 and 450, respectively:

1. [Available ]Manufacturers:

a. DiversiFoam Products.

b. Dow Chemical Company.

c. Owens Corning.

d. Pactiv Building Products Division.

e. <Insert manufacturer's name.>

2. Type IV, 1.60 lb/cu. ft. (26 kg/cu. m), unless otherwise indicated.

If retaining Type IV in subparagraph above along with one or more types in four subparagraphs below, indicate locations of each type on Drawings, by inserts, or in the Insulation Schedule at the end of Part 3.

3. Type X, 1.30 lb/cu. ft. (21 kg/cu. m).

4. Type VI, 1.80 lb/cu. ft. (29 kg/cu. m).

5. Type VII, 2.20 lb/cu. ft. (35 kg/cu. m).

6. Type V, 3.00 lb/cu. ft. (48 kg/cu. m).

First paragraph below describes products intended for below-grade applications.  Verify whether manufacturer's insulation board is suitable for soil pressures to which it will be exposed.  See product list in Evaluations.  Delete if this product is specified in other Sections, such as Division 33 Section "Subdrainage" and Division 07 waterproofing Sections.

B. Extruded-Polystyrene Drainage Panels:  ASTM C 578, of type and density indicated below and fabricated with one side having a matrix of drainage and edge channels.

1. [Available ]Manufacturers:

a. DiversiFoam Products.

b. Dow Chemical Company.

c. Owens Corning.

d. <Insert manufacturer's name.>

2. Type IV, 1.60 lb/cu. ft. (26 kg/cu. m).

Types VI and VII in subparagraphs below are available only from Dow and Owens Corning.

3. Type VI, 1.80 lb/cu. ft. (29 kg/cu. m).

4. Type VII, 2.20 lb/cu. ft. (35 kg/cu. m).

C. Fabric-Faced, Extruded-Polystyrene Drainage Panels:  ASTM C 578, Type VI, with a density of 1.80 lb/cu. ft. (29 kg/cu. m), faced with insulation manufacturer's standard nonwoven filtration fabric and fabricated with 1 side having a matrix of drainage and edge channels.

1. [Available ]Manufacturers:

a. Owens Corning.

b. T. Clear Corporation.

c. <Insert manufacturer's name.>

D. Molded-Polystyrene Board Insulation:  ASTM C 578, of type and density indicated below, with maximum flame-spread and smoke-developed indexes of 75 and 450, respectively:

1. [Available ]Manufacturers:

a. DiversiFoam Products.

b. Manufacturers with a third-party certification program satisfying model building code mandatory requirements for foam plastics.

c. <Insert manufacturer's name.>

Retain one of three subparagraphs below.  If more than one is required, indicate location of each on Drawings or by inserts and add appropriate qualifiers to requirements below; for example, for insulation type predominating, add ", unless otherwise indicated" and for secondary locations, add "where indicated."

2. Type I, 0.90 lb/cu. ft. (15 kg/cu. m).

3. Type VIII, 1.15 lb/cu. ft. (18 kg/cu. m).

4. Type II, 1.35 lb/cu. ft. (22 kg/cu. m).

E. Foil-Faced, Polyisocyanurate Board Insulation:  ASTM C 1289, Type I, Class [1 or 2] [1] [2], with maximum flame-spread and smoke-developed indexes of 75 and 450, respectively, based on tests performed on unfaced core on thicknesses up to 4 inches (101 mm).

1. [Available ]Manufacturers:

a. Atlas Roofing Corporation.

b. Dow Chemical Company.

c. Rmax, Inc.

d. <Insert manufacturer's name.>

2.3 CELLULAR-GLASS INSULATION

A. Manufacturer:  Pittsburgh Corning Corporation.

Type I in paragraph below is available in sizes 12 by 18 inches (305 by 457 mm) and 18 by 24 inches (457 by 610 mm).  Type IV is available in size 24 by 48 inches (610 by 1219 mm).  See Evaluations for available thicknesses.

B. Cellular-Glass Insulation:  ASTM C 552 Type [I (flat block)] [IV (board) faced on both sides with manufacturer's special kraft-paper sheets laminated to glass block with asphalt], with unfaced insulation passing ASTM E 136 for combustion characteristics.

2.4 GLASS-FIBER BOARD INSULATION

A. [Available ]Manufacturers:

1. CertainTeed Corporation.

2. Johns Manville.

3. Knauf Fiber Glass.

4. Owens Corning.

5. <Insert manufacturer's name.>

Flexible glass-fiber board insulation in first two paragraphs below is not significantly different from blanket insulation in batt form but is located in this Article because some manufacturers list it as complying with ASTM standards for insulation in board form.

B. Unfaced, Flexible Glass-Fiber Board Insulation:  ASTM C 612, Type IA; ASTM C 553, Types I, II, and III; or ASTM C 665, Type I; with maximum flame-spread and smoke-developed indexes of 25 and 50, respectively, passing ASTM E 136 for combustion characteristics; and of the following nominal density and thermal resistivity:

1. Nominal density of 1.0 lb/cu. ft. (16 kg/cu. m), thermal resistivity of 3.7 deg F x h x sq. ft./Btu x in. at 75 deg F (25.7 K x m/W at 24 deg C).

Delete subparagraph above or below.  Of manufacturers listed, only Johns Manville offers 1.0-lb/cu. ft. (16-kg/cu. m) density indicated above.

2. Nominal density of not less than 1.5 lb/cu. ft. (24 kg/cu. m) nor more than 1.7 lb/cu. ft. (27 kg/cu. m), thermal resistivity of 4 deg F x h x sq. ft./Btu x in. at 75 deg F (27.7 K x m/W at 24 deg C).

C. Foil-Faced, Flexible Glass-Fiber Board Insulation:  ASTM C 612, Type IA or ASTM C 553, Types I, II, and III; faced on 1 side with foil-scrim-kraft vapor retarder; with maximum flame-spread and smoke-developed indexes of 25 and 50, respectively; and of the following nominal density and thermal resistivity:

1. Nominal density of 1.0 lb/cu. ft. (16 kg/cu. m), thermal resistivity of 3.7 deg F x h x sq. ft./Btu x in. at 75 deg F (25.7 K x m/W at 24 deg C).

Delete subparagraph above or below.  Of manufacturers listed, only Johns Manville offers 1.0-lb/cu. ft. (16-kg/cu. m) density indicated above.

2. Nominal density of not less than 1.5 lb/cu. ft. (24 kg/cu. m) nor more than 1.7 lb/cu. ft. (27 kg/cu. m), thermal resistivity of 4 deg F x h x sq. ft./Btu x in. at 75 deg F (27.7 K x m/W at 24 deg C).

D. Unfaced, Glass-Fiber Board Insulation:  ASTM C 612, Type IA or Types IA and IB; with maximum flame-spread and smoke-developed indexes of 25 and 50, respectively;[ passing ASTM E 136 for combustion characteristics;] and of the following nominal density and thermal resistivity:

Delete densities in four subparagraphs below not required.  If retaining more than one, indicate location of each on Drawings or by inserts.

1. Nominal density of 2.25 lb/cu. ft. (36 kg/cu. m), thermal resistivity of 4.3 deg F x h x sq. ft./Btu x in. at 75 deg F (29.8 K x m/W at 24 deg C).

2. Nominal density of 3 lb/cu. ft. (48 kg/cu. m), thermal resistivity of 4.3 deg F x h x sq. ft./Btu x in. at 75 deg F (29.8 K x m/W at 24 deg C).

3. Nominal density of 4.25 lb/cu. ft. (68 kg/cu. m), thermal resistivity of 4.3 deg F x h x sq. ft./Btu x in. at 75 deg F (29.8 K x m/W at 24 deg C).

4. Nominal density of 6 lb/cu. ft. (96 kg/cu. m), thermal resistivity of 4.4 deg F x h x sq. ft./Btu x in. at 75 deg F (30.5 K x m/W at 24 deg C).

E. Foil-Faced, Glass-Fiber Board Insulation:  ASTM C 612, Type IA or Types IA and IB; faced on 1 side with foil-scrim-kraft or foil-scrim-polyethylene vapor retarder, with maximum flame-spread and smoke-developed indexes of 25 and 50, respectively; and of the following nominal density and thermal resistivity:

Delete densities in two subparagraphs below not required.  If retaining more than one, indicate location of each on Drawings or by inserts.

1. Nominal density of 2.25 lb/cu. ft. (36 kg/cu. m), thermal resistivity of 4.3 deg F x h x sq. ft./Btu x in. at 75 deg F (29.8 K x m/W at 24 deg C).

2. Nominal density of 3 lb/cu. ft. (48 kg/cu. m), thermal resistivity of 4.3 deg F x h x sq. ft./Btu x in. at 75 deg F (29.8 K x m/W at 24 deg C).

Of manufacturers listed, only Knauf offers 4.25-lb/cu. ft. (68-kg/cu. m) density indicated in first subparagraph below.

3. Nominal density of 4.25 lb/cu. ft. (68 kg/cu. m), thermal resistivity of 4.3 deg F x h x sq. ft./Btu x in. at 75 deg F (29.8 K x m/W at 24 deg C).

4. Nominal density of 6 lb/cu. ft. (96 kg/cu. m), thermal resistivity of not less than 4.34 deg F x h x sq. ft./Btu x in. at 75 deg F (30.1 K x m/W at 24 deg C).

Insulation in paragraph and subparagraphs below is intended for installation behind spandrel glass panels, for acoustical applications, and for similar applications where a dark surface is required.  Of manufacturers listed, only CertainTeed and Johns Manville provide board insulation faced with black glass-fiber mat.  Knauf provides board insulation with a black polymer finish.

F. Glass-Mat-Faced, Glass-Fiber Board Insulation:  ASTM C 612, Type IA or Types IA and IB; faced on 1 side with black glass-fiber mat or black polymer finish; maximum flame-spread and smoke-developed indexes of 25 and 50, respectively; and of the following nominal density and thermal resistivity:

Delete densities in four subparagraphs below not required.  If retaining more than one, indicate location of each on Drawings or by inserts.

1. Nominal density of 1.5 lb/cu. ft. (24 kg/cu. m), thermal resistivity of 4.2 deg F x h x sq. ft./Btu x in. at 75 deg F (29.1 K x m/W at 24 deg C).

2. Nominal density of 2.25 lb/cu. ft. (36 kg/cu. m), thermal resistivity of 4.3 deg F x h x sq. ft./Btu x in. at 75 deg F (29.8 K x m/W at 24 deg C).

3. Nominal density of 3 lb/cu. ft. (48 kg/cu. m), thermal resistivity of 4.3 deg F x h x sq. ft./Btu x in. at 75 deg F (29.8 K x m/W at 24 deg C).

4. Nominal density of 6 lb/cu. ft. (96 kg/cu. m), thermal resistivity of 4.5 deg F x h x sq. ft./Btu x in. at 75 deg F (31.2 K x m/W at 24 deg C).

2.5 SLAG-WOOL-FIBER/ROCK-WOOL-FIBER BOARD INSULATION

A. [Available ]Manufacturers:

1. Fibrex Insulations Inc.

2. Owens Corning.

3. Thermafiber.

4. <Insert manufacturer's name.>

B. Unfaced, Slag-Wool-Fiber/Rock-Wool-Fiber Board Insulation:  ASTM C 612, maximum flame-spread and smoke-developed indexes of 15 and 0, respectively; passing ASTM E 136 for combustion characteristics; and of the following nominal density and thermal resistivity:

Delete densities in first three subparagraphs below not required.  If retaining more than one, indicate location of each on Drawings or by inserts.

1. Nominal density of 4 lb/cu. ft. (64 kg/cu. m), Types IA and IB, thermal resistivity of 4 deg F x h x sq. ft./Btu x in. at 75 deg F (27.7 K x m/W at 24 deg C).

2. Nominal density of 6 lb/cu. ft. (96 kg/cu. m), Type II, thermal resistivity of 4.16 deg F x h x sq. ft./Btu x in. at 75 deg F (28.8 K x m/W at 24 deg C).

3. Nominal density of 8 lb/cu. ft. (128 kg/cu. m), Type III, thermal resistivity of 4.35 deg F x h x sq. ft./Btu x in. at 75 deg F (30.2 K x m/W at 24 deg C).

4. Fiber Color:  Regular color, unless otherwise indicated.

Retain subparagraph above for concealed locations.  Retain subparagraph below where dark fiber insulation is required, such as behind glass spandrel panels and for other applications exposed to view.

5. Fiber Color:  Darkened, where indicated.

C. Foil-Faced, Slag-Wool-Fiber/Rock-Wool-Fiber Board Insulation:  ASTM C 612; faced on 1 side with foil-scrim or foil-scrim-polyethylene vapor retarder; with maximum flame-spread and smoke-developed indexes of 25 and 5, respectively; and of the following nominal density and thermal resistivity:

Delete densities in three subparagraphs below not required.  If retaining more than one, indicate location of each on Drawings or by inserts.

1. Nominal density of 4 lb/cu. ft. (64 kg/cu. m), Types IA and IB, thermal resistivity of 4 deg F x h x sq. ft./Btu x in. at 75 deg F (27.7 K x m/W at 24 deg C).

2. Nominal density of 6 lb/cu. ft. (96 kg/cu. m), Type II, thermal resistivity of 4.16 deg F x h x sq. ft./Btu x in. at 75 deg F (28.8 K x m/W at 24 deg C).

3. Nominal density of 8 lb/cu. ft. (128 kg/cu. m), Type III, thermal resistivity of 4.35 deg F x h x sq. ft./Btu x in. at 75 deg F (30.2 K x m/W at 24 deg C).

2.6 GLASS-FIBER BLANKET INSULATION

A. [Available ]Manufacturers:

1. CertainTeed Corporation.

2. Guardian Fiberglass, Inc.

3. Johns Manville.

4. Knauf Fiber Glass.

5. Owens Corning.

6. <Insert manufacturer's name.>

B. Unfaced, Glass-Fiber Blanket Insulation:  ASTM C 665, Type I (blankets without membrane facing); consisting of fibers; with maximum flame-spread and smoke-developed indexes of 25 and 50, respectively; passing ASTM E 136 for combustion characteristics.

Verify availability of polypropylene-scrim kraft and the relative cost of different facings with manufacturers listed.

C. Faced, Glass-Fiber Blanket Insulation:  ASTM C 665, Type III (blankets with reflective membrane facing), Class A (membrane-faced surface with a flame-spread index of 25 or less); Category 1 (membrane is a vapor barrier), faced with[ foil-scrim-kraft, foil-scrim, or foil-scrim-polyethylene] [polypropylene-scrim-kraft] vapor-retarder membrane on 1 face.

Delete paragraph and subparagraphs below if both thicknesses and thermal resistances (not thermal resistivities) are indicated on Drawings.  See Evaluations.

D. Where glass-fiber blanket insulation is indicated by the following thicknesses, provide blankets in batt or roll form with thermal resistances indicated:

1. 3-1/2 inches (89 mm) thick with a thermal resistance of [11 deg F x h x sq. ft./Btu at 75 deg F (1.9 K x sq. m/W at 24 deg C)] [13 deg F x h x sq. ft./Btu at 75 deg F (2.3 K x sq. m/W at 24 deg C)].

2. 3-5/8 inches (92 mm) thick with a thermal resistance of 11 deg F x h x sq. ft./Btu at 75 deg F (1.9 K x sq. m/W at 24 deg C).

3. 5-1/2 inches (140 mm) thick with a thermal resistance of 19 deg F x h x sq. ft./Btu at 75 deg F (3.3 K x sq. m/W at 24 deg C).

4. 6-1/2 inches (165 mm) thick with a thermal resistance of 21 deg F x h x sq. ft./Btu at 75 deg F (3.7 K x sq. m/W at 24 deg C).

5. [9-1/2 inches (241 mm)] [10 inches (254 mm)] [10-1/4 inches (260 mm)] thick with a thermal resistance of 30 deg F x h x sq. ft./Btu at 75 deg F (5.2 K x sq. m/W at 24 deg C).

6. <Insert thickness and thermal resistance.>

2.7 SLAG-WOOL-FIBER/ROCK-WOOL-FIBER BLANKET INSULATION

A. [Available ]Manufacturers:

1. Fibrex Insulations Inc.

2. Owens Corning.

3. Thermafiber.

4. <Insert manufacturer's name.>

B. Unfaced, Slag-Wool-Fiber/Rock-Wool-Fiber Blanket Insulation:  ASTM C 665, Type I (blankets without membrane facing); consisting of fibers; with maximum flame-spread and smoke-developed indexes of 25 and 50, respectively; passing ASTM E 136 for combustion characteristics.

Insert thermal resistances (not thermal resistivities) for thicknesses required and indicated on Drawings if desired.  See Evaluations.

C. Faced, Slag-Wool-Fiber/Rock-Wool-Fiber Blanket Insulation:  ASTM C 665, Type III (blankets with reflective membrane facing), Class A (membrane-faced surface with a flame spread of 25 or less); Category 1 (membrane is a vapor barrier), faced with foil-scrim-kraft, foil-scrim, or foil-scrim-polyethylene vapor-retarder membrane on 1 face.

D. Where slag-wool-fiber/rock-wool-fiber blanket insulation is indicated by the following thicknesses, provide blankets in batt form with thermal resistances indicated:

1. 1-1/2 inches (38 mm) thick with a thermal resistance of 6 deg F x h x sq. ft./Btu at 75 deg F (1 K x sq. m/W at 24 deg C).

2. 3-1/2 inches (89 mm) thick with a thermal resistance of 13 deg F x h x sq. ft./Btu at 75 deg F (2.3 K x sq. m/W at 24 deg C).

3. 4 inches (101 mm) thick with a thermal resistance of 16 deg F x h x sq. ft./Btu at 75 deg F (2.8 K x sq. m/W at 24 deg C).

4. 5-1/4 inches (133 mm) thick with a thermal resistance of 19 deg F x h x sq. ft./Btu at 75 deg F (3.3 K x sq. m/W at 24 deg C).

5. 6 inches (152 mm) thick with a thermal resistance of 22 deg F x h x sq. ft./Btu at 75 deg F (3.9 K x sq. m/W at 24 deg C).

6. <Insert thickness and thermal resistance.>

2.8 LOOSE-FILL INSULATION

A. Cellulosic-Fiber Loose-Fill Insulation:  ASTM C 739, chemically treated for flame-resistance, processing, and handling characteristics.

Retain type in paragraph below to suit application methods required and indicated on Drawings.

B. Glass-Fiber Loose-Fill Insulation:  ASTM C 764, [Type I for pneumatic application] [or] [Type II for poured application]; with maximum flame-spread and smoke-developed indexes of 5.

2.9 SPRAY-APPLIED CELLULOSIC INSULATION

Retain required type(s) in this Article.  If more than one type is required, indicate location of each on Drawings.

A. Self-Supported, Spray-Applied Cellulosic Insulation:  ASTM C 1149, [Type I (materials applied with liquid adhesive; suitable for either exposed or enclosed applications),] [Type II (materials containing a dry adhesive activated by water during installation; intended only for enclosed or covered applications),] [Type III (materials containing an adhesive mixed with water during application; intended for application on attic floors),] chemically treated for flame-resistance, processing, and handling characteristics.

2.10 RADIANT BARRIERS

Radiant barrier in first paragraph below is a proprietary coating available in either a solvent- or water-based formulation.  Barriers in second paragraph are proprietary products consisting of sheets (substrates) faced with aluminum foil or metallic coatings.  If solvent-based coating is selected, verify its acceptability with local air quality-control board.  Specify products by name and description.  Refer to manufacturers' literature for proper use.  See Evaluations.

A. Interior Radiation Control Coating:  ASTM C 1321.  Silver-colored, not thickness-dependent, low-emissivity [solvent] [water]-based coating, formulated for adherence to substrates indicated and with a surface emittance value of 0.25 or less as measured per ASTM C 1371.

1. [Available ]Products:

Products in two subparagraphs below may exceed 0.25 surface emittance value when applied to porous materials such as brick and concrete masonry units.  Verify with manufacturer.

a. SOLEC Corporation; LO/MIT-I.

Product in subparagraph above is solvent based; product in subparagraph below is water based.

b. SOLEC Corporation; LO/MIT-II.

B. Sheet Radiant Barriers:  ASTM C 1313 and as follows:

1. [Available ]Products:

Products in first two subparagraphs below are sheet radiant barriers with foil on both sides of substrate.  If another type is required, insert products below.

a. Innovative Energy, Inc.; R+Heatshield [Commercial Solid] [Perforated].

b. Innovative Insulation, Inc.; Super R [Premium (Commercial)] [Plus (Industrial)].

c. <Insert manufacturer's name; product name or designation.>

2. Sheet Construction:  [Foil on one side of substrate] [Foil on both sides of substrate] [Vacuum metallizing on substrate].

3. Surface-Burning Characteristics:  Maximum flame-spread and smoke-developed indexes of [5 and 10] <Insert indexes>, respectively.

4. Tear Resistance:  <Insert value.>

Retain first option in first subparagraph below if radiant barrier is to serve as vapor retarder; if not, retain second option.

5. Water-Vapor Transmission:  [1 perm, maximum] [5 perms or greater].

6. Sheet Width:  <Insert width.>

2.11 VAPOR RETARDERS

This Article includes vapor retarders applied separately from insulation that includes vapor retarders as facings.  Delete materials not required for applications retained.  No manufacturers and products are listed for polyethylene vapor retarders specified in first paragraph below.

A. Polyethylene Vapor Retarders:  ASTM D 4397, 6 mils (0.15 mm) thick, with maximum permeance rating of 0.13 perm (7.5 ng/Pa x s x sq. m).

B. Reinforced-Polyethylene Vapor Retarders:  2 outer layers of polyethylene film laminated to an inner reinforcing layer consisting of either nylon cord or polyester scrim and weighing not less than 25 lb/1000 sq. ft. (12 kg/100 sq. m), with maximum permeance rating of 0.0507 perm (2.9 ng/Pa x s x sq. m).

1. [Available ]Products:

a. Raven Industries Inc.; DURA-SKRIM 6WW.

b. Reef Industries, Inc.; Griffolyn T-65.

c. <Insert manufacturer's name; product name or designation.>

C. Fire-Retardant, Reinforced-Polyethylene Vapor Retarders:  2 outer layers of polyethylene film laminated to an inner reinforcing layer consisting of either nonwoven grid of nylon cord or polyester scrim and weighing not less than 22 lb/1000 sq. ft. (10 kg/100 sq. m), with maximum permeance rating of 0.1317 perm (7.56 ng/Pa x s x sq. m) and with flame-spread and smoke-developed indexes of not more than 5 and 60, respectively.

1. [Available ]Products:

a. Raven Industries Inc.; DURA-SKRIM 2FR.

b. Reef Industries, Inc.; Griffolyn T-55 FR.

c. <Insert manufacturer's name; product name or designation.>

D. Foil-Polyester-Film Vapor Retarders:  2 layers of 0.5-mil- (0.013-mm-) thick polyester film laminated to an inner layer of 1-mil- (0.025-mm-) thick aluminum foil, with maximum water-vapor transmission rate in flat condition of 0.0 g/h x sq. m and with maximum flame-spread and smoke-developed indexes of 5.

1. Product:  Subject to compliance with requirements, provide "Zero Perm" by Alumiseal Corporation.

E. Vapor-Retarder Tape:  Pressure-sensitive tape of type recommended by vapor-retarder manufacturer for sealing joints and penetrations in vapor retarder.

Retain two paragraphs below if retaining in Part 3 the installation method recommended by Raven Industries for installing vapor retarders over steel studs.

F. Vapor-Retarder Fasteners:  Pancake-head, self-tapping steel drill screws; with fender washers.

G. Single-Component Nonsag Urethane Sealant:  ASTM C 920, Type I, Grade NS, Class 25, Use NT related to exposure, and Use O related to vapor-barrier-related substrates.

Retain paragraph below if retaining Alumiseal's "Zero Perm."

H. Adhesive for Vapor Retarders:  Product recommended by vapor-retarder manufacturer and with demonstrated capability to bond vapor retarders securely to substrates indicated.

2.12 AUXILIARY INSULATING MATERIALS

Delete first paragraph below if not retaining insulation with vapor-retarder facings.

A. Vapor-Retarder Tape:  Pressure-sensitive tape of type recommended by insulation manufacturers for sealing joints and penetrations in vapor-retarder facings.

B. Adhesive for Bonding Insulation:  Product with demonstrated capability to bond insulation securely to substrates indicated without damaging insulation and substrates.

C. Asphalt Coating for Cellular-Glass Block Insulation:  Cutback asphalt or asphalt emulsion of type recommended by manufacturer of cellular-glass block insulation.

D. Eave Ventilation Troughs:  Preformed, rigid fiberboard or plastic sheets designed and sized to fit between roof framing members and to provide cross ventilation between insulated attic spaces and vented eaves.

2.13 INSULATION FASTENERS

Anchor in paragraph below is an example of a mechanical fastener.  Prong anchors, welding pins, pointed rods, etc., are also available; insert here as required.

A. Adhesively Attached, Spindle-Type Anchors:  Plate welded to projecting spindle; capable of holding insulation of thickness indicated securely in position indicated with self-locking washer in place; and complying with the following requirements:

1. [Available ]Products:

a. AGM Industries, Inc.; Series T TACTOO Insul-Hangers.

b. Eckel Industries of Canada; Stic-Klip Type N Fasteners.

c. Gemco; Spindle Type.

d. <Insert manufacturer's name; product name or designation.>

Revise two subparagraphs below if stainless steel or another metal is required.

2. Plate:  Perforated galvanized carbon-steel sheet, 0.030 inch (0.762 mm) thick by 2 inches (50 mm) square.

3. Spindle:  Copper-coated, low carbon steel; fully annealed; 0.105 inch (2.67 mm) in diameter; length to suit depth of insulation indicated.

Anchors in paragraph below are intended for attaching insulation to mullions while preventing it from touching spandrel glass.

B. Adhesively Attached, Angle-Shaped, Spindle-Type Anchors:  Angle welded to projecting spindle; capable of holding insulation of thickness indicated securely in position indicated with self-locking washer in place; and complying with the following requirements:

1. [Available ]Products:

a. Gemco; 90-Degree Insulation Hangers.

b. <Insert manufacturer's name; product name or designation.>

Revise subparagraphs below if stainless steel or another metal is required.

2. Angle:  Formed from 0.030-inch- (0.762-mm-) thick, perforated, galvanized carbon-steel sheet with each leg 2 inches (50 mm) square.

3. Spindle:  Copper-coated, low carbon steel; fully annealed; 0.105 inch (2.67 mm) in diameter; length to suit depth of insulation indicated.

Revise size in first paragraph below if required.

C. Insulation-Retaining Washers:  Self-locking washers formed from 0.016-inch- (0.41-mm-) thick galvanized steel sheet, with beveled edge for increased stiffness, sized as required to hold insulation securely in place, but not less than 1-1/2 inches (38 mm) square or in diameter.

1. [Available ]Products:

a. AGM Industries, Inc.; RC150.

b. AGM Industries, Inc.; SC150.

c. Gemco; Dome-Cap.

d. Gemco; R-150.

e. Gemco; S-150.

f. <Insert manufacturer's name; product name or designation.>

Retain subparagraph and associated subparagraphs below if anchors are used in crawlspaces, ceiling plenums, attic spaces, etc., where sharp ends of spindles would be exposed to human contact.

2. Protect ends with capped self-locking washers incorporating a spring steel insert to ensure permanent retention of cap in the following locations:

a. Crawlspaces.

b. Ceiling plenums.

c. Attic spaces.

d. Where indicated.

e. <Insert location.>

D. Insulation Standoff:  Spacer fabricated from galvanized mild-steel sheet for fitting over spindle of insulation anchor to maintain air space of [1 inch (25 mm)] [2 inches (50 mm)] [3 inches (76 mm)] between face of insulation and substrate to which anchor is attached.

1. [Available ]Products:

a. Gemco; Clutch Clip.

b. <Insert manufacturer's name; product name or designation.>

E. Anchor Adhesive:  Product with demonstrated capability to bond insulation anchors securely to substrates indicated without damaging insulation, fasteners, and substrates.

1. [Available ]Products:

a. AGM Industries, Inc.; TACTOO Adhesive.

b. Eckel Industries of Canada; Stic-Klip Type S Adhesive.

c. Gemco; Tuff Bond Hanger Adhesive.

d. <Insert manufacturer's name; product name or designation.>

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine substrates and conditions, with Installer present, for compliance with requirements of Sections in which substrates and related work are specified and for other conditions affecting performance.

1. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 PREPARATION

A. Clean substrates of substances harmful to insulation or vapor retarders, including removing projections capable of puncturing vapor retarders or of interfering with insulation attachment.

3.3 INSTALLATION, GENERAL

A. Comply with insulation manufacturer's written instructions applicable to products and application indicated.

B. Install insulation that is undamaged, dry, and unsoiled and that has not been left exposed at any time to ice, rain, and snow.

C. Extend insulation in thickness indicated to envelop entire area to be insulated.  Cut and fit tightly around obstructions and fill voids with insulation.  Remove projections that interfere with placement.

D. Water-Piping Coordination:  If water piping is located within insulated exterior walls, coordinate location of piping to ensure that it is placed on warm side of insulation and insulation encapsulates piping.

E. For preformed insulating units, provide sizes to fit applications indicated and selected from manufacturer's standard thicknesses, widths, and lengths.  Apply single layer of insulation units to produce thickness indicated unless multiple layers are otherwise shown or required to make up total thickness.

3.4 INSTALLATION OF [PERIMETER] [AND] [UNDER-SLAB] INSULATION

Delete first paragraph and subparagraph below if support is not required during backfilling.

A. On vertical surfaces, set insulation units in adhesive applied according to manufacturer's written instructions.  Use adhesive recommended by insulation manufacturer.

1. If not otherwise indicated, extend insulation a minimum of 24 inches (610 mm) below exterior grade line.

B. On horizontal surfaces, loosely lay insulation units according to manufacturer's written instructions.  Stagger end joints and tightly abut insulation units.

Usually delete paragraph below unless backfill material is coarse or if even minor insulation damage cannot be tolerated.

C. Protect below-grade insulation on vertical surfaces from damage during backfilling by applying protection course with joints butted.  Set in adhesive according to insulation manufacturer's written instructions.

Usually delete paragraph below unless extensive slab installation work is likely to damage insulation.

D. Protect top surface of horizontal insulation from damage during concrete work by applying protection course with joints butted.

3.5 INSTALLATION OF CAVITY-WALL INSULATION

Delete this Article if masonry insulation is specified in Division 04 Section "Unit Masonry."

A. On units of foam-plastic board insulation, install pads of adhesive spaced approximately 24 inches (610 mm) o.c. both ways on inside face, and as recommended by manufacturer.  Fit courses of insulation between wall ties and other obstructions, with edges butted tightly in both directions.  Press units firmly against inside substrates indicated.

Delete subparagraph below if insulation fills cavity.  Coordinate with Division 04 Section "Unit Masonry" where ties are specified.

1. Supplement adhesive attachment of insulation by securing boards with two-piece wall ties designed for this purpose and specified in Division 04 Section "Unit Masonry."

Delete paragraph and subparagraphs below if no cellular-glass insulation.

B. Install units of cellular-glass insulation with closely fitting joints using method indicated:

1. Gob Method:  Apply 4 gobs of adhesive per unit and set units firmly against inside wythe of masonry or other construction as shown.  Apply gobs at each corner; spread gobs to form pads 4 inches (101 mm) in diameter by 1/4 inch (6 mm) thick.

Method in subparagraph above is suitable for wall applications only.  Method in first subparagraph below is suitable for walls and ceilings, but manufacturer advises using mechanical fasteners on ceilings in high-risk areas.

2. Serrated-Trowel Method:  Apply adhesive to entire surface of each cellular-glass insulation unit with serrated trowel complying with insulation manufacturer's written instructions.

3. Coat edges of insulation units with full bed of adhesive to seal joints between insulation and between insulation and adjoining construction.

Retain subparagraph above if insulation is subjected to severe moisture and freezing-thawing.  Retain subparagraph below for nominal protection where there may be occasional moisture and freezing-thawing.  Coatings also act as barriers against air infiltration.

4. Coat exterior face (cold face) of installed cellular-glass block insulation course with asphalt coating.

3.6 INSTALLATION OF GENERAL BUILDING INSULATION

A. Apply insulation units to substrates by method indicated, complying with manufacturer's written instructions.  If no specific method is indicated, bond units to substrate with adhesive or use mechanical anchorage to provide permanent placement and support of units.

B. Seal joints between foam-plastic insulation units by applying adhesive, mastic, or sealant to edges of each unit to form a tight seal as units are shoved into place.  Fill voids in completed installation with adhesive, mastic, or sealant as recommended by insulation manufacturer.

Specify location of vapor retarder in paragraph below based on vapor-flow analysis of a construction assembly.

C. Set vapor-retarder-faced units with vapor retarder [to warm-in-winter side] [in location indicated] <Insert location> of construction, unless otherwise indicated.

Delete paragraph above and subparagraph below if no units are furnished with vapor-retarder faces.

1. Tape joints and ruptures in vapor retarder, and seal each continuous area of insulation to surrounding construction to ensure airtight installation.

Delete paragraph and subparagraphs below if no mineral-fiber insulation is used in cavities of framing members.

D. Install mineral-fiber insulation in cavities formed by framing members according to the following requirements:

1. Use insulation widths and lengths that fill the cavities formed by framing members.  If more than one length is required to fill cavity, provide lengths that will produce a snug fit between ends.

2. Place insulation in cavities formed by framing members to produce a friction fit between edges of insulation and adjoining framing members.

Delete first subparagraph below if recessed lighting fixtures are rated for contact with insulation.

3. Maintain 3-inch (76-mm) clearance of insulation around recessed lighting fixtures.

4. Install eave ventilation troughs between roof framing members in insulated attic spaces at vented eaves.

Delete subparagraph below if no metal-framed wall construction.

5. For metal-framed wall cavities where cavity heights exceed 96 inches (2438 mm), support unfaced blankets mechanically and support faced blankets by taping flanges of insulation to flanges of metal studs.

Delete subparagraph and associated subparagraphs below if no wood-framed construction.

6. For wood-framed construction, install mineral-fiber blankets according to ASTM C 1320 and as follows:

a. With faced blankets having stapling flanges, secure insulation by inset, stapling flanges to sides of framing members.

Delete subparagraph above or below.  Retain above with adhesive application of gypsum board.  Retain below if mechanical attachment of gypsum board is used.

b. With faced blankets having stapling flanges, lap blanket flange over flange of adjacent blanket to maintain continuity of vapor retarder once finish material is installed over it.

Revise first paragraph and subparagraphs below to indicate type of concrete substrate, such as architectural precast concrete panels or cast-in-place concrete walls.

E. Install board insulation on concrete substrates by adhesively attached, spindle-type insulation anchors as follows:

1. Fasten insulation anchors to concrete substrates with insulation anchor adhesive according to anchor manufacturer's written instructions.  Space anchors according to insulation manufacturer's written instructions for insulation type, thickness, and application indicated.

Show width of cavity on Drawings.

2. Apply insulation standoffs to each spindle to create cavity width indicated between concrete substrate and insulation.

3. After adhesive has dried, install board insulation by pressing insulation into position over spindles and securing it tightly in place with insulation-retaining washers, taking care not to compress insulation below indicated thickness.

4. Where insulation will not be covered by other building materials, apply capped washers to tips of spindles.

F. Install board insulation in curtain-wall construction where indicated on Drawings according to curtain-wall manufacturer's written instructions.

1. Retain insulation in place by metal clips and straps or integral pockets within window frames, spaced at intervals recommended in writing by insulation manufacturer to hold insulation securely in place without touching spandrel glass.  Maintain cavity width of dimension indicated between insulation and glass.

2. Install insulation where it contacts perimeter fire-containment system to prevent insulation from bowing under pressure from perimeter fire-containment system.

Delete paragraph and subparagraph below if no loose-fill insulation.  If retaining only Type I glass-fiber loose-fill insulation in Part 2, retain "by pouring" option in paragraph below.  If retaining only Type II glass-fiber loose-fill insulation, retain "by machine blowing" option.

G. Place loose-fill insulation into spaces indicated, [either] [by pouring] [or] [by machine blowing], to comply with ASTM C 1015.  Level horizontal applications to uniform thickness as indicated, lightly settle to uniform density, but do not compact excessively.

Delete subparagraph below if no cellulosic-fiber loose-fill insulation.

1. For cellulosic-fiber loose-fill insulation, comply with the Cellulose Insulation Manufacturers Association's Special Report #3, "Standard Practice for Installing Cellulose Insulation."

Delete paragraph below if no self-supported, spray-applied cellulosic insulation.

H. Apply self-supported, spray-applied cellulosic insulation according to manufacturer's written instructions.  Do not apply insulation until installation of pipes, ducts, conduits, wiring, and electrical outlets in walls is completed and windows, electrical boxes, and other items not indicated to receive insulation are masked.  After insulation is applied, make it flush with face of studs by using method recommended by insulation manufacturer.

Delete paragraph below if no voids or if not needed for sound deadening, sound absorption, thermal protection, or air-infiltration reduction.

I. Stuff glass-fiber loose-fill insulation into miscellaneous voids and cavity spaces where shown.  Compact to approximately 40 percent of normal maximum volume equaling a density of approximately 2.5 lb/cu. ft. (40 kg/cu. m).

3.7 INSTALLATION OF INSULATION IN CEILINGS FOR SOUND ATTENUATION

A. Install [3-inch- (76-mm-)] <Insert thickness> thick, unfaced [glass] [slag-wool-fiber/rock-wool]-fiber blanket insulation over suspended ceilings at partitions in a width that extends insulation 48 inches (1219 mm) on either side of partition.

Delete paragraph above or below.

B. Install [1-1/2-inch- (38-mm-)] <Insert thickness> thick, unfaced [glass] [slag-wool-fiber/rock-wool]-fiber blanket insulation over suspended ceilings so that insulation extends over entire ceiling.

3.8 INSTALLATION OF RADIANT BARRIERS

A. Install interior radiation control coating system according to ASTM C 1321.

Delete paragraph above or below to coordinate with type of radiant barrier retained in Part 2.

B. Install sheet radiant barriers in locations indicated according to ASTM C 1158.

3.9 INSTALLATION OF VAPOR RETARDERS

A. General:  Extend vapor retarder to extremities of areas to be protected from vapor transmission.  Secure in place with adhesives or other anchorage system as indicated.  Extend vapor retarder to cover miscellaneous voids in insulated substrates, including those filled with loose-fiber insulation.

B. Seal vertical joints in vapor retarders over framing by lapping not less than two wall studs.  Fasten vapor retarders to wood framing at top, end, and bottom edges; at perimeter of wall openings; and at lap joints.  Space fasteners 16 inches (400 mm) o.c.

Paragraph above applies to polyethylene vapor retarders over open framing; delete if not applicable.  Retain first two paragraphs below to specify installation method recommended by Raven Industries for installing vapor retarders over metal framing.

C. Before installing vapor retarder, apply urethane sealant to flanges of metal framing including runner tracks, metal studs, and framing around door and window openings.  Seal overlapping joints in vapor retarders with vapor-retarder tape according to vapor-retarder manufacturer's written instructions.  Seal butt joints with vapor-retarder tape.  Locate all joints over framing members or other solid substrates.

D. Firmly attach vapor retarders to metal framing and solid substrates with vapor-retarder fasteners as recommended by vapor-retarder manufacturer.

E. Seal joints caused by pipes, conduits, electrical boxes, and similar items penetrating vapor retarders with vapor-retarder tape to create an airtight seal between penetrating objects and vapor retarder.

F. Repair tears or punctures in vapor retarders immediately before concealment by other work.  Cover with vapor-retarder tape or another layer of vapor retarder.

3.10 PROTECTION

A. Protect installed insulation[ and vapor retarders] from damage due to harmful weather exposures, physical abuse, and other causes.  Provide temporary coverings or enclosures where insulation is subject to abuse and cannot be concealed and protected by permanent construction immediately after installation.

Insert specific protection requirements here.

3.11 INSULATION SCHEDULE

Retain this Article or, as an alternative, a tabular schedule on Drawings if multiple types of insulation are required for Project and the method of noting which types of insulation are required in specific locations uses numbered insulation types rather than descriptions of insulation products.

A. Insulation Type <Insert number>:  [Type IV] <Insert Type> extruded-polystyrene board insulation.

B. Insulation Type <Insert number>:  [Type VI] <Insert Type> extruded-polystyrene drainage panels.

C. Insulation Type <Insert number>:  Fabric-faced, extruded-polystyrene drainage panels.

D. Insulation Type <Insert number>:  [Type I] <Insert Type> molded-polystyrene board insulation.

E. Insulation Type <Insert number>:  Foil-faced, polyisocyanurate board insulation.

F. Insulation Type <Insert number>:  Cellular-glass insulation.

G. Insulation Type <Insert number>:  Unfaced, flexible glass-fiber board insulation.

H. Insulation Type <Insert number>:  Foil-faced, flexible glass-fiber board insulation.

I. Insulation Type <Insert number>:  Unfaced, glass-fiber board insulation.

J. Insulation Type <Insert number>:  Foil-faced, glass-fiber board insulation.

K. Insulation Type <Insert number>:  Glass-mat-faced, glass-fiber board insulation.

L. Insulation Type <Insert number>:  Unfaced, slag-wool-fiber/rock-wool-fiber board insulation.

M. Insulation Type <Insert number>:  Foil-faced, slag-wool-fiber/rock-wool-fiber board insulation.

N. Insulation Type <Insert number>:  Unfaced, glass-fiber blanket insulation.

O. Insulation Type <Insert number>:  Faced, glass-fiber blanket insulation.

P. Insulation Type <Insert number>:  Unfaced, slag-wool-fiber/rock-wool-fiber blanket insulation.

Q. Insulation Type <Insert number>:  Faced, slag-wool-fiber/rock-wool-fiber blanket insulation.

R. Insulation Type <Insert number>:  Cellulosic-fiber loose-fill insulation.

S. Insulation Type <Insert number>:  Glass-fiber loose-fill insulation.

T. Insulation Type <Insert number>:  Self-supported, spray-applied cellulosic insulation.

END OF SECTION 072100

THERMAL INSULATION
072100 - 1

