Copyright 2011 AIA
MasterSpec Professional
11/11

Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 071413 - HOT FLUID-APPLIED RUBBERIZED ASPHALT WATERPROOFING
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Rubberized-asphalt waterproofing membrane[, unreinforced][, reinforced].

2. Molded-sheet drainage panels.

3. Insulation.

4. Plaza-deck pavers supported on pedestals.

1.2 PREINSTALLATION MEETINGS

Retain "Preinstallation Conference" Paragraph below if Work of this Section is extensive or complex enough to justify a conference.

A. Preinstallation Conference: Conduct conference at [Project site] <Insert location>.

If needed, insert list of conference participants not mentioned in Section 013100 "Project Management and Coordination."

1.3 ACTION SUBMITTALS

A. Product Data: For each type of product.

B. Shop Drawings: Show details for substrate joints and cracks, sheet flashings, penetrations, inside and outside corners, tie-ins to adjoining waterproofing, and other termination conditions.

C. Samples: For plaza-deck pavers[, full sized] in each color and texture required.

1.4 INFORMATIONAL SUBMITTALS

A. Sample Warranties: For special warranties.

1.5 QUALITY ASSURANCE

Retain "Installer Qualifications" Paragraph below if applicable. For warranty purposes, manufacturer may qualify an installer. Coordinate paragraph with qualifications manufacturer requires of Installer.

A. Installer Qualifications: An authorized representative who is trained and approved by manufacturer.

1.6 WARRANTY

When warranties are required, verify with Owner's counsel that warranties stated in this article are not less than remedies available to Owner under prevailing local laws. Example in "Special Warranty" Paragraph below is a labor-and-material warranty. Verify coverage with manufacturers. Manufacturers' warranties customarily do not include costs of excavating and exposing the waterproofing membrane as well as backfilling and restoring affected construction in vertical applications.

A. Special Warranty: Manufacturer agrees to repair or replace waterproofing and sheet flashings that do not comply with requirements or that fail to remain watertight within specified warranty period.

Verify available warranties and warranty periods. Fabric-reinforced, hot fluid-applied waterproofing may qualify for 10-year warranties from some manufacturers.

1. Warranty Period: [Five] [10] <Insert number> years from date of Substantial Completion.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

2.1 WATERPROOFING MEMBRANE

A. Hot Fluid-Applied, Rubberized-Asphalt Waterproofing Membrane: Single component; 100 percent solids; hot fluid-applied, rubberized asphalt.

Retain "Products" Subparagraph and list of manufacturers and products below to require specific products or a comparable product from other manufacturers.

1. Products: Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. American Hydrotech, Inc; [Monolithic Membrane 6125] [Permaquik 6100].

b. Barrett Company; [Ram-Tough 250].

c. Carlisle Coatings & Waterproofing Inc; CCW-500R.

d. Henry Company; [790-11].

e. Tamko Building Products, Inc; [TW-Hot Melt].

f. Tremco Incorporated; [Tremproof 150].

g. <Insert manufacturer's name; product name or designation>.

Insert product physical and performance properties below if required. Manufacturers still report properties according to withdrawn CAN/CGSB-37.50, "Hot Applied, Rubberized Asphalt for Roofing and Waterproofing." See Evaluations for discussion and a listing of these properties.

2.2 AUXILIARY MATERIALS

Revise primer and adhesives in this article to manufacturer-approved, VOC-conforming products when VOC limits apply.

A. Primer: ASTM D 41/D 41M, asphaltic primer.

Retain "Elastomeric Sheet" Paragraph below if used to reinforce joints, cracks, and terminations or for flashings. Revise or insert proprietary materials, such as self-adhering, rubberized asphalt with fabric facer or modified bituminous sheet, if not subject to hydrostatic head or frequent immersion in water.

B. Elastomeric Sheet: 50-mil- (1.3-mm-) minimum, uncured sheet neoprene[ with manufacturer's recommended contact adhesives] as follows:

1. Tensile Strength: 1400 psi (9.6 MPa) minimum; ASTM D 412, Die C.

2. Elongation: 300 percent minimum; ASTM D 412.

3. Tear Resistance: 125 psi (860 kPa) minimum; ASTM D 624, Die C.

4. Brittleness: Does not break at minus 30 deg F (34 deg C); ASTM D 2137.

Retain "Metal Termination Bars" Paragraph below if required by manufacturer to fasten top edge of elastomeric flashing sheet against wall at expansion or moving joints.

C. Metal Termination Bars: Manufacturer's standard, predrilled stainless-steel or aluminum termination bars; approximately 1 by 1/8 inch (25 by 3 mm) thick; with stainless-steel anchors.

D. Sealants and Accessories: Manufacturer's recommended sealants and accessories.

Retain "Reinforcing Fabric" Paragraph below for joint-reinforcing fabric strips and for reinforced waterproofing membrane.

E. Reinforcing Fabric: Manufacturer's recommended, spun-bonded polyester fabric.

Retain one of two "Protection Course" paragraphs below, or revise to insert other protection materials. Distinguish locations, such as plaza-deck and foundation walls, if more than one type of protection course is required.

Asphaltic protection course in first "Protection Course" Paragraph below is manufactured by W. R. Meadows and is also available from several other waterproofing manufacturers.

F. Protection Course: ASTM D 6506, semirigid sheets of fiberglass or mineral-reinforced-asphaltic core, pressure laminated between two asphalt-saturated fibrous liners and as follows:

1. Thickness: [1/8 inch (3 mm)] [1/4 inch (6 mm)], nominal.

2. Thickness: 1/8 inch (3 mm), nominal, for vertical applications; 1/4 inch (6 mm), nominal, elsewhere.

G. Protection Course: Manufacturer's standard, 80- to 90-mil- (2.0- to 2.3-mm-) thick, fiberglass-reinforced rubberized asphalt or modified bituminous sheet.

2.3 MOLDED-SHEET DRAINAGE PANELS

Retain this article if drainage panels are required. Retain "Nonwoven-Geotextile-Faced, Molded-Sheet Drainage Panel" Paragraph below if specifying nonwoven-geotextile-faced drainage panels, usually for foundation walls.

A. Nonwoven-Geotextile-Faced, Molded-Sheet Drainage Panel: Manufactured composite subsurface drainage panels consisting of a nonwoven, needle-punched geotextile facing with an apparent opening size not exceeding No. 70 (0.21-mm) sieve, laminated to one side [with] [or] [without] a polymeric film bonded to the other side of a studded, nonbiodegradable, molded-plastic-sheet drainage core, with a vertical flow rate of 9 to 15 gpm/ft. (112 to 188 L/min. per m).

Retain "Woven-Geotextile-Faced, Molded-Sheet Drainage Panel" Paragraph below if specifying woven-geotextile-faced drainage panels, usually for plaza decks.

B. Woven-Geotextile-Faced, Molded-Sheet Drainage Panel: Manufactured composite subsurface drainage panels consisting of a woven-geotextile facing with an apparent opening size not exceeding No. 40 (0.43-mm) sieve, laminated to one side [with] [or] [without] a polymeric film bonded to the other side of a studded, nonbiodegradable, molded-plastic-sheet drainage core, with a horizontal flow rate not less than 2.8 gpm/ft. (35 L/min. per m).

2.4 INSULATION

Retain "Board Insulation" Paragraph below if board insulation is required over waterproofing and if board insulation forms the first layer beneath an insulation drainage panel. Type IV and Type VI insulation are usually limited to vertical applications. Type VII and Type V insulation, with higher compressive resistances, are used on plaza decks.

A. Board Insulation: Extruded-polystyrene board insulation complying with ASTM C 578, [Type IV, 25-psi (173-kPa)] [Type VI, 40-psi (276-kPa)] [Type VII, 60-psi (414-kPa)] [Type V, 100-psi (690-kPa)] minimum compressive resistance, [square] [or] [shiplap] edged.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. DiversiFoam Products.

b. Dow Chemical Company (The).

c. Owens Corning.

d. Pactiv Corporation.

e. T. Clear Corporation.

f. <Insert manufacturer's name>.

2.5 PLAZA-DECK PAVERS

Retain this article for plaza-deck pavers supported on pedestals.

"Plaza-Deck Pavers" Paragraph below describes concrete pavers commonly used in pedestal-set applications over insulation and waterproofing. Limit pedestal systems to pedestrian plazas. Verify availability of deck pavers with characteristics retained.

A. Plaza-Deck Pavers: Heavyweight, hydraulically pressed, concrete units, [square edged] [with top edges beveled 3/16 inch (5 mm)], manufactured for use as plaza-deck pavers; minimum compressive strength [7500 psi (52 MPa)] [6500 psi (45 MPa)] <Insert value>, ASTM C 140; absorption not greater than 5 percent, ASTM C 140; no breakage and maximum 1 percent mass loss when tested for freeze-thaw resistance according to ASTM C 67.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Hanover Architectural Products.

b. Hastings Pavement Company, LLC.

c. Roofblok Limited.

d. Sunny Brook Pressed Concrete Co.

e. Wausau Tile Inc.

f. Westile Roofing Products.

g. <Insert manufacturer's name>.

Retain one thickness and one face size from options in "Thickness" and "Face Size" subparagraphs below. Include special paver sizes and insert descriptions of custom pavers, such as stair tread and riser units, coping or curbed termination pavers, and oversize pavers.

3. Thickness: [1-5/8 inches (41 mm)] [1-3/4 inches (45 mm)] [2 inches (51 mm)] [2-3/8 inches (60 mm)] <Insert dimension>.

4. Face Size: [8-7/8 inches (225 mm) square] [9 inches (229 mm) square] [9 by 18 inches (229 by 457 mm)] [12 inches (305 mm) square] [12 by 24 inches (305 by 610 mm)] [18 inches (457 mm) square] [24 inches (610 mm) square] [As indicated] <Insert dimensions and shape>.

5. Color: [As indicated by manufacturer's designations] [Match Architect's sample] [As selected by Architect from manufacturer's full range] <Insert color>.

Retain "Paver Supports" Paragraph below if using pedestal systems for paver supports.

B. Paver Supports: Paver manufacturer's standard SBR rubber, high-density polyethylene, or polyurethane paver support assembly, including [fixed-height] [adjustable or stackable] pedestals, shims, and spacer tabs for joint spacing of [1/8 inch (3 mm)] [3/16 inch (5 mm)] [1/8 to 3/16 inch (3 to 5 mm)].

PART 3 -  EXECUTION

3.1 PREPARATION

A. Clean and prepare substrates according to manufacturer's written instructions. Provide clean, dust-free, and dry substrate for waterproofing application.

B. Close off deck drains and other deck penetrations to prevent spillage and migration of waterproofing fluids.

3.2 JOINTS, CRACKS, AND TERMINATIONS

A. Prepare and treat substrates to receive waterproofing membrane, including joints and cracks, deck drains, corners, and penetrations according to manufacturer's written instructions.

Usually retain two subparagraphs below. Retain first for reinforcing strips over moving or large joints and cracks.

1. Adhere strip of elastomeric sheet to substrate in a layer of hot rubberized asphalt. Extend elastomeric sheet a minimum of 6 inches (150 mm) on each side of moving joints and cracks or joints and cracks exceeding 1/8 inch (3 mm) thick, and beyond deck drains and penetrations. Apply second layer of hot fluid-applied, rubberized asphalt over elastomeric sheet.

Retain subparagraph below for reinforcing strips over nonmoving joints and cracks not exceeding 1/8 inch (3 mm) thick.

2. Embed strip of reinforcing fabric into a layer of hot rubberized asphalt. Extend reinforcing fabric a minimum of 6 inches (150 mm) on each side of nonmoving joints and cracks not exceeding 1/8 inch (3 mm) thick, and beyond roof drains and penetrations.

Retain subparagraph below with fabric-reinforced joints for unreinforced waterproofing membrane.

a. Apply second layer of hot fluid-applied, rubberized asphalt over reinforcing fabric.

Revise or delete paragraph below if using expansion-joint gaskets or expansion-joint cover assemblies. Do not use modified bituminous flashing sheets for this condition.

B. At expansion joints and discontinuous deck-to-wall or deck-to-deck joints, bridge joints with elastomeric sheet extended a minimum of 6 inches (150 mm) on each side of joints and adhere to substrates in a layer of hot rubberized asphalt. Apply second layer of hot fluid-applied, rubberized asphalt over elastomeric sheet.

3.3 FLASHING INSTALLATION

A. Install elastomeric sheets at terminations of waterproofing membrane according to manufacturer's written instructions.

3.4 MEMBRANE APPLICATION

A. Apply primer, at manufacturer's recommended rate, over prepared substrate and allow it to dry.

B. Heat and apply rubberized asphalt according to manufacturer's written instructions.

Retain "Unreinforced Membrane" or "Reinforced Membrane" Paragraph below, or both. If retaining both, indicate location of each system on Drawings.

C. Unreinforced Membrane: Apply hot rubberized asphalt to substrates and adjoining surfaces indicated. Spread to form a uniform, unreinforced, seamless membrane, [180-mil (4.5-mm) minimum thickness] [180-mil (4.5-mm) average thickness, but not less than 125 mils (3.2 mm)thick].

D. Reinforced Membrane: Apply hot rubberized asphalt to substrates and adjoining surfaces indicated. Spread to a thickness of 90 mils (2.3 mm); embed reinforcing fabric, overlapping sheets 2 inches (50 mm); spread another 125-mil- (3.2-mm-) thick layer to provide a uniform, reinforced, seamless membrane 215 mils (5.5 mm) thick.

E. Apply waterproofing over prepared joints and up wall terminations and vertical surfaces to heights indicated or required by manufacturer.

Protection course also prevents insulation from sticking to membrane. Retain first option in paragraph below for foundation wall applications and second option for horizontal applications.

F. Cover waterproofing with protection course with overlapped joints before membrane is subject to [backfilling] [construction or vehicular traffic].

3.5 MOLDED-SHEET DRAINAGE PANEL INSTALLATION

A. Place and secure molded-sheet drainage panels, with geotextile facing away from wall or deck substrate according to manufacturer's written instructions. Use methods that do not penetrate waterproofing. Lap edges and ends of geotextile to maintain continuity. Protect installed molded-sheet drainage panels during subsequent construction.

Retain subparagraph below if board insulation or protection course is installed before installing molded-sheet drainage panels.

1. For vertical applications, install [board insulation] [protection course] before installing drainage panels.

3.6 INSULATION INSTALLATION

Retain first paragraph below if support is required during backfilling.

A. On vertical surfaces, set insulation units into rubberized asphalt according to manufacturer's written instructions.

B. On horizontal surfaces, loosely lay insulation units according to manufacturer's written instructions. Stagger end joints and tightly abut insulation units.

3.7 PLAZA-DECK PAVER INSTALLATION

A. Install concrete pavers according to manufacturer's written instructions.

Retain first two paragraphs below if setting pavers on paving pedestals.

B. Accurately install [fixed] [adjustable]-height paver pedestals and accessories to elevations required. Adjust for final level and slope with shims.

C. Loosely lay pavers on pedestals, maintaining a uniform open joint width. Tightly seat pavers against spacers to eliminate lateral movement or drift of paving assembly. Align joint patterns parallel in each direction.

Insert special installation requirements below. Examples might include tread/riser units on tabs or treatment of pavers at plaza/building expansion joints.

D. Install pavers to not vary more than 1/16 inch (1.6 mm) in elevation between adjacent pavers or more than 1/16 inch (1.6 mm) from surface plane elevation of individual paver.

E. Maintain tolerances of paving installation within [1/4 inch in 10 feet (1:48)] <Insert value> of surface plane in any direction.

3.8 CLEANING AND PROTECTION

A. Protect waterproofing from damage and wear during remainder of construction period.

B. Clean spillage and soiling from adjacent construction using cleaning agents and procedures recommended by manufacturer of affected construction.

END OF SECTION 071413
	HOT FLUID-APPLIED RUBBERIZED ASPHALT WATERPROOFING
	071413 - 1



