Copyright 2010 AIA
MasterSpec Professional
11/10

Copyright 2010 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 077200 - ROOF ACCESSORIES
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Roof curbs.

2. Equipment supports.

3. Roof hatches.

4. Hatch-type heat and smoke vents.

5. Dropout-type heat and smoke vents.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of roof accessory indicated.

Retain first paragraph below for Work that involves custom fabrication.

B. Shop Drawings: For roof accessories.

C. Samples: For each exposed product and for each color and texture specified.

1.3 INFORMATIONAL SUBMITTALS

Retain first paragraph below if Drawings do not include detailed plans or if Project involves unusual coordination requirements.

A. Coordination Drawings: Roof plans, drawn to scale, and coordinating penetrations and roof-mounted items.

B. Warranty: Sample of special warranty.

1.4 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

1.5 WARRANTY

Retain paragraph below for factory-coated metal. Delete if metal is field finished or left uncoated. Coordinate with finishes retained in Part 2. Periods of 20 years or longer are for fluoropolymer finishes and are included with manufacturers' published data.

A. Special Warranty on Painted Finishes: Manufacturer's standard form in which manufacturer agrees to repair finishes or replace roof accessories that show evidence of deterioration of factory-applied finishes within [20] [10] <Insert number> years from date of Substantial Completion.

PART 2 -  PRODUCTS

2.1 METAL MATERIALS

A. Zinc-Coated (Galvanized) Steel Sheet: ASTM A 653/A 653M, G90 (Z275) coating designation.

For field painting specified in Section 099113 "Exterior Painting" and Section 099123 "Interior Painting,"retain first or second subparagraph below.

1. Mill-Phosphatized Finish: Manufacturer's standard for field painting.

2. Factory Prime Coating: Where field painting is indicated, apply pretreatment and white or light-colored, factory-applied, baked-on epoxy primer coat, with a minimum dry film thickness of 0.2 mil (0.005 mm).

3. Exposed Coil-Coated Finish: Two-coat fluoropolymer finish; AAMA 621; system consisting of primer and fluoropolymer color topcoat containing not less than 70 percent PVDF resin by weight.

4. Baked-Enamel or Powder-Coat Finish: Manufacturer's standard two-coat, baked-on finish consisting of prime coat and thermosetting topcoat, with a minimum dry film thickness of 1 mil (0.025 mm) for topcoat.

B. Aluminum-Zinc Alloy-Coated Steel Sheet: ASTM A 792/A 792M, AZ50 (AZM150) coated.

Retain one of three subparagraphs below. Retain first subparagraph for field painting specified in Section 099113 "Exterior Painting" and Section 099123 "Interior Painting."

1. Factory Prime Coating: Where field painting is indicated, apply pretreatment and white or light-colored, factory-applied, baked-on epoxy primer coat, with a minimum dry film thickness of 0.2 mil (0.005 mm).

2. Exposed Coil-Coated Finish: Two-coat fluoropolymer finish; AAMA 621; system consisting of primer and fluoropolymer color topcoat containing not less than 70 percent PVDF resin by weight

3. Baked-Enamel or Powder-Coat Finish: Manufacturer's standard two-coat, baked-on finish consisting of prime coat and thermosetting topcoat, with a minimum dry film thickness of 1 mil (0.025 mm) for topcoat.

C. Aluminum Sheet: ASTM B 209 (ASTM B 209M), manufacturer's standard alloy for finish required, with temper to suit forming operations and performance required.

Retain one of six subparagraphs below. Retain second subparagraph for field painting specified in Section 099113 "Exterior Painting" and Section 099123 "Interior Painting."

1. Mill Finish: As manufactured.

2. Factory Prime Coating: Where field painting is indicated, apply pretreatment and white or light-colored, factory-applied, baked-on epoxy primer coat, with a minimum dry film thickness of 0.2 mil (0.005 mm).

Retain one or both of first two subparagraphs below for anodized finish. Class II finish is standard with many manufacturers.

3. Clear Anodic Finish: AAMA 611, Class II, 0.010 mm or thicker.

4. Color Anodic Finish: AAMA 611, Class II, 0.010 mm or thicker.

5. Exposed Coil-Coated Finish: Two-coat fluoropolymer finish; AAMA 620; system consisting of primer and fluoropolymer color topcoat containing not less than 70 percent PVDF resin by weight.

6. Baked-Enamel or Powder-Coat Finish: AAMA 2603 except with a minimum dry film thickness of 1.5 mils (0.04 mm).

D. Aluminum Extrusions and Tubes: ASTM B 221 (ASTM B 221M), manufacturer's standard alloy and temper for type of use, finished to match assembly where used, otherwise mill finished.

E. Stainless-Steel Sheet and Shapes: ASTM A 240/A 240M or ASTM A 666, Type 304.

F. Steel Shapes: ASTM A 36/A 36M, hot-dip galvanized according to ASTM A 123/A 123M unless otherwise indicated.

2.2 MISCELLANEOUS MATERIALS

A. General: Provide materials and types of fasteners, protective coatings, sealants, and other miscellaneous items required by manufacturer for a complete installation.

Retain one or both of first two paragraphs below if acrylic or polycarbonate materials are specified for glazing of hatches or heat and smoke vents.

B. Acrylic Glazing: ASTM D 4802, thermoformable, monolithic sheet, manufacturer's standard, Type UVA (formulated with UV absorber), Finish 1 (smooth or polished).

C. Polycarbonate Glazing: Thermoformable, monolithic polycarbonate sheets manufactured by extrusion process, burglar-resistance rated according to UL 972 with an average impact strength of [12 to 16 ft-lbf/in. (640 to 854 J/m)] <Insert value> of width when tested according to ASTM D 256, Method A (Izod).

D. Wood Nailers: Softwood lumber, pressure treated with waterborne preservatives for aboveground use, acceptable to authorities having jurisdiction, containing no arsenic or chromium, and complying with AWPA C2; not less than 1-1/2 inches (38 mm) thick.

Retain first paragraph below if required to prevent entry through the openings; revise to suit Project.

E. Security Grilles: [3/4-inch (19-mm)] <Insert dimension> diameter, ASTM A 1011/A 1011M steel bars spaced [6 inches (150 mm)] <Insert dimension> o.c. in one direction and [12 inches (300 mm)] <Insert dimension> o.c. in the other; factory finished with manufacturer's or fabricator's standard, universal shop primer compatible with substrate and field-applied finish paint system indicated.

F. Fasteners: Roof accessory manufacturer's recommended fasteners suitable for application and metals being fastened. Match finish of exposed fasteners with finish of material being fastened. Provide nonremovable fastener heads to exterior exposed fasteners.

G. Sealants: As recommended by roof accessory manufacturer for installation indicated.

2.3 ROOF CURBS

A. Roof Curbs: Internally reinforced roof-curb units[ with integral spring-type vibration isolators and] capable of supporting superimposed live and dead loads, including equipment loads and other construction indicated on Drawings; with welded or mechanically fastened and sealed corner joints,[ integral metal cant,] [ stepped integral metal cant raised the thickness of roof insulation,] and integrally formed deck-mounting flange at perimeter bottom.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of two subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. AES Industries, Inc.

b. Curbs Plus, Inc.

c. Custom Solution Roof and Metal Products.

d. Greenheck Fan Corporation.

e. LM Curbs.

f. Metallic Products Corp.

g. Milcor Inc.; Commercial Products Group of Hart & Cooley, Inc.

h. Pate Company (The).

i. Roof Products, Inc.

j. Safe Air of Illinois.

k. Thybar Corporation.

l. Vent Products Co., Inc.

m. <Insert manufacturer's name>.

Retain one of first three paragraphs below.

B. Material: [Zinc-coated (galvanized)] [Aluminum-zinc alloy-coated] steel sheet, [0.052 inch (1.32 mm)] [0.079 inch (2.01 mm)] <Insert dimension> thick.

First option in first subparagraph below applies only to zinc-coated (galvanized) steel sheet.

1. Finish: [Mill phosphatized] [Factory prime coating] [Two-coat fluoropolymer] [Baked enamel or powder coat] <Insert finish>.

Retain subparagraph below if retaining either of last two options in subparagraph above.

2. Color: [As indicated by manufacturer's designations] [Match Architect's sample] [As selected by Architect from manufacturer's full range] <Insert color>.

C. Material: Aluminum sheet, [0.090 inch (2.28 mm)] <Insert dimension> thick.

1. Finish: [Mill] [Factory prime coating] [Clear anodic] [Color anodic] [Two-coat fluoropolymer] [Baked enamel or powder coat] <Insert finish>.

Retain subparagraph below if retaining any of last three options in subparagraph above.

2. Color: [As indicated by manufacturer's designations] [Match Architect's sample] [As selected by Architect from manufacturer's full range] [Light bronze] [Medium bronze] [Dark bronze] <Insert color>.

D. Material: Stainless-steel sheet, [0.078 inch (1.98 mm)] <Insert dimension> thick.

1. Finish: [Manufacturer's standard] [No. 2D, directional polish finish] <Insert finish>.

E. Construction:

Retain first subparagraph below if required.

1. Insulation: Factory insulated with [1-1/2-inch- (38-mm-)] <Insert dimension> thick [cellulosic] [glass]-fiber board insulation.

Retain first subparagraph below if interior metal liner is required.

2. Liner: Same material as curb, of manufacturer's standard thickness and finish.

3. Factory-installed wood nailer at top of curb, continuous around curb perimeter.

4. On ribbed or fluted metal roofs, form deck-mounting flange at perimeter bottom to conform to roof profile.

5. Fabricate curbs to minimum height of [12 inches (300 mm)] <Insert dimension> unless otherwise indicated.

6. Top Surface: Level around perimeter with roof slope accommodated by sloping the deck-mounting flange.

7. Sloping Roofs: Where roof slope exceeds 1:48, fabricate curb with perimeter curb height tapered to accommodate roof slope so that top surface of perimeter curb is level. Equip unit with water diverter or cricket on side that obstructs water flow.

Retain subparagraph below if required.

8. Security Grille: Provide where indicated.

2.4 EQUIPMENT SUPPORTS

A. Equipment Supports: Internally reinforced metal equipment supports capable of supporting superimposed live and dead loads, including equipment loads and other construction indicated on Drawings; with welded or mechanically fastened and sealed corner joints,[ integral metal cant,] [ stepped integral metal cant raised the thickness of roof insulation,] and integrally formed deck-mounting flange at perimeter bottom.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of two subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. AES Industries, Inc.

b. Curbs Plus, Inc.

c. Custom Solution Roof and Metal Products.

d. Greenheck Fan Corporation.

e. LM Curbs.

f. Milcor Inc.; Commercial Products Group of Hart & Cooley, Inc.

g. Pate Company (The).

h. Roof Products, Inc.

i. Thybar Corporation.

j. Vent Products Co., Inc.

k. <Insert manufacturer's name>.

Retain one of first three paragraphs below.

B. Material: [Zinc-coated (galvanized)] [Aluminum-zinc alloy-coated] steel sheet, [0.052 inch (1.32 mm)] [0.079 inch (2.01 mm)] <Insert dimension> thick.

First option in first subparagraph below applies only to zinc-coated (galvanized) steel sheet.

1. Finish: [Mill phosphatized] [Factory prime coating] [Two-coat fluoropolymer] [Baked enamel or powder coat] <Insert finish>.

Retain subparagraph below if retaining either of last two options in subparagraph above.

2. Color: [As indicated by manufacturer's designations] [Match Architect's sample] [As selected by Architect from manufacturer's full range] <Insert color>.

C. Material: Aluminum sheet, [0.090 inch (2.28 mm)] <Insert dimension> thick.

1. Finish: [Mill] [Factory prime coating] [Clear anodic] [Color anodic] [Two-coat fluoropolymer] [Baked enamel or powder coat] <Insert finish>.

Retain subparagraph below if retaining any of last three options in subparagraph above.

2. Color: [As indicated by manufacturer's designations] [Match Architect's sample] [As selected by Architect from manufacturer's full range] [Light bronze] [Medium bronze] [Dark bronze] <Insert color>.

D. Material: Stainless-steel sheet, [0.078 inch (1.98 mm)] <Insert dimension> thick.

1. Finish: [Manufacturer's standard] [No. 2D, directional polish finish] <Insert finish>.

E. Construction:

Retain first subparagraph below if required.

1. Insulation: Factory insulated with [1-1/2-inch- (38-mm-)] <Insert dimension> thick [cellulosic] [glass]-fiber board insulation.

Retain first subparagraph below if interior metal liner is required.

2. Liner: Same material as equipment support, of manufacturer's standard thickness and finish.

3. Factory-installed continuous wood nailers [3-1/2 inches (90 mm)] [5-1/2 inches (140 mm)] <Insert dimension> wide at tops of equipment supports.

4. Metal Counterflashing: Manufacturer's standard, removable, fabricated of same metal and finish as equipment support.

5. On ribbed or fluted metal roofs, form deck-mounting flange at perimeter bottom to conform to roof profile.

Equipment-support height in first subparagraph below may be determined by adding thickness of roof insulation to the minimum base flashing height recommended by roofing membrane manufacturer or established by office practice.

6. Fabricate equipment supports to minimum height of [12 inches (300 mm)] <Insert dimension> unless otherwise indicated.

7. Sloping Roofs: Where roof slope exceeds 1:48, fabricate each support with height to accommodate roof slope so that tops of supports are level with each other. Equip supports with water diverters or crickets on sides that obstruct water flow.

Retain subparagraph below if required.

8. Security Grille: Provide where indicated.

2.5 ROOF HATCH

A. Roof Hatches: Metal roof-hatch units with lids and insulated [single] [double]-walled curbs, welded or mechanically fastened and sealed corner joints, continuous lid-to-curb counterflashing and weathertight perimeter gasketing,[ integral metal cant,] [ stepped integral metal cant raised the thickness of roof insulation,] and integrally formed deck-mounting flange at perimeter bottom.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of two subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. AES Industries, Inc.

b. Babcock-Davis.

c. Bilco Company (The).

d. Bristolite Skylights.

e. Custom Solution Roof and Metal Products.

f. Dur-Red Products.

g. Hi Pro International, Inc.

h. J. L. Industries, Inc.

i. Metallic Products Corp.

j. Milcor Inc.; Commercial Products Group of Hart & Cooley, Inc.

k. Naturalite Skylight Systems; Vistawall Group (The).

l. Nystrom.

m. O'Keeffe's Inc.

n. Pate Company (The).

o. Precision Ladders, LLC.

p. <Insert manufacturer's name>.

Retain one of first two paragraphs below if type and size are not indicated on Drawings; for more than one type or size, indicate locations on Drawings or by inserts.

B. Type and Size: Single-leaf lid, [30 by 36 inches (750 by 900 mm)] [30 by 54 inches (750 by 1370 mm)] [30 by 96 inches (750 by 2440 mm)] <Insert dimensions>.

C. Type and Size: Double-leaf lid, [72 by 96 inches (1830 by 2440 mm)] <Insert dimensions>.

D. Loads: Minimum [40-lbf/sq. ft. (1.9-kPa)] <Insert value> external live load and [20-lbf/sq. ft. (0.95-kPa)] <Insert value> internal uplift load.

Retain subparagraph below if hatch lid is glazed.

1. Dome Glazing: Minimum [40-lbf/sq. ft. (1.9-kPa)] <Insert value> external live load and [20-lbf/sq. ft. (0.95-kPa)] <Insert value> internal uplift load.

Retain one of first three paragraphs below.

E. Hatch Material: [Zinc-coated (galvanized)] [Aluminum-zinc alloy-coated] steel sheet, [0.079 inch (2.01 mm)] <Insert dimension> thick.

First option in first subparagraph below applies only to zinc-coated (galvanized) steel sheet.

1. Finish: [Mill phosphatized] [Factory prime coating] [Two-coat fluoropolymer] [Baked enamel or powder coat] <Insert finish>.

Retain subparagraph below if retaining either of last two options in subparagraph above.

2. Color: [As indicated by manufacturer's designations] [Match Architect's sample] [As selected by Architect from manufacturer's full range] <Insert color>.

F. Hatch Material: Aluminum sheet, [0.090 inch (2.28 mm)] <Insert dimension> thick.

1. Finish: [Mill] [Factory prime coating] [Clear anodic] [Color anodic] [Two-coat fluoropolymer] [Baked enamel or powder coat] <Insert finish>.

Retain subparagraph below if retaining any of last three options in subparagraph above.

2. Color: [As indicated by manufacturer's designations] [Match Architect's sample] [As selected by Architect from manufacturer's full range] [Light bronze] [Medium bronze] [Dark bronze] <Insert color>.

G. Hatch Material: Stainless-steel sheet, [0.078 inch (1.98 mm)] <Insert dimension> thick.

1. Finish: [Manufacturer's standard] [No. 2D, directional polish finish] <Insert finish>.

H. Construction:

Retain one option in first subparagraph below. Insulation is exposed to exterior in roof hatches with single-walled curbs.

1. Insulation: [Cellulosic-fiber] [Glass-fiber] [Polyisocyanurate] board.

Retain one of first two subparagraphs below; first is more common.

2. Hatch Lid: Opaque, insulated, and double walled, with manufacturer's standard metal liner of same material and finish as outer metal lid.

3. Hatch Lid: Glazed, insulated, and double walled, with manufacturer's standard metal liner of same material and finish as outer metal lid.

Retain first subparagraph below if requiring a double-walled curb.

4. Curb Liner: Manufacturer's standard, of same material and finish as metal curb.

5. On ribbed or fluted metal roofs, form flange at perimeter bottom to conform to roof profile.

6. Fabricate curbs to minimum height of [12 inches (300 mm)] <Insert dimension> unless otherwise indicated.

7. Sloping Roofs: Where slope or roof deck exceeds 1:48, fabricate curb with perimeter curb height that is [constant] [tapered to accommodate roof slope so that top surfaces of perimeter curb are level]. Equip hatch with water diverter or cricket on side that obstructs water flow.

Retain first paragraph below if hatch lid is glazed.

I. Hatch-Lid Glazing: [Single] [Double] glazing of thickness capable of resisting indicated loads.

1. Single-Dome Color: [Colorless, transparent] [White, translucent] [Gray tinted, transparent] [Bronze tinted, transparent] <Insert requirement>.

Retain subparagraph above or both subparagraphs below.

2. Outer Double-Dome Color: [Colorless, transparent] [White, translucent] [Gray tinted, transparent] [Bronze tinted, transparent] <Insert requirement>.

3. Inner Double-Dome Color: [Colorless, transparent] [White, translucent] [Gray tinted, transparent] [Bronze tinted, transparent] <Insert requirement>.

Galvanized-steel hardware in first paragraph below is standard.

J. Hardware: Galvanized-steel spring latch with turn handles, butt- or pintle-type hinge system, and padlock hasps inside and outside.

1. Provide two-point latch on lids larger than 84 inches (2130 mm).

2. Provide remote-control operation.

Retain one or both paragraphs below; revise to suit Project.

K. Safety Railing System: Roof-hatch manufacturer's standard system including rails, clamps, fasteners, safety barrier at railing opening, and accessories required for a complete installation; attached to roof hatch and complying with 29 CFR 1910.23 requirements and authorities having jurisdiction.

L. Ladder-Assist Post: Roof-hatch manufacturer's standard device for attachment to roof-access ladder. Post locks in place on full extension; release mechanism returns post to closed position.

2.6 HEAT AND SMOKE VENTS

A. Hatch-Type Heat and Smoke Vents: Manufacturer's standard, with [single] [double]-walled insulated curbs, welded or mechanically fastened and sealed corner joints, integral condensation gutter, and cap flashing. Fabricate with insulated double-walled lid and continuous weathertight perimeter lid gaskets, and equip with automatic self-lifting mechanisms and UL-listed [fusible links rated at 165 deg F (74 deg C)] [fire-suppression system] [smoke-detection system].

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Babcock-Davis.

b. Bilco Company (The).

c. Bristolite Skylights.

d. Dur-Red Products.

e. Hi Pro International, Inc.

f. J. L. Industries, Inc.

g. Milcor Inc.; Commercial Products Group of Hart & Cooley, Inc.

h. Naturalite Skylight Systems; Vistawall Group (The).

i. Nystrom.

j. O'Keeffe's Inc.

k. Pate Company (The).

l. Western Canwell.

m. <Insert manufacturer's name>.

Retain one of first two subparagraphs below if type and size are not indicated on Drawings; for more than one type or size, indicate locations on Drawings or by inserts.

3. Type and Size: Single-leaf lid, [30 by 36 inches (750 by 900 mm)] [30 by 54 inches (750 by 1370 mm)] [30 by 96 inches (750 by 2440 mm)] <Insert dimensions>.

4. Type and Size: Double-leaf lid, [72 by 96 inches (1830 by 2440 mm)] <Insert dimensions>.

5. Loads: Minimum [40-lbf/sq. ft. (1.9-kPa)] <Insert value> external live load and [30-lbf/sq. ft. (1.4-kPa)] <Insert value> internal uplift load.

Retain first subparagraph below if required. The industry offers UL approval with values in option. If roof-load criteria are greater, verify that increased load values will maintain UL approval.

a. When release is actuated, lid shall open against [10-lbf/sq. ft. (0.5-kPa)] <Insert value> snow or wind load and lock in position.

Retain first subparagraph below if hatch lid is glazed.

b. Hatch-Lid Glazing: Minimum [40-lbf/sq. ft. (1.9-kPa)] <Insert value> external live load and [20-lbf/sq. ft. (0.95-kPa)] <Insert value> internal uplift load.

Revise one or more options in first subparagraph below if required by authorities having jurisdiction or for insurance purposes. Compliance with UL 793 is requirement of IBC.

6. Heat and Smoke Vent Standard: Provide units that have been tested and [listed to comply with UL 793] [and] [are FM Approved].

Retain one of three "Curb, Framing, and Lid Material" subparagraphs below.

7. Curb, Framing, and Lid Material: [Zinc-coated (galvanized)] [Aluminum-zinc alloy-coated] steel sheet, [0.079 inch (2.01 mm)] <Insert dimension> thick.

First option in first subparagraph below applies only to zinc-coated (galvanized) steel sheet.

a. Finish: [Mill phosphatized] [Factory prime coating] [Two-coat fluoropolymer] [Baked enamel or powder coat] <Insert finish>.

Retain first subparagraph below if retaining either of last two options in last subparagraph above.

b. Color: [As indicated by manufacturer's designations] [Match Architect's sample] [As selected by Architect from manufacturer's full range] <Insert color>.

8. Curb, Framing, and Lid Material: Aluminum sheet, [0.090 inch (2.28 mm)] <Insert dimension> thick.

a. Finish: [Mill] [Factory prime coating] [Clear anodic] [Color anodic] [Two-coat fluoropolymer] [Baked enamel or powder coat] <Insert finish>.

Retain first subparagraph below if retaining any of last three options in last subparagraph above.

b. Color: [As indicated by manufacturer's designations] [Match Architect's sample] [As selected by Architect from manufacturer's full range] [Light bronze] [Medium bronze] [Dark bronze] <Insert color>.

9. Curb, Framing, and Lid Material: Stainless-steel sheet, [0.078 inch (1.98 mm)] <Insert dimension> thick.

a. Finish: [Manufacturer's standard] [No. 2D, directional polish finish] <Insert finish>.

10. Construction:

Retain one option in first subparagraph below. Insulation is exposed to exterior in smoke and heat vents with single-walled curbs.

a. Insulation: [Cellulosic-fiber] [Glass-fiber] [Polyisocyanurate] board.

Retain one of first two subparagraphs below; first is more common.

b. Hatch Lid: Opaque, insulated, and double walled, with manufacturer's standard metal liner of same material and finish as outer metal lid.

c. Hatch Lid: Glazed, insulated, and double walled, with manufacturer's standard metal liner of same material and finish as outer metal lid.

Retain first subparagraph below if requiring a double-walled curb.

d. Exterior Curb Liner: Manufacturer's standard, of same material and finish as metal curb.

e. Fabricate curbs to minimum height of [12 inches (300 mm)] <Insert dimension> unless otherwise indicated.

f. Sloping Roofs: Where slope or roof deck exceeds 1:48, fabricate curb with perimeter curb height that is [constant] [tapered to accommodate roof slope so that top surfaces of perimeter curb are level]. Equip hatch with water diverter or cricket on side that obstructs water flow.

Retain first subparagraph below if required.

g. Security Grille: Provide where indicated.

Retain first subparagraph below if hatch lid is glazed.

11. Hatch-Lid Glazing: [Single] [Double] glazing of thickness capable of resisting indicated loads; [colorless, transparent] [white, translucent] <Insert color requirement>.

12. Hardware: Manufacturer's standard, corrosion resistant or hot-dip galvanized; with hinges, hold-open devices, and independent manual-release devices for [inside] [and] [outside] operation of lids.

B. Dropout-Type Heat and Smoke Vents: Manufacturer's standard, gravity operated and automatic; with [single] [double]-walled insulated curbs and frame, welded or mechanically fastened and sealed corner joints, integral condensation gutter, cap flashing, and heat-sensitive dome glazing that will deform and drop out of vent opening according to heat and smoke vent standard indicated.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Construction Specialties, Inc.

b. Naturalite Skylight Systems; Vistawall Group (The).

c. Pate Company (The).

d. Plasteco, Inc.

e. <Insert manufacturer's name>.

3. Loads: Minimum [40-lbf/sq. ft. (1.9-kPa)] <Insert value> external live load and [30-lbf/sq. ft. (1.4-kPa)] <Insert value> internal uplift load.

a. Dome Glazing: Minimum [40-lbf/sq. ft. (1.9-kPa)] <Insert value> external live load and [20-lbf/sq. ft. (0.95-kPa)] <Insert value> internal uplift load.

Revise one or more options in first subparagraph below if required by authorities having jurisdiction or for insurance purposes. Compliance with UL 793 is requirement of the IBC.

4. Heat and Smoke Vent Standard: Provide units that have been tested and [listed to comply with UL 793] [and] [are FM Approved].

Retain one of three "Curb and Framing Material" subparagraphs below.

5. Curb and Framing Material: [Zinc-coated (galvanized)] [Aluminum-zinc alloy-coated] steel sheet, [0.079 inch (2.01 mm)] <Insert dimension> thick.

First option in first subparagraph below applies only to zinc-coated (galvanized) steel sheet.

a. Finish: [Mill phosphatized] [Factory prime coating] [Two-coat fluoropolymer] [Baked enamel or powder coat] <Insert finish>.

Retain first subparagraph below if retaining either of last two options in last subparagraph above.

b. Color: [As indicated by manufacturer's designations] [Match Architect's sample] [As selected by Architect from manufacturer's full range] <Insert color>.

6. Curb and Framing Material: Aluminum sheet, [0.090 inch (2.28 mm)] <Insert dimension> thick.

a. Finish: [Mill] [Factory prime coating] [Clear anodic] [Color anodic] [Two-coat fluoropolymer] [Baked enamel or powder coat] <Insert finish>.

Retain first subparagraph below if retaining any of last three options in last subparagraph above.

b. Color: [As indicated by manufacturer's designations] [Match Architect's sample] [As selected by Architect from manufacturer's full range] [Light bronze] [Medium bronze] [Dark bronze] <Insert color>.

7. Curb and Framing Material: Stainless-steel sheet, [0.078 inch (1.98 mm)] <Insert dimension> thick.

a. Finish: [Manufacturer's standard] [No. 2D, directional polish finish] <Insert finish>.

8. Construction:

Retain one option in first subparagraph below. Insulation is exposed to exterior in smoke and heat vents with single-walled curbs.

a. Insulation: [Cellulosic-fiber] [Glass-fiber] [Polyisocyanurate] board.

Retain first subparagraph below if requiring a double-walled curb.

b. Exterior Curb Liner: Manufacturer's standard, of same material and finish as metal curb.

c. Fabricate curbs to minimum height of [12 inches (300 mm)] <Insert dimension> unless otherwise indicated.

d. Sloping Roofs: Where slope of roof deck exceeds 1:48, fabricate curb with perimeter curb height that is [constant] [tapered to accommodate roof slope so that top surfaces of perimeter curb are level]. Equip unit with water diverter or cricket on side that obstructs water flow.

9. Dome Glazing: [Single] [Double] [acrylic] [polycarbonate] glazing of thickness capable of resisting indicated loads.

a. Single-Dome Color: [Colorless, transparent] [White, translucent] [Gray tinted, transparent] [Bronze tinted, transparent] <Insert requirement>.

Retain last subparagraph above or first two subparagraphs below.

b. Outer Double-Dome Color: [Colorless, transparent] [White, translucent] [Gray tinted, transparent] [Bronze tinted, transparent] <Insert requirement>.

c. Inner Double-Dome Color: [Colorless, transparent] [White, translucent] [Gray tinted, transparent] [Bronze tinted, transparent] <Insert requirement>.

10. Hardware: Manufacturer's standard, corrosion resistant or hot-dip galvanized; with hinges, hold-open devices, and independent manual-release devices for [inside] [and] [outside] operation of lids.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. General: Verify dimensions of roof openings for roof accessories. Install roof accessories according to manufacturer's written instructions.

1. Install roof accessories level, plumb, true to line and elevation, and without warping, jogs in alignment, excessive oil canning, buckling, or tool marks.

2. Anchor roof accessories securely in place so they are capable of resisting indicated loads.

3. Use fasteners, separators, sealants, and other miscellaneous items as required to complete installation of roof accessories and fit them to substrates.

4. Install roof accessories to resist exposure to weather without failing, rattling, leaking, or loosening of fasteners and seals.

B. Metal Protection: Protect metals against galvanic action by separating dissimilar metals from contact with each other or with corrosive substrates by painting contact surfaces with bituminous coating or by other permanent separation as recommended by manufacturer.

1. Coat concealed side of [uncoated aluminum] [stainless-steel] roof accessories with bituminous coating where in contact with wood, ferrous metal, or cementitious construction.

2. Underlayment: Where installing roof accessories directly on cementitious or wood substrates, install a course of felt underlayment and cover with a slip sheet, or install a course of polyethylene sheet.

Retain first paragraph below for field-installed security grilles. Retain option if ends of bars cannot be welded to structural frame or curb walls.

C. Security Grilles: Weld bar intersections and[, using tamper-resistant bolts, attach the] ends of bars to structural frame or primary curb walls.

D. Seal joints with sealant as required by roof accessory manufacturer.

3.2 REPAIR AND CLEANING

A. Galvanized Surfaces: Clean field welds, bolted connections, and abraded areas and repair galvanizing according to ASTM A 780.

B. Touch up factory-primed surfaces with compatible primer ready for field painting according to Section 099113 "Exterior Painting" and Section 099123 "Interior Painting."

C. Replace roof accessories that have been damaged or that cannot be successfully repaired by finish touchup or similar minor repair procedures.

END OF SECTION 077200

	ROOF ACCESSORIES
	077200 - 1



