Copyright 2011 AIA
MasterSpec Professional
02/11

Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 078123 - INTUMESCENT FIREPROOFING
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section includes mastic and intumescent fire-resistive coatings (MIFRC).

B. Related Requirements:

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

1. Section 078100 "Applied Fireproofing" for sprayed fire-resistive materials (SFRM).

2. Section 099646 "Intumescent Painting" for intumescent paints that are fire retarding, but not fire resistive.

1.2 PREINSTALLATION MEETINGS

A. Preinstallation Conference: Conduct conference at [Project site] <Insert location>.

1.3 ACTION SUBMITTALS

A. Product Data: For each type of product.

B. LEED Submittals:

"Product Data for Credit EQ 4.2" Subparagraph below applies to LEED-NC, LEED-CI, and LEED-CS. Coordinate with requirements for paints and coatings.

1. Product Data for Credit EQ 4.2: For paints and coatings, documentation including printed statement of VOC content.

"Laboratory Test Reports for Credit EQ 4" Subparagraph below applies to LEED for Schools.

2. Laboratory Test Reports for Credit EQ 4: For paints and coatings, documentation indicating that products comply with the testing and product requirements of the California Department of Health Services' "Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers."

C. Samples: For each exposed product and for each color and texture specified.

1.4 INFORMATIONAL SUBMITTALS

A. Product certificates.

B. Evaluation reports.

C. Field quality-control reports.

1.5 QUALITY ASSURANCE

Verify that MIFRC manufacturers qualify installers who are available to perform work in Project area.

A. Installer Qualifications: A firm or individual certified, licensed, or otherwise qualified by fireproofing manufacturer as experienced and with sufficient trained staff to install manufacturer's products according to specified requirements.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see SECTION 016000 "Product Requirements."

2.1 MATERIALS, GENERAL

A. Assemblies: Provide fireproofing, including auxiliary materials, according to requirements of each fire-resistance design and manufacturer's written instructions.

UL 263 is cited as equivalent to ASTM E 119 in the IBC's International Building Code 2007 Supplement (hereafter, the IBC 2007 Supplement), but not in earlier versions.

B. Fire-Resistance Design: Indicated on Drawings, tested according to [ASTM E 119] [ASTM E 119 or UL 263] <Insert testing requirement> by a qualified testing agency. Identify products with appropriate markings of applicable testing agency.

1. Steel members are to be considered unrestrained unless specifically noted otherwise.

Retain option in "VOC Content" Paragraph below if required for LEED-NC, LEED-CI, or LEED-CS Credit EQ 4.2 or if required by authorities having jurisdiction; coordinate with products and revise to suit Project.

C. VOC Content: Products shall comply with VOC content limits of authorities having jurisdiction[.][ and the following VOC limits when calculated according to 40 CFR 59, Subpart D (EPA Method 24):]

Retain applicable VOC content limits in subparagraphs below; revise if required.

1. Flat Paints and Coatings: 50 g/L.

2. Nonflat Paints and Coatings: 150 g/L.

3. Primers, Sealers, and Undercoaters: 200 g/L.

4. Anticorrosive and Antirust Paints Applied to Ferrous Metals: 250 g/L.

Many MIFRC, independent of primers and topcoats, have low or zero VOC content.

5. Fireproofing Exterior Coatings: 350 g/L.

Retain "Low-Emitting Materials" Paragraph below if required for LEED for Schools Credit EQ 4.

D. Low-Emitting Materials: Fireproofing used within the weatherproofing system shall comply with the testing and product requirements of the California Department of Health Services' "Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers."

E. Asbestos: Provide products containing no detectable asbestos.

2.2 MASTIC AND INTUMESCENT FIRE-RESISTIVE COATINGS

MIFRC materials and finishes vary with manufacturer and product and are based on approved fire-resistance designs that comply with the fire-resistance ratings of building elements as required by code.

Copy "MIFRC" Paragraph below and re-edit for each product or fire-resistance design. Topcoat may be mandatory or optional; it provides additional protection to fireproofing and offers greater color selection.

Insert drawing designation; consider using the approved fire-resistance design as drawing designation. Use these designations on Drawings to identify each product or fire-resistance design.

A. MIFRC <Insert drawing designation>: Manufacturer's standard, [factory-mixed formulation] [or] [factory-mixed, multicomponent system consisting of intumescent base coat and topcoat], and complying with indicated fire-resistance design.

Retain "Products" Subparagraph and list of manufacturers and products below to require specific products or a comparable product from other manufacturers.

1. Products: Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

Coordinate subparagraphs below with approved fire-resistance design, material composition, and other requirements retained.

a. Albi Manufacturing, Division of StanChem Inc.; [Albi Clad 800] [and] [Albi Clad TF] <Insert product name or designation>.

b. Carboline Company, subsidiary of RPM International, Fireproofing Products Div.; [AD Firefilm III] [Nullifire S605] [Nullifire S606] [Nullifire S607] [Thermo-Lag 3000-A] [Thermo-Lag 3000-FC] [Thermo-Lag 3000-P] [Thermo-Lag 3000-SA] [Thermo-Lag 3000-SP] [and] [Thermo-Sorb] <Insert product name or designation>.

c. International Paint Limited, subsidiary of Akzo Nobel N. V.; [Chartek 7] [Chartek 8] [Chartek 1709] [Interchar 212] [Interchar 404] [and] [Interchar 963] <Insert product name or designation>.

d. Isolatek International; [Cafco SprayFilm-WB 3] [and] [Cafco SprayFilm-WB 4] <Insert product name or designation>.

e. <Insert manufacturer's name; product name or designation>.

Retain "Application" Subparagraph below if applicable. UL's "Fire Resistance Directory" includes testing for these three optional uses (exposures).

2. Application: Designated for ["exterior"] ["interior general purpose"] [and] ["conditioned interior space purpose"] use by a qualified testing agency acceptable to authorities having jurisdiction.

3. Thickness: As required for fire-resistance design indicated, measured according to requirements of fire-resistance design.

4. Surface-Burning Characteristics: Flame-spread and smoke-developed indexes of 25 and 50, respectively, or less according to ASTM E 84.

If required, insert "Hardness" and "Bond Strength" subparagraphs. The IBC and UL do not have hardness or bond-strength requirements for MIFRC.

Retain "Finish" Subparagraph below if appearance is a concern.

5. Finish: [As selected by Architect from manufacturer's standard finishes] [Spray-textured finish] [Rolled, spray-textured finish] <Insert requirement>.

a. Color and Gloss: [As indicated by manufacturer's designations] [Match Architect's sample] [As selected by Architect from manufacturer's full range] <Insert color and gloss>.

2.3 AUXILIARY MATERIALS

A. General: Provide auxiliary materials that are compatible with fireproofing and substrates and are approved by UL or another testing and inspecting agency acceptable to authorities having jurisdiction for use in fire-resistance designs indicated.

B. Substrate Primers: Primers approved by fireproofing manufacturer.

C. Topcoat: Suitable for application over applied fireproofing; of type recommended in writing by fireproofing manufacturer for each fire-resistance design.

PART 3 -  EXECUTION

3.1 PREPARATION

A. Cover other work subject to damage from fallout or overspray of fireproofing materials during application.

B. Prime substrates where included in fire-resistance design and where recommended in writing by fireproofing manufacturer unless compatible shop primer has been applied and is in satisfactory condition to receive fireproofing.

C. For applications visible on completion of Project, repair substrates to remove surface imperfections that could affect uniformity of texture and thickness in finished surface of fireproofing.

3.2 APPLICATION

A. Examine substrates, areas, and conditions, with Installer present, for compliance with requirements for substrates and other conditions affecting performance of the Work and according to each fire-resistance design. Verify that objects penetrating fireproofing are securely attached to substrates and that substrates receiving fireproofing are not obstructed by ducts, piping, equipment, or other suspended construction that will interfere with fireproofing application.

B. Construct fireproofing assemblies that are identical to fire-resistance design indicated and products as specified, tested, and substantiated by test reports; for thickness, primers, topcoats, finishing, and other materials and procedures affecting fireproofing work.

C. Spray apply fireproofing to maximum extent possible. Following the spraying operation in each area, complete the coverage by trowel application or other placement method recommended in writing by fireproofing manufacturer.

D. Do not install enclosing or concealing construction until after fireproofing has been applied, inspected, and tested and corrections have been made to deficient applications.

E. Finishes: Where indicated, apply fireproofing to produce the following finishes:

1. Manufacturer's Standard Finishes: Finish according to manufacturer's written instructions for each finish selected.

2. Spray-Textured Finish: Finish left as spray applied with no further treatment.

3. Rolled, Spray-Textured Finish: Even finish produced by rolling spray-applied finish with a damp paint roller to remove drippings and excessive roughness.

4. Skip-Troweled Finish: Even leveled surface produced by troweling spray-applied finish to smooth out the texture and neaten edges.

3.3 FIELD QUALITY CONTROL

Retain first option in "Special Inspections" Paragraph below if Owner engages special inspector. Consider retaining second option if authorities having jurisdiction allow Contractor to engage special inspector. If retaining second option, retain "Field quality-control reports" Paragraph in "Informational Submittals" Article. See "Special Inspections" Article in the Evaluations.

A. Special Inspections: [Owner will engage] [Engage] a qualified special inspector to perform the following special inspections:

1. Test and inspect as required by the IBC, 1704.11.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

B. Fireproofing will be considered defective if it does not pass tests and inspections.

1. Remove and replace fireproofing that does not pass tests and inspections, and retest.

2. Apply additional fireproofing, per manufacturer's written instructions, where test results indicate insufficient thickness, and retest.

C. Prepare test and inspection reports.

3.4 CLEANING AND REPAIRING

A. Cleaning: Immediately after completing spraying operations in each containable area of Project, remove material overspray and fallout from surfaces of other construction and clean exposed surfaces to remove evidence of soiling.

B. Repair fireproofing damaged by other work before concealing it with other construction.

C. Repair fireproofing by reapplying it using same method as original installation or using manufacturer's recommended trowel-applied product.

END OF SECTION 078123

	INTUMESCENT FIREPROOFING
	078123 - 1



