Copyright 2010 AIA
MasterSpec Professional
02/10

Copyright 2010 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 078413 - PENETRATION FIRESTOPPING
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Penetrations in fire-resistance-rated walls.

2. Penetrations in horizontal assemblies.

3. Penetrations in smoke barriers.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product indicated.

B. LEED Submittals:

"Product Data for Credit IEQ 4.1" Subparagraph below applies to LEED-NC, LEED-CI, and LEED-CS; coordinate with requirements selected in Part 2.

1. Product Data for Credit IEQ 4.1: For penetration firestopping sealants and sealant primers, documentation including printed statement of VOC content.

"Laboratory Test Reports for Credit IEQ 4" Subparagraph below applies to LEED for Schools.

2. Laboratory Test Reports for Credit IEQ 4: For penetration firestopping selants and sealant primers, documentation indicating that products comply with the testing and product requirements of the California Department of Health Services' "Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers."

C. Product Schedule: For each penetration firestopping system. Include location and design designation of qualified testing and inspecting agency.

Retain subparagraph below only after verifying that authorities having jurisdiction will accept modifications handled by method in subparagraph.

1. Where Project conditions require modification to a qualified testing and inspecting agency's illustration for a particular penetration firestopping condition, submit illustration, with modifications marked, approved by penetration firestopping manufacturer's fire-protection engineer as an engineering judgment or equivalent fire-resistance-rated assembly.

1.3 INFORMATIONAL SUBMITTALS

A. Installer Certificates: From Installer indicating penetration firestopping has been installed in compliance with requirements and manufacturer's written recommendations.

B. Product test reports.

1.4 QUALITY ASSURANCE

If retaining first paragraph below, verify that installers are available to perform work in Project location.

A. Installer Qualifications: A firm that has been approved by FM Global according to FM Global 4991, "Approval of Firestop Contractors," or been evaluated by UL and found to comply with its "Qualified Firestop Contractor Program Requirements."

B. Fire-Test-Response Characteristics: Penetration firestopping shall comply with the following requirements:

1. Penetration firestopping tests are performed by [UL] [Intertek ETL SEMKO] [FM Global] [a qualified testing agency acceptable to authorities having jurisdiction] <Insert name of qualified testing agency>.

2. Penetration firestopping is identical to those tested per testing standard referenced in "Penetration Firestopping" Article. Provide rated systems bearing marking of qualified testing and inspection agency.

C. Preinstallation Conference: Conduct conference at [Project site] <Insert location>.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain paragraph and list of manufacturers in this article. See Section 016000 "Product Requirements."

A. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

1. A/D Fire Protection Systems Inc.

2. Grace Construction Products.

3. Hilti, Inc.

4. Johns Manville.

5. Nelson Firestop Products.

6. NUCO Inc.

7. Passive Fire Protection Partners.

8. RectorSeal Corporation.

9. Specified Technologies Inc.

10. 3M Fire Protection Products.

11. Tremco, Inc.; Tremco Fire Protection Systems Group.

12. USG Corporation.

13. <Insert manufacturer's name>.

2.2 PENETRATION FIRESTOPPING

A. Provide penetration firestopping that is produced and installed to resist spread of fire according to requirements indicated, resist passage of smoke and other gases, and maintain original fire-resistance rating of construction penetrated. Penetration firestopping systems shall be compatible with one another, with the substrates forming openings, and with penetrating items if any.

B. Penetrations in Fire-Resistance-Rated Walls: Ratings determined per ASTM E 814 or UL 1479, based on testing at a positive pressure differential of 0.01-inch wg (2.49 Pa).

F-rating in subparagraph below indicates resistance to flame spread.

1. F-Rating: Not less than the fire-resistance rating of constructions penetrated.

C. Penetrations in Horizontal Assemblies: Ratings determined per ASTM E 814 or UL 1479, based on testing at a positive pressure differential of 0.01-inch wg (2.49 Pa).

F-rating in first subparagraph below indicates resistance to flame spread.

1. F-Rating: At least 1 hour, but not less than the fire-resistance rating of constructions penetrated.

T-rating in subparagraph below indicates resistance to excessive thermal transmission.

2. T-Rating: At least 1 hour, but not less than the fire-resistance rating of constructions penetrated except for floor penetrations within the cavity of a wall.

D. Penetrations in Smoke Barriers: Provide penetration firestopping with ratings determined per UL 1479.

L-rating in subparagraph below indicates resistance to air leakage.

1. L-Rating: Not exceeding 5.0 cfm/sq. ft. (0.025 cu. m/s per sq. m) of penetration opening at 0.30-inch wg (74.7 Pa) at both ambient and elevated temperatures.

E. Exposed Penetration Firestopping: Provide products with flame-spread and smoke-developed indexes of less than 25 and 450, respectively, as determined per ASTM E 84.

Retain first paragraph below if required for LEED-NC, LEED-CI, or LEED-CS Credit IEQ 4.1.

F. VOC Content: Penetration firestopping sealants and sealant primers shall comply with the following limits for VOC content when calculated according to 40 CFR 59, Subpart D (EPA Method 24):

1. Sealants: 250 g/L.

2. Sealant Primers for Nonporous Substrates: 250 g/L.

3. Sealant Primers for Porous Substrates: 775 g/L.

Retain "Low-Emitting Materials" Paragraph below if required for LEED for Schools Credit IEQ 4.

G. Low-Emitting Materials: Penetration firestopping sealants and sealant primers shall comply with the testing and product requirements of the California Department of Health Services' "Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers."

H. Accessories: Provide components for each penetration firestopping system that are needed to install fill materials and to maintain ratings required. Use only those components specified by penetration firestopping manufacturer and approved by qualified testing and inspecting agency for firestopping indicated.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Examine substrates and conditions, with Installer present, for compliance with requirements for opening configurations, penetrating items, substrates, and other conditions affecting performance of the Work.

B. Install penetration firestopping to comply with manufacturer's written installation instructions and published drawings for products and applications indicated.

C. Install forming materials and other accessories of types required to support fill materials during their application and in the position needed to produce cross-sectional shapes and depths required to achieve fire ratings indicated.

1. After installing fill materials and allowing them to fully cure, remove combustible forming materials and other accessories not indicated as permanent components of firestopping.

D. Install fill materials for firestopping by proven techniques to produce the following results:

1. Fill voids and cavities formed by openings, forming materials, accessories, and penetrating items as required to achieve fire-resistance ratings indicated.

2. Apply materials so they contact and adhere to substrates formed by openings and penetrating items.

3. For fill materials that will remain exposed after completing the Work, finish to produce smooth, uniform surfaces that are flush with adjoining finishes.

3.2 IDENTIFICATION

Retain this article if labels are required; revise if labeling is limited to selected applications.

A. Identify penetration firestopping with preprinted metal or plastic labels. Attach labels permanently to surfaces adjacent to and within 6 inches (150 mm) of firestopping edge so labels will be visible to anyone seeking to remove penetrating items or firestopping. Use mechanical fasteners or self-adhering-type labels with adhesives capable of permanently bonding labels to surfaces on which labels are placed. Include the following information on labels:

1. The words "Warning - Penetration Firestopping - Do Not Disturb. Notify Building Management of Any Damage."

2. Contractor's name, address, and phone number.

3. Designation of applicable testing and inspecting agency.

4. Date of installation.

5. Manufacturer's name.

6. Installer's name.

3.3 FIELD QUALITY CONTROL

Retain this article if field quality control will be provided by Owner. If required, inspection of penetration firestopping is performed according to ASTM E 2174, "On-Site Inspection of Installed Fire Stops." To prevent conflicts of interest, ASTM E 2174 precludes making Contractor responsible for engaging the testing agency.

A. Owner will engage a qualified testing agency to perform tests and inspections.

B. Where deficiencies are found or penetration firestopping is damaged or removed because of testing, repair or replace penetration firestopping to comply with requirements.

C. Proceed with enclosing penetration firestopping with other construction only after inspection reports are issued and installations comply with requirements.

3.4 PENETRATION FIRESTOPPING SCHEDULE

Retain paragraphs in schedule below and revise to suit Project. Delete schedule if penetration firestopping systems are to be selected by Contractor.

Retain first paragraph below if UL-classified systems are required. See Evaluations for explanation of UL-system numbers.

A. Where UL-classified systems are indicated, they refer to system numbers in UL's "Fire Resistance Directory" under product Category XHEZ.

Retain first paragraph below if Intertek ETL SEMKO-listed systems are required.

B. Where Intertek ETL SEMKO-listed systems are indicated, they refer to design numbers in Intertek ETL SEMKO's "Directory of Listed Building Products" under "Firestop Systems."

Retain first paragraph below if FM Global-approved systems are required.

C. Where FM Global-approved systems are indicated, they refer to design numbers listed in FM Global's "Building Materials Approval Guide" under "Wall and Floor Penetration Fire Stops."

Copy and re-edit remaining paragraphs for each system required. Coordinate with manufacturers specified in Part 2. If retaining "FS" option as means of identifying location of each firestopping application on Drawings, insert number to complete drawing designation.

D. Firestopping with No Penetrating Items[ FS-<#>]:

1. UL-Classified Systems: [C-AJ-] [C-BJ-] [F-A-] [F-B-] [F-C-] [W-J-] [W-L-] <Insert four-digit number> [0001-0999].

2. Intertek ETL SEMKO-Listed Systems: <Insert design numbers>.

3. FM Global-Approved Systems: <Insert design numbers>.

E. Firestopping for Metallic Pipes, Conduit, or Tubing[ FS-<#>]:

1. UL-Classified Systems: [C-AJ-] [C-BJ-] [C-BK-] [F-A-] [F-B-] [F-C-] [F-E-] [W-J-] [W-K-] [W-L-] [W-N-] <Insert four-digit number> [1001-1999].

2. Intertek ETL SEMKO-Listed Systems: <Insert design number>.

3. FM Global-Approved Systems: <Insert design number>.

F. Firestopping for Nonmetallic Pipe, Conduit, or Tubing[ FS-<#>]:

1. UL-Classified Systems: [C-AJ-] [C-BJ-] [C-BK-] [F-A-] [F-B-] [F-C-] [F-E-] [W-J-] [W-K-] [W-L-] [W-N-] <Insert four-digit number> [2001-2999].

2. Intertek ETL SEMKO-Listed Systems: <Insert design number>.

3. FM Global-Approved Systems: <Insert design number>.

G. Firestopping for Electrical Cables[ FS-<#>]:

1. UL-Classified Systems: [C-AJ-] [C-BJ-] [C-BK-] [F-A-] [F-B-] [F-C-] [F-E-] [W-J-] [W-K-] [W-L-] <Insert four-digit number> [3001-3999].

2. Intertek ETL SEMKO-Listed Systems: <Insert design number>.

3. FM Global-Approved Systems: <Insert design number>.

H. Firestopping for Cable Trays with Electric Cables[ FS-<#>]:

1. UL-Classified Systems: [C-AJ-] [C-BJ-] [F-A-] [F-B-] [F-C-] [W-J-] [W-K-] [W-L-] <Insert four-digit number> [4001-4999].

2. Intertek ETL SEMKO-Listed Systems: <Insert design number>.

3. FM Global-Approved Systems: <Insert design number>.

I. Firestopping for Insulated Pipes[ FS-<#>]:

1. UL-Classified Systems: [C-AJ-] [C-BJ-] [C-BK-] [F-A-] [F-B-] [F-C-] [F-E-] [W-J-] [W-L-] [W-N-] <Insert four-digit number> [5001-5999].

2. Intertek ETL SEMKO-Listed Systems: <Insert design number>.

3. FM Global-Approved Systems: <Insert design number>.

J. Firestopping for Miscellaneous Electrical Penetrants[ FS-<#>]:

1. UL-Classified Systems: [C-AJ-] [C-BJ-] [F-A-] [W-L-] [W-J-] <Insert four-digit number> [6001-6999].

2. Intertek ETL SEMKO-Listed Systems: <Insert design number>.

3. FM Global-Approved Systems: <Insert design number>.

K. Firestopping for Miscellaneous Mechanical Penetrants[ FS-<#>]:

1. UL-Classified Systems: [C-AJ-] [C-BJ-] [F-A-] [F-B-] [F-C-] [F-E-] [W-J-] [W-L-] [W-N-] <Insert four-digit number> [7001-7999].

2. Intertek ETL SEMKO-Listed Systems: <Insert design number>.

3. FM Global-Approved Systems: <Insert design number>.

L. Firestopping for Groupings of Penetrants[ FS-<#>]:

1. UL-Classified Systems: [C-AJ-] [C-BJ-] [F-A-] [F-B-] [F-C-] [F-E-] [W-J-] [W-L-] <Insert four-digit number> [8001-8999].

2. Intertek ETL SEMKO-Listed Systems: <Insert design number>.

3. FM Global-Approved Systems: <Insert design number>.

END OF SECTION 078413

	PENETRATION FIRESTOPPING
	078413 - 1



