Copyright 2010 AIA
MasterSpec Professional
02/10

Copyright 2010 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 078446 - FIRE-RESISTIVE JOINT SYSTEMS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Joints in or between fire-resistance-rated constructions.

2. Joints at exterior curtain-wall/floor intersections.

3. Joints in smoke barriers.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product indicated.

B. LEED Submittals:

"Product Data for Credit IEQ 4.1" Subparagraph below applies to LEED-NC, LEED-CI, and LEED-CS; coordinate with requirements selected in Part 2.

1. Product Data for Credit IEQ 4.1: For fire-resistive joint system sealants, documentation including printed statement of VOC content.

"Laboratory Test Reports for Credit IEQ 4" Subparagraph below applies to LEED for Schools Credit IEQ 4.

2. Laboratory Test Reports for Credit IEQ 4: For fire-resistive joint system sealants, documentation indicating that products comply with the testing and product requirements of the California Department of Health Services' "Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers."

C. Product Schedule: For each fire-resistive joint system. Include location and design designation of qualified testing agency.

Retain subparagraph below only after verifying that authorities having jurisdiction will accept modifications handled by method in subparagraph.

1. Where Project conditions require modification to a qualified testing agency's illustration for a particular fire-resistive joint system condition, submit illustration, with modifications marked, approved by fire-resistive joint system manufacturer's fire-protection engineer as an engineering judgment or equivalent fire-resistance-rated assembly.

1.3 INFORMATIONAL SUBMITTALS

A. Installer Certificates: From Installer indicating fire-resistive joint systems have been installed in compliance with requirements and manufacturer's written recommendations.

B. Product test reports.

1.4 QUALITY ASSURANCE

If retaining first paragraph below, verify that installers are available to perform work in Project location.

A. Installer Qualifications: A firm that has been approved by FM Global according to FM Global 4991, "Approval of Firestop Contractors," or been evaluated by UL and found to comply with UL's "Qualified Firestop Contractor Program Requirements."

B. Fire-Test-Response Characteristics: Fire-resistive joint systems shall comply with the following requirements:

1. Fire-resistive joint system tests are performed by [UL] [Intertek ETL SEMKO] [a qualified testing agency acceptable to authorities having jurisdiction] <Insert name of qualified testing agency>.

C. Preinstallation Conference: Conduct conference at [Project site] <Insert location>.

PART 2 -  PRODUCTS

2.1 FIRE-RESISTIVE JOINT SYSTEMS

A. Where required, provide fire-resistive joint systems that are produced and installed to resist spread of fire according to requirements indicated, resist passage of smoke and other gases, and maintain original fire-resistance rating of assemblies in or between which fire-resistive joint systems are installed. Fire-resistive joint systems shall accommodate building movements without impairing their ability to resist the passage of fire and hot gases.

B. Joints in or between Fire-Resistance-Rated Construction: Ratings determined per ASTM E 1966 or UL 2079:

1. Fire-Resistance Rating: Equal to or exceeding the fire-resistance rating of construction they will join.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain subparagraph and list of manufacturers below. See Section 016000 "Product Requirements."

2. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. A/D Fire Protection Systems Inc.

b. CEMCO.

c. Fire Trak Corp.

d. Grace Construction Products.

e. Hilti, Inc.

f. Johns Manville.

g. Nelson Firestop Products.

h. NUCO Inc.

i. Passive Fire Protection Partners.

j. RectorSeal Corporation .

k. Specified Technologies Inc.

l. 3M Fire Protection Products.

m. Tremco, Inc.; Tremco Fire Protection Systems Group.

n. USG Corporation.

o. <Insert manufacturer's name>.

C. Joints at Exterior Curtain-Wall/Floor Intersections: Rating determined by ASTM E 119 based on testing at a positive pressure differential of 0.01-inch wg (2.49 Pa) or ASTM E 2307.

1. Fire-Resistance Rating: Equal to or exceeding the fire-resistance rating of the floor assembly.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain subparagraph and list of manufacturers below. See Section 016000 "Product Requirements."

2. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. A/D Fire Protection Systems Inc.

b. Grace Construction Products.

c. Hilti, Inc.

d. Johns Manville.

e. Nelson Firestop Products.

f. NUCO Inc.

g. Passive Fire Protection Partners.

h. RectorSeal Corporation.

i. Specified Technologies Inc.

j. 3M Fire Protection Products.

k. Thermafiber, Inc.

l. Tremco, Inc.; Tremco Fire Protection Systems Group.

m. USG Corporation.

n. <Insert manufacturer's name>.

D. Joints in Smoke Barriers: Ratings determined per UL 2079.

L-rating in first subparagraph below indicates resistance to air leakage.

1. L-Rating: Not exceeding 5.0 cfm/ft (0.00775 cu. m/s x m) of joint at 0.30 inch wg (74.7 Pa) at both ambient and elevated temperatures.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain subparagraph and list of manufacturers below. See Section 016000 "Product Requirements."

2. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. A/D Fire Protection Systems Inc.

b. Grace Construction Products.

c. Hilti, Inc.

d. Johns Manville.

e. Nelson Firestop Products.

f. NUCO Inc.

g. Passive Fire Protection Partners.

h. RectorSeal Corporation.

i. Specified Technologies Inc.

j. 3M Fire Protection Products.

k. Tremco, Inc.; Tremco Fire Protection Systems Group.

l. USG Corporation.

m. <Insert manufacturer's name>.

E. Exposed Fire-Resistive Joint Systems: Provide products with flame-spread and smoke-developed indexes of less than 25 and 450, respectively, as determined per ASTM E 84.

Retain "VOC Content" Paragraph below if required for LEED-NC, LEED-CI, or LEED-CS Credit IEQ 4.1. Coordinate with product selection in other Part 2 articles to ensure that products selected comply.

F. VOC Content: Fire-resistive joint system sealants shall comply with the following limits for VOC content when calculated according to 40 CFR 59, Subpart D (EPA Method 24):

1. Architectural Sealants: 250 g/L.

2. Sealant Primers for Nonporous Substrates: 250 g/L.

3. Sealant Primers for Porous Substrates: 775 g/L.

Retain "Low-Emitting Materials" Paragraph below if required for LEED for Schools Credit IEQ 4.

G. Low-Emitting Materials: Fire-resistive joint system sealants shall comply with the testing and product requirements of the California Department of Health Services' "Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers."

H. Accessories: Provide components of fire-resistive joint systems, including primers and forming materials, that are needed to install fill materials and to maintain ratings required. Use only components specified by fire-resistive joint system manufacturer and approved by the qualified testing agency for systems indicated.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Examine substrates and conditions, with Installer present, for compliance with requirements for joint configurations, substrates, and other conditions affecting performance of the Work.

B. Install fire-resistive joint systems to comply with manufacturer's written installation instructions and published drawings for products and applications indicated.

C. Install forming materials and other accessories of types required to support fill materials during their application and in position needed to produce cross-sectional shapes and depths required to achieve fire ratings indicated.

1. After installing fill materials and allowing them to fully cure, remove combustible forming materials and other accessories not indicated as permanent components of fire-resistive joint system.

D. Install fill materials for fire-resistive joint systems by proven techniques to produce the following results:

1. Fill voids and cavities formed by joints and forming materials as required to achieve fire-resistance ratings indicated.

2. Apply fill materials so they contact and adhere to substrates formed by joints.

3. For fill materials that will remain exposed after completing the Work, finish to produce smooth, uniform surfaces that are flush with adjoining finishes.

3.2 IDENTIFICATION

Retain this article if labels are required. Revise if labeling is limited to selected applications.

A. Identify fire-resistive joint systems with preprinted metal or plastic labels. Attach labels permanently to surfaces adjacent to and within 6 inches (150 mm) of joint edge so labels will be visible to anyone seeking to remove or penetrate joint system. Use mechanical fasteners or self-adhering-type labels with adhesives capable of permanently bonding labels to surfaces on which labels are placed. Include the following information on labels:

1. The words "Warning - Fire-Resistive Joint System - Do Not Disturb. Notify Building Management of Any Damage."

2. Contractor's name, address, and phone number.

3. Designation of applicable testing agency.

4. Date of installation.

5. Manufacturer's name.

6. Installer's name.

3.3 FIELD QUALITY CONTROL

Retain this article if field quality control will be provided by Owner. If required, inspection of fire-resistive joint systems is performed according to ASTM E 2393, "On-Site Inspection of Installed Fire-Resistive Joint Systems." To prevent conflicts of interest, ASTM E 2393 precludes making Contractor responsible for engaging the testing agency.

A. Inspecting Agency: Owner will engage a qualified testing agency to perform tests and inspections.

B. Where deficiencies are found or fire-resistive joint systems are damaged or removed due to testing, repair or replace fire-resistive joint systems so they comply with requirements.

C. Proceed with enclosing fire-resistive joint systems with other construction only after inspection reports are issued and installations comply with requirements.

3.4 FIRE-RESISTIVE JOINT SYSTEM SCHEDULE

Retain and revise paragraphs below to suit Project.

Retain first paragraph below if UL-classified systems are required. Retain first option for floor-to-floor, wall-to-wall, floor-to-wall, head-of-wall, bottom-of-wall, and wall-to-wall joints intended for use as corner guards; retain second option for perimeter fire-containment systems.

A. Where UL-classified systems are indicated, they refer to system numbers in UL's "Fire Resistance Directory" under product [Category XHBN] [or] [Category XHDG].

Retain first paragraph below if Intertek ETL SEMKO-listed systems are required. Fire-resistive joint systems and perimeter fire-barrier systems are included in both "Firestop Systems" and "Expansion/Seismic Joints" product categories. Verify location of listing and retain one or both options.

B. Where Intertek ETL SEMKO-listed systems are indicated, they refer to design numbers in Intertek ETL SEMKO's "Directory of Listed Building Products" under product category [Expansion/Seismic Joints] [or] [Firestop Systems].

If retaining "FRJS" or "PFRJS" options in remaining paragraphs below as means of identifying location of each fire-resistive joint system application on Drawings, insert number to complete drawing designations.

Copy and re-edit paragraphs for each system required. Coordinate with manufacturers specified in Part 2.

C. Floor-to-Floor, Fire-Resistive Joint Systems[ FRJS-<#>]:

1. UL-Classified Systems: FF-[D] [S]-<Insert four-digit number> [0000-0999] [1000-1999] [2000-2999] [3000-3999] [4000-4999].

D. Wall-to-Wall, Fire-Resistive Joint Systems[ FRJS-<#>]:

1. UL-Classified Systems: WW-[D] [S]-<Insert four-digit number> [0000-0999] [1000-1999] [2000-2999] [3000-3999] [4000-4999].

E. Floor-to-Wall, Fire-Resistive Joint Systems[ FRJS-<#>]:

1. UL-Classified Systems: FW-[D] [S]-<Insert four-digit number> [0000-0999] [1000-1999] [2000-2999] [3000-3999] [4000-4999].

F. Head-of-Wall, Fire-Resistive Joint Systems[ FRJS-<#>]:

1. UL-Classified Systems: HW-[D] [S]-<Insert four-digit number> [0000-0999] [1000-1999] [2000-2999] [3000-3999] [4000-4999].

2. Intertek ETL SEMKO-Listed Systems: <Insert design number>.

G. Bottom-of-Wall, Fire-Resistive Joint Systems[ FRJS-<#>]:

1. UL-Classified Systems: BW-[D] [S]-<Insert four-digit number> [0000-0999] [1000-1999] [2000-2999] [3000-3999] [4000-4999].

H. Wall-to-Wall, Fire-Resistive Joint Systems Intended for Use as Corner Guards[ FRJS-<#>]:

1. UL-Classified Systems: CG-[D] [S]-<Insert four-digit number> [0000-0999] [1000-1999] [2000-2999] [3000-3999] [4000-4999].

I. Perimeter Fire-Resistive Joint Systems[ PFRJS-<#>]:

1. UL-Classified Perimeter Fire-Containment Systems: CW-[D] [S]-<Insert four-digit number> [0000-0999] [1000-1999] [2000-2999].

2. Intertek ETL SEMKO-Listed, Perimeter Fire-Barrier Systems: <Insert design number>.

END OF SECTION 078446

	FIRE-RESISTIVE JOINT SYSTEMS
	078446 - 1



