Copyright 2011 AIA
MasterSpec Professional
11/11

Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 081113 - HOLLOW METAL DOORS AND FRAMES
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section includes hollow-metal work.

1.2 DEFINITIONS

Retain "Minimum Thickness" Paragraph below to indicate that metal thicknesses specified are base-metal measurements and do not include metallic coatings or finishes. Thicknesses indicated in this Section are according to SDI A250.8 and NAAMM-HMMA 803, both of which use the same values.

A. Minimum Thickness: Minimum thickness of base metal without coatings according to NAAMM-HMMA 803 or SDI A250.8.

1.3 ACTION SUBMITTALS

A. Product Data: For each type of product.

B. LEED Submittals:

1. Product Data for Credit MR 4: For products having recycled content, documentation indicating percentages by weight of postconsumer and preconsumer recycled content. Include statement indicating cost for each product having recycled content.

SDI A250.8 indicates that manufacturer's published details can replace Shop Drawings for hollow-metal work unless otherwise specified.

C. Shop Drawings: Include elevations, door edge details, frame profiles, metal thicknesses, preparations for hardware, and other details.

D. Samples for Initial Selection: For units with factory-applied color finishes.

E. Samples for Verification: For each type of exposed finish required.

F. Schedule: Prepared by or under the supervision of supplier, using same reference numbers for details and openings as those on Drawings.

1.4 INFORMATIONAL SUBMITTALS

A. Product test reports.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

2.1 MANUFACTURERS

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers. Verify specific capabilities with individual manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

1. Amweld International, LLC.

2. Apex Industries, Inc.

3. Ceco Door Products; an Assa Abloy Group company.

4. Commercial Door & Hardware Inc.

5. Concept Frames, Inc.

6. Curries Company; an Assa Abloy Group company.

7. Custom Metal Products.

8. Daybar.

9. Deansteel.

10. de La Fontaine Industries.

11. DKS Steel Door & Frame Sys. Inc.

12. Door Components, Inc.

13. Fleming-Baron Door Products.

14. Gensteel Doors Inc.

15. Greensteel Industries, Ltd.

16. HMF Express.

17. Hollow Metal Inc.

18. Hollow Metal Xpress.

19. J/R Metal Frames Manufacturing, Inc.

20. Karpen Steel Custom Doors & Frames.

21. L.I.F. Industries, Inc.

22. LaForce, Inc.

23. Megamet Industries, Inc.

24. Mesker Door Inc.

25. Michbi Doors Inc.

26. MPI Group, LLC (The).

27. National Custom Hollow Metal.

28. North American Door Corp.

29. Philipp Manufacturing Co (The).

30. Pioneer Industries, Inc.

31. Premier Products, Inc.

32. Republic Doors and Frames.

33. Rocky Mountain Metals, Inc.

34. Security Metal Products Corp.

35. Shanahans Manufacturing Ltd.

36. Steelcraft; an Ingersoll-Rand company.

37. Steward Steel; Door Division.

38. Stiles Custom Metal, Inc.

39. Titan Metal Products, Inc.

40. Trillium Steel Doors Limited.

41. West Central Mfg. Inc.

42. <Insert manufacturer's name>.

2.2 REGULATORY REQUIREMENTS

Revise "Fire-Rated Assemblies" Paragraph below to allow neutral pressure testing if required and as acceptable to authorities having jurisdiction. Retain option if temperature-rise assemblies are required.

A. Fire-Rated Assemblies: Complying with NFPA 80 and listed and labeled by a qualified testing agency acceptable to authorities having jurisdiction for fire-protection ratings[ and temperature-rise limits] indicated, based on testing at positive pressure according to NFPA 252 or UL 10C.

1. Smoke- and Draft-Control Assemblies: Provide an assembly with gaskets listed and labeled for smoke and draft control by a qualified testing agency acceptable to authorities having jurisdiction, based on testing according to UL 1784 and installed in compliance with NFPA 105.

B. Fire-Rated, Borrowed-Light Assemblies: Complying with NFPA 80 and listed and labeled by a testing and inspecting agency acceptable to authorities having jurisdiction for fire-protection ratings indicated, based on testing according to NFPA 257 or UL 9.

2.3 INTERIOR DOORS AND FRAMES

"Standard-Duty Doors and Frames," "Heavy-Duty Door and Frames," and "Extra-Heavy-Duty Doors and Frames" paragraphs below describe door- and frame-assembly types produced to SDI requirements; if Project contains more than one type, retain each applicable paragraph and indicate locations; if Project contains more than one variation for each paragraph, copy and indicate locations of each variation.

A. Standard-Duty Doors and Frames: SDI A250.8, Level 1. [At locations indicated in the Door and Frame Schedule] <Insert locations>.

1. Physical Performance: Level C according to SDI A250.4.

2. Doors:

a. Type: As indicated in the Door and Frame Schedule.

b. Thickness: [1-3/4 inches (44.5 mm)] [1-3/8 inches (34.9 mm)].

c. Face: [Uncoated,] [Metallic-coated,] cold-rolled steel sheet, minimum thickness of 0.032 inch (0.8 mm).

d. Edge Construction: [Model 1, Full Flush] [Model 2, Seamless].

e. Core: [Kraft-paper honeycomb] [Polystyrene] [Polyurethane] [Polyisocyanurate] [Mineral board] [Vertical steel stiffener] [Manufacturer's standard].

3. Frames:

a. Materials: [Uncoated,] [Metallic-coated,] cold-rolled steel sheet, minimum thickness of 0.042 inch (1.0 mm).

b. Construction: [Knocked down] [Slip-on drywall] [Face welded] [Full profile welded].

Second option in "Exposed Finish" Subparagraph below is unavailable for welded frames.

4. Exposed Finish: [Prime] [Factory].

B. Heavy-Duty Doors and Frames: SDI A250.8, Level 2. [At locations indicated in the Door and Frame Schedule] <Insert locations>.

1. Physical Performance: Level B according to SDI A250.4.

2. Doors:

a. Type: As indicated in the Door and Frame Schedule.

b. Thickness: 1-3/4 inches (44.5 mm).

c. Face: [Uncoated,] [Metallic-coated,] cold-rolled steel sheet, minimum thickness of 0.042 inch (1.0 mm).

d. Edge Construction: [Model 1, Full Flush] [Model 2, Seamless].

e. Core: [Kraft-paper honeycomb] [Polystyrene] [Polyurethane] [Polyisocyanurate] [Mineral board] [Vertical steel stiffener] [Manufacturer's standard].

3. Frames:

a. Materials: [Uncoated,] [Metallic-coated,] steel sheet, minimum thickness of 0.053 inch (1.3 mm).

b. Construction: [Knocked down] [Slip-on drywall] [Face welded] [Full profile welded].

Second option in "Exposed Finish" Subparagraph below is unavailable for welded frames.

4. Exposed Finish: [Prime] [Factory].

"Extra-Heavy-Duty Doors and Frames" Paragraph below describes interior-use assemblies fabricated to SDI requirements and containing doors with 0.053-inch (1.3-mm) thick, 16-gage face sheets and laminated cores.

C. Extra-Heavy-Duty Doors and Frames: SDI A250.8, Level 3. [At locations indicated in the Door and Frame Schedule] <Insert locations>.

1. Physical Performance: Level A according to SDI A250.4.

2. Doors:

a. Type: As indicated in the Door and Frame Schedule.

b. Thickness: 1-3/4 inches (44.5 mm).

c. Face: [Uncoated,] [Metallic-coated,] cold-rolled steel sheet, minimum thickness of 0.053 inch (1.3 mm).

d. Edge Construction: [Model 1, Full Flush] [Model 2, Seamless] [Model 3, Stile and Rail].

e. Core: [Kraft-paper honeycomb] [Polystyrene] [Polyurethane] [Polyisocyanurate] [Mineral board] [Vertical steel stiffener] [Manufacturer's standard].

3. Frames:

a. Materials: [Uncoated] [Metallic-coated] steel sheet, minimum thickness of 0.053 inch (1.3 mm).

b. Construction: [Knocked down] [Slip-on drywall] [Face welded] [Full profile welded].

Second option in "Exposed Finish" Subparagraph below is unavailable for welded frames.

4. Exposed Finish: [Prime] [Factory].

2.4 EXTERIOR HOLLOW-METAL DOORS AND FRAMES

"Heavy-Duty Door and Frames" and "Extra-Heavy-Duty Doors and Frames" paragraphs below describe door- and frame-assembly types produced to SDI requirements; if Project contains more than one type, retain each applicable paragraph and indicate locations; if Project contains more than one variation for each paragraph, copy and indicate locations of each variation. SDI does not recommend standard-duty doors and frames for exterior use.

A. Heavy-Duty Doors and Frames: SDI A250.8, Level 2. [At locations indicated in the Door and Frame Schedule] <Insert locations>.

1. Physical Performance: Level B according to SDI A250.4.

2. Doors:

a. Type: As indicated in the Door and Frame Schedule.

b. Thickness: 1-3/4 inches (44.5 mm).

c. Face: Metallic-coated steel sheet, minimum thickness of 0.042 inch (1.0 mm), with minimum A40 (ZF120) coating.

d. Edge Construction: [Model 1, Full Flush] [Model 2, Seamless].

e. Core: [Polystyrene] [Polyurethane] [Polyisocyanurate] [Manufacturer's standard insulation material].

The value used in the option in "Thermal-Rated Doors" Subparagraph below is for polyurethane-core doors and is an example only; verify ratings with manufacturers.

3. Thermal-Rated Doors: Provide doors fabricated with thermal-resistance value (R-value) of not less than [2.1 deg F x h x sq. ft./Btu (0.370 K x sq. m/W)] <Insert R-value> when tested according to ASTM C 1363.

4. Frames:

a. Materials: Metallic-coated steel sheet, minimum thickness of 0.053 inch (1.3 mm), with minimum A40 (ZF120) coating.

b. Construction: [Knocked down] [Face welded] [Full profile welded].

Second option in "Exposed Finish" Subparagraph below is unavailable for welded frames.

5. Exposed Finish: [Prime] [Factory].

B. Extra-Heavy-Duty Doors and Frames: SDI A250.8, Level 3. [At locations indicated in the Door and Frame Schedule] <Insert locations>.

1. Physical Performance: Level A according to SDI A250.4.

2. Doors:

a. Type: As indicated in the Door and Frame Schedule.

b. Thickness: 1-3/4 inches (44.5 mm).

c. Face: Metallic-coated steel sheet, minimum thickness of 0.053 inch (1.3 mm), with minimum A40 (ZF120) coating.

d. Edge Construction: [Model 1, Full Flush] [Model 2, Seamless] [Model 3, Stile and Rail].

e. Core: [Polystyrene] [Polyurethane] [Polyisocyanurate] [Manufacturer's standard insulation material].

The value used in the option in "Thermal-Rated Doors" Subparagraph below is for polyurethane-core doors and is an example only; verify ratings with manufacturers.

3. Thermal-Rated Doors: Provide doors fabricated with thermal-resistance value (R-value) of not less than [2.1 deg F x h x sq. ft./Btu (0.370 K x sq. m/W)] <Insert R-value> when tested according to ASTM C 1363.

4. Frames:

a. Materials: Metallic-coated steel sheet, minimum thickness of 0.053 inch (1.3 mm), with minimum A40 (ZF120) coating.

b. Construction: [Knocked down] [Face welded] [Full profile welded].

Second option in "Exposed Finish" Subparagraph below is unavailable for welded frames.

5. Exposed Finish: [Prime] [Factory].

2.5 FRAME ANCHORS

A. Jamb Anchors:

1. Masonry Type: Adjustable strap-and-stirrup or T-shaped anchors to suit frame size, not less than 0.042 inch (1.0 mm) thick, with corrugated or perforated straps not less than 2 inches (51 mm) wide by 10 inches (254 mm) long; or wire anchors not less than 0.177 inch (4.5 mm) thick.

2. Stud-Wall Type: Designed to engage stud, welded to back of frames; not less than 0.042 inch (1.0 mm) thick.

3. Compression Type for Drywall Slip-on Frames: Adjustable compression anchors.

4. Postinstalled Expansion Type for In-Place Concrete or Masonry: Minimum 3/8-inch- (9.5-mm-) diameter bolts with expansion shields or inserts. Provide pipe spacer from frame to wall, with throat reinforcement plate, welded to frame at each anchor location.

B. Floor Anchors: Formed from same material as frames, minimum thickness of 0.042 inch (1.0 mm), and as follows:

1. Monolithic Concrete Slabs: Clip-type anchors, with two holes to receive fasteners.

2. Separate Topping Concrete Slabs: Adjustable-type anchors with extension clips, allowing not less than 2-inch (51-mm) height adjustment. Terminate bottom of frames at finish floor surface.

2.6 MATERIALS

Retain "Recycled Content of Steel Products" Paragraph below to specify recycled content if applying for LEED Credit MR 4. USGBC allows a default value of 25 percent to be used for steel, without documentation; higher percentages can be claimed if they are supported by appropriate documentation. The Steel Recycling Institute indicates that steel sheet typically has 23 percent postconsumer recycled content and 1.5 percent preconsumer recycled content.

A. Recycled Content of Steel Products: Postconsumer recycled content plus one-half of preconsumer recycled content not less than [25] <Insert number> percent.

B. Cold-Rolled Steel Sheet: ASTM A 1008/A 1008M, Commercial Steel (CS), Type B; suitable for exposed applications.

C. Hot-Rolled Steel Sheet: ASTM A 1011/A 1011M, Commercial Steel (CS), Type B; free of scale, pitting, or surface defects; pickled and oiled.

D. Metallic-Coated Steel Sheet: ASTM A 653/A 653M, Commercial Steel (CS), Type B.

E. Frame Anchors: ASTM A 879/A 879M, Commercial Steel (CS), 04Z (12G) coating designation; mill phosphatized.

1. For anchors built into exterior walls, steel sheet complying with ASTM A 1008/A 1008M or ASTM A 1011/A 1011M, hot-dip galvanized according to ASTM A 153/A 153M, Class B.

F. Inserts, Bolts, and Fasteners: Hot-dip galvanized according to ASTM A 153/A 153M.

G. Power-Actuated Fasteners in Concrete: From corrosion-resistant materials.

H. Grout: ASTM C 476, except with a maximum slump of 4 inches (102 mm), as measured according to ASTM C 143/C 143M.

I. Mineral-Fiber Insulation: ASTM C 665, Type I (blankets without membrane facing).

J. Glazing: Section 088000 "Glazing."

Retain "Bituminous Coating" Paragraph below if required for grouted frames.

K. Bituminous Coating: Cold-applied asphalt mastic, compounded for 15-mil (0.4-mm) dry film thickness per coat.

2.7 FABRICATION

A. Fabricate hollow-metal work to be rigid and free of defects, warp, or buckle. Accurately form metal to required sizes and profiles, with minimum radius for metal thickness. Where practical, fit and assemble units in manufacturer's plant. To ensure proper assembly at Project site, clearly identify work that cannot be permanently factory assembled before shipment.

B. Hollow-Metal Doors:

1. Exterior Doors: Provide weep-hole openings in bottoms of exterior doors to permit moisture to escape. Seal joints in top edges of doors against water penetration.

Retain "Astragals" Subparagraph below if astragals are required for fire-protection rating.

2. Astragals: Provide overlapping astragal on one leaf of pairs of doors where required by NFPA 80 for fire-performance rating or where indicated.

C. Hollow-Metal Frames: Where frames are fabricated in sections due to shipping or handling limitations, provide alignment plates or angles at each joint, fabricated of same thickness metal as frames.

1. [Sidelight] [and] [Transom Bar] Frames: Provide closed tubular members with no visible face seams or joints, fabricated from same material as door frame. Fasten members at crossings and to jambs by butt welding.

2. Provide countersunk, flat- or oval-head exposed screws and bolts for exposed fasteners unless otherwise indicated.

3. Grout Guards: Weld guards to frame at back of hardware mortises in frames to be grouted.

4. Floor Anchors: Weld anchors to bottoms of jambs with at least four spot welds per anchor; however, for slip-on drywall frames, provide anchor clips or countersunk holes at bottoms of jambs.

5. Jamb Anchors: Provide number and spacing of anchors as follows:

Fire ratings may require additional anchors.

a. Masonry Type: Locate anchors not more than 16 inches (406 mm) from top and bottom of frame. Space anchors not more than 32 inches (813 mm) o.c., to match coursing, and as follows:

1) Two anchors per jamb up to 60 inches (1524 mm) high.

2) Three anchors per jamb from 60 to 90 inches (1524 to 2286 mm) high.

3) Four anchors per jamb from 90 to 120 inches (2286 to 3048 mm) high.

4) Four anchors per jamb plus one additional anchor per jamb for each 24 inches (610 mm) or fraction thereof above 120 inches (3048 mm) high.

b. Stud-Wall Type: Locate anchors not more than 18 inches (457 mm) from top and bottom of frame. Space anchors not more than 32 inches (813 mm) o.c. and as follows:

1) Three anchors per jamb up to 60 inches (1524 mm) high.

2) Four anchors per jamb from 60 to 90 inches (1524 to 2286 mm) high.

3) Five anchors per jamb from 90 to 96 inches (2286 to 2438 mm) high.

4) Five anchors per jamb plus one additional anchor per jamb for each 24 inches (610 mm) or fraction thereof above 96 inches (2438 mm) high.

c. Compression Type: Not less than two anchors in each frame.

d. Postinstalled Expansion Type: Locate anchors not more than 6 inches (152 mm) from top and bottom of frame. Space anchors not more than 26 inches (660 mm) o.c.

6. Door Silencers: Except on weather-stripped frames, drill stops to receive door silencers.

a. Single-Door Frames: Drill stop in strike jamb to receive three door silencers.

b. Double-Door Frames: Drill stop in head jamb to receive two door silencers.

D. Hardware Preparation: Factory prepare hollow-metal work to receive templated mortised hardware; include cutouts, reinforcement, mortising, drilling, and tapping according to SDI A250.6, the Door Hardware Schedule, and templates.

1. Reinforce doors and frames to receive nontemplated, mortised, and surface-mounted door hardware.

2. Comply with applicable requirements in SDI A250.6 and BHMA A156.115 for preparation of hollow-metal work for hardware.

E. Stops and Moldings: Provide stops and moldings around glazed lites and louvers where indicated. Form corners of stops and moldings with [butted] [or] [mitered] hairline joints.

1. Single Glazed Lites: Provide fixed stops and moldings welded on secure side of hollow-metal work.

2. Multiple Glazed Lites: Provide fixed and removable stops and moldings so that each glazed lite is capable of being removed independently.

3. Provide fixed frame moldings on outside of exterior and on secure side of interior doors and frames.

4. Provide loose stops and moldings on inside of hollow-metal work.

5. Coordinate rabbet width between fixed and removable stops with glazing and installation types indicated.

2.8 STEEL FINISHES

Retain "Prime Finish" or "Factory Finish" Paragraph below.

A. Prime Finish: Clean, pretreat, and apply manufacturer's standard primer.

1. Shop Primer: SDI A250.10.

B. Factory Finish: SDI A250.3.

Retain "Color and Gloss" Subparagraph below for factory finish.

1. Color and Gloss: [As indicated by manufacturer's designations] [Match Architect's sample] [As selected by Architect from manufacturer's full range] <Insert color and gloss>.

2.9 ACCESSORIES

Retain "Louvers" Paragraph below for door louvers. Revise to include other types such as pierced louvers, adjustable louvers, air grilles, and galvanized exterior louvers with insect screens.

A. Louvers: Provide [sightproof] [lightproof] louvers for interior doors, where indicated, which comply with SDI 111C, with blades or baffles formed of 0.020-inch- (0.5-mm-) thick, cold-rolled steel sheet set into 0.032-inch- (0.8-mm-) thick steel frame.

See Evaluations for discussion of fire-rated louvers.

1. Fire-Rated Automatic Louvers: Movable blades closed by actuating fusible link, and listed and labeled for use in fire-rated door assemblies of type and fire-resistance rating indicated.

B. Mullions and Transom Bars: Join to adjacent members by welding or rigid mechanical anchors.

C. Grout Guards: Formed from same material as frames, not less than 0.016 inch (0.4 mm) thick.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Hollow-Metal Frames: Install hollow-metal frames of size and profile indicated. Comply with SDI A250.11 or NAAMM-HMMA 840 as required by standards specified.

1. Set frames accurately in position; plumbed, aligned, and braced securely until permanent anchors are set. After wall construction is complete, remove temporary braces, leaving surfaces smooth and undamaged.

Retain any of first seven subparagraphs below to suit Project.

a. At fire-rated openings, install frames according to NFPA 80.

b. Where frames are fabricated in sections because of shipping or handling limitations, field splice at approved locations by welding face joint continuously; grind, fill, dress, and make splice smooth, flush, and invisible on exposed faces.

c. Install frames with removable stops located on secure side of opening.

d. Install door silencers in frames before grouting.

e. Remove temporary braces necessary for installation only after frames have been properly set and secured.

f. Check plumb, square, and twist of frames as walls are constructed. Shim as necessary to comply with installation tolerances.

g. Field apply bituminous coating to backs of frames that will be filled with grout containing antifreezing agents.

2. Floor Anchors: Provide floor anchors for each jamb and mullion that extends to floor, and secure with postinstalled expansion anchors.

Retain first subparagraph below if permitted.

a. Floor anchors may be set with power-actuated fasteners instead of postinstalled expansion anchors if so indicated and approved on Shop Drawings.

3. Metal-Stud Partitions: Solidly pack mineral-fiber insulation inside frames.

4. Masonry Walls: Coordinate installation of frames to allow for solidly filling space between frames and masonry with grout.

5. Concrete Walls: Solidly fill space between frames and concrete with mineral-fiber insulation.

6. In-Place Concrete or Masonry Construction: Secure frames in place with postinstalled expansion anchors. Countersink anchors, and fill and make smooth, flush, and invisible on exposed faces.

7. In-Place Metal or Wood-Stud Partitions: Secure slip-on drywall frames in place according to manufacturer's written instructions.

8. Installation Tolerances: Adjust hollow-metal door frames for squareness, alignment, twist, and plumb to the following tolerances:

a. Squareness: Plus or minus 1/16 inch (1.6 mm), measured at door rabbet on a line 90 degrees from jamb perpendicular to frame head.

b. Alignment: Plus or minus 1/16 inch (1.6 mm), measured at jambs on a horizontal line parallel to plane of wall.

c. Twist: Plus or minus 1/16 inch (1.6 mm), measured at opposite face corners of jambs on parallel lines, and perpendicular to plane of wall.

d. Plumbness: Plus or minus 1/16 inch (1.6 mm), measured at jambs at floor.

B. Hollow-Metal Doors: Fit hollow-metal doors accurately in frames, within clearances specified below. Shim as necessary.

1. Non-Fire-Rated Steel Doors:

Revise clearances in "Between Door and Frame Jambs and Head," "Between Edges of Pairs of Doors," "At Bottom of Door," and "Between Door Face and Stop" subparagraphs below to suit Project. Clearances indicated are based on SDI requirements; revise if required for HMMA products.

a. Between Door and Frame Jambs and Head: 1/8 inch (3.2 mm) plus or minus 1/32 inch (0.8 mm).

b. Between Edges of Pairs of Doors: 1/8 inch (3.2 mm) to 1/4 inch (6.3 mm) plus or minus 1/32 inch (0.8 mm).

c. At Bottom of Door: [3/4 inch (19.1 mm)] [5/8 inch (15.8 mm)] plus or minus 1/32 inch (0.8 mm).

d. Between Door Face and Stop: 1/16 inch (1.6 mm) to 1/8 inch (3.2 mm) plus or minus 1/32 inch (0.8 mm).

Retain "Fire-Rated Doors" and "Smoke-Control Doors" subparagraphs below if required.

2. Fire-Rated Doors: Install doors with clearances according to NFPA 80.

3. Smoke-Control Doors: Install doors and gaskets according to NFPA 105.

C. Glazing: Comply with installation requirements in Section 088000 "Glazing" and with hollow-metal manufacturer's written instructions.

1. Secure stops with countersunk flat- or oval-head machine screws spaced uniformly not more than 9 inches (230 mm) o.c. and not more than 2 inches (51 mm) o.c. from each corner.

3.2 ADJUSTING AND CLEANING

A. Final Adjustments: Check and readjust operating hardware items immediately before final inspection. Leave work in complete and proper operating condition. Remove and replace defective work, including hollow-metal work that is warped, bowed, or otherwise unacceptable.

B. Remove grout and other bonding material from hollow-metal work immediately after installation.

Retain "Prime-Coat Touchup" or "Metallic-Coated Surface Touchup" Paragraph below for field touchup of painted surfaces; or delete both and retain "Touchup Painting" Paragraph below if it is included in painting Sections.

C. Prime-Coat Touchup: Immediately after erection, sand smooth rusted or damaged areas of prime coat and apply touchup of compatible air-drying, rust-inhibitive primer.

D. Metallic-Coated Surface Touchup: Clean abraded areas and repair with galvanizing repair paint according to manufacturer's written instructions.

E. Touchup Painting: Cleaning and touchup painting of abraded areas of paint are specified in painting Sections.

END OF SECTION 081113

	HOLLOW METAL DOORS AND FRAMES
	081113 - 1



