Copyright 2010 AIA
MasterSpec Professional
11/10

Copyright 2010 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 089119 - FIXED LOUVERS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section includes fixed, [extruded-aluminum] [and] [formed-metal] louvers.

B. Related Requirements:

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

1. Section 081113 "Hollow Metal Doors and Frames" for louvers in hollow-metal doors.

2. Section 081416 "Flush Wood Doors" for louvers in flush wood doors.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product.

1. For louvers specified to bear AMCA seal, include printed catalog pages showing specified models with appropriate AMCA Certified Ratings Seals.

B. Shop Drawings: For louvers and accessories. Include plans, elevations, sections, details, and attachments to other work. Show frame profiles and blade profiles, angles, and spacing.

C. Samples: For each type of metal finish required.

Retain "Delegated-Design Submittal" Paragraph below if design services have been delegated to Contractor.

D. Delegated-Design Submittal: For louvers indicated to comply with structural[ and seismic] performance requirements, including analysis data signed and sealed by the qualified professional engineer responsible for their preparation.

1.3 INFORMATIONAL SUBMITTALS

Reports are generally unnecessary if product data bearing AMCA Certified Ratings Seal are required.

A. Product Test Reports: Based on tests performed according to AMCA 500-L.

Retain paragraph below if windborne-debris-impact resistance is required.

B. Windborne-debris-impact-resistance test reports.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

2.1 PERFORMANCE REQUIREMENTS

Retain "Delegated Design" Paragraph below if Contractor is required to assume responsibility for design. Most louver manufacturers do not have an engineer on staff who is legally authorized to practice in the jurisdiction where Project is located. For this reason, deleting below is advisable unless using large louvers. If specifying large or structurally complex louvers and relying on manufacturer for information about their structural performance, below can be retained and louver manufacturer or Contractor can engage a local engineer to prepare the required calculations.

A. Delegated Design: Design louvers, including comprehensive engineering analysis by a qualified professional engineer, using structural[ and seismic] performance requirements and design criteria indicated.

B. Structural Performance: Louvers shall withstand the effects of gravity loads and the following loads and stresses within limits and under conditions indicated without permanent deformation of louver components, noise or metal fatigue caused by louver-blade rattle or flutter, or permanent damage to fasteners and anchors. Wind pressures shall be considered to act normal to the face of the building.

Retain one of two "Wind Loads" subparagraphs below. If retaining first, indicate pressures on appropriate elevation Drawings. Requirements in second are examples only. Revise to suit Project. Consult a structural engineer to quantify design loads applicable to Project. Verify compliance with codes. See Evaluations.

1. Wind Loads: Determine loads based on pressures as indicated on Drawings.

2. Wind Loads: Determine loads based on a uniform pressure of [20 lbf/sq. ft. (957 Pa)] [30 lbf/sq. ft. (1436 Pa)] <Insert value>, acting inward or outward.

Retain "Windborne-Debris-Impact Resistance" Paragraph below if required by Project. The IBC defines wind-borne-debris regions. Enhanced protection applies to essential facilities. Verify requirements of authorities having jurisdiction.

C. Windborne-Debris-Impact Resistance: Louvers located within 30 feet (9.1 m) of grade shall pass [basic] [enhanced]-protection, large-missile testing requirements in ASTM E 1996 for [Wind Zone 1] [Wind Zone 2] [Wind Zone 3] [Wind Zone 4] when tested according to ASTM E 1886. Test specimens shall be no smaller in width and length than louvers indicated for use on Project.

Revise "Seismic Performance" Paragraph below to indicate specific loads determined by Project's structural engineer or refer to loads indicated on Drawings. Model building codes and ASCE/SEI 7 establish criteria for buildings subject to earthquake motions. Verify requirements with structural engineer.

D. Seismic Performance: Louvers, including attachments to other construction, shall withstand the effects of earthquake motions determined according to [ASCE/SEI 7] <Insert requirement>.

Design earthquake spectral response acceleration, short period (Sds) is determined by Project's location and site classification. This information is usually provided in structural notes on Drawings.

1. Design earthquake spectral response acceleration, short period (Sds) for Project is <Insert value>.

Component Importance Factor is generally 1.0 unless the structure is in Seismic Use Group III and louver is necessary for continued operation of facility or failure of louver could impair continued operation of facility, in which case the Component Importance Factor is 1.5.

2. Component Importance Factor: [1.5] [1.0].

Delete "Louver Performance Ratings" Paragraph below and performance ratings in Part 2 if louvers are sufficiently oversized that performance is not critical.

E. Louver Performance Ratings: Provide louvers complying with requirements specified, as demonstrated by testing manufacturer's stock units identical to those provided, except for length and width according to AMCA 500-L.

2.2 FIXED, EXTRUDED-ALUMINUM LOUVERS

Copy paragraphs below and re-edit for each product.

Insert drawing designation for each product required. Use these designations on Drawings to identify each product.

A. Horizontal, Nondrainable-Blade Louver <Insert drawing designation>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Air Balance Inc.; a Mestek company.

b. Air Flow Company, Inc.

c. Airolite Company, LLC (The).

d. All-Lite Architectural Products.

e. American Warming and Ventilating; a Mestek company.

f. Architectural Louvers; Harray, LLC.

g. Arrow United Industries; a division of Mestek, Inc.

h. Carnes Company, Inc.

i. Cesco Products; a division of Mestek, Inc.

j. Construction Specialties, Inc.

k. Dowco Products Group; Safe Air of Illinois.

l. Greenheck Fan Corporation.

m. Louvers & Dampers; a division of Mestek, Inc.

n. Metal Form Manufacturing, Inc.

o. NCA Manufacturing, Inc.

p. Nystrom, Inc.

q. Pottorff.

r. Reliable Products, Inc.

s. Ruskin Company; Tomkins PLC.

t. United Enertech.

u. Vent Products Co., Inc.

v. <Insert manufacturer's name>.

Requirements in first three subparagraphs below are based on products available from listed manufacturers. Revise to suit Project.

3. Louver Depth: [2 inches (50 mm)] [4 inches (100 mm)] [6 inches (150 mm)] <Insert dimension>.

4. Blade Profile: [Plain blade without] [Blade with] center baffle.

Insert descriptive requirements below that relate to appearance, such as blade spacing and angle, if required. If inserting such requirements, verify that louvers are available that comply with these requirements and with performance requirements selected.

5. Frame and Blade Nominal Thickness: Not less than [0.080 inch (2.03 mm)] [0.060 inch (1.52 mm) for blades and 0.080 inch (2.03 mm) for frames].

6. Mullion Type: [Exposed] [Semirecessed] [Fully recessed].

7. Louver Performance Ratings:

Requirements for free area, point of beginning water penetration, and air performance in three subparagraphs below are based on products available from listed manufacturers. If more than one choice is given for a requirement, the most lenient choice allows many products in the category to comply, resulting in competitive pricing; the most restrictive choice limits products to high-performance designs, potentially with higher costs.

a. Free Area: Not less than [7.5 sq. ft. (0.70 sq. m)] [8.0 sq. ft. (0.74 sq. m)] [8.5 sq. ft. (0.79 sq. m)] <Insert value> for 48-inch- (1220-mm-) wide by 48-inch- (1220-mm-) high louver.

b. Point of Beginning Water Penetration: Not less than [700 fpm (3.6 m/s)] [750 fpm (3.8 m/s)] [800 fpm (4.1 m/s)] [850 fpm (4.3 m/s)] [900 fpm (4.6 m/s)] [950 fpm (4.8 m/s)] <Insert value>.

Do not specify free-area velocity in "Air Performance" Subparagraph below that is greater than point of beginning water penetration specified in "Point of Beginning Water Penetration" Subparagraph above.

c. Air Performance: Not more than [0.10-inch wg (25-Pa)] <Insert value> static pressure drop at [650-fpm (3.3-m/s)] [700-fpm (3.6-m/s)] [750-fpm (3.8-m/s)] <Insert value> free-area [exhaust] [intake] velocity.

B. Horizontal, Drainable-Blade Louver <Insert drawing designation>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Air Balance Inc.; a Mestek company.

b. Air Flow Company, Inc.

c. Airolite Company, LLC (The).

d. All-Lite Architectural Products.

e. American Warming and Ventilating; a Mestek company.

f. Architectural Louvers; Harray, LLC.

g. Arrow United Industries; a division of Mestek, Inc.

h. Carnes Company, Inc.

i. Cesco Products; a division of Mestek, Inc.

j. Construction Specialties, Inc.

k. Dowco Products Group; Safe Air of Illinois.

l. Greenheck Fan Corporation.

m. Industrial Louvers, Inc.

n. Louvers & Dampers; a division of Mestek, Inc.

o. Metal Form Manufacturing, Inc.

p. NCA Manufacturing, Inc.

q. Nystrom, Inc.

r. Pottorff.

s. Reliable Products, Inc.

t. Ruskin Company; Tomkins PLC.

u. United Enertech.

v. Vent Products Co., Inc.

w. <Insert manufacturer's name>.

Requirements in "Louver Depth" and "Frame and Blade Nominal Thickness" subparagraphs below are based on products available from listed manufacturers. Revise to suit Project.

3. Louver Depth: [4 inches (100 mm)] [6 inches (150 mm)] <Insert dimension>.

Insert descriptive requirements below that relate to appearance, such as blade spacing and angle, if required. If inserting such requirements, verify that louvers are available that comply with these requirements and with performance requirements selected.

4. Frame and Blade Nominal Thickness: Not less than [0.080 inch (2.03 mm)] [0.060 inch (1.52 mm) for blades and 0.080 inch (2.03 mm) for frames].

5. Mullion Type: Exposed.

6. Louver Performance Ratings:

Requirements for free area, point of beginning water penetration, and air performance in first four subparagraphs below are based on products available from listed manufacturers. If more than one choice is given for a requirement, the most lenient choice allows many products in the category to comply, resulting in competitive pricing; the most restrictive choice limits products to high-performance designs, potentially with higher costs.

a. Free Area: Not less than [7.0 sq. ft. (0.65 sq. m)] [7.5 sq. ft. (0.70 sq. m)] [8.0 sq. ft. (0.74 sq. m)] [8.5 sq. ft. (0.79 sq. m)] <Insert value> for 48-inch- (1220-mm-) wide by 48-inch- (1220-mm-) high louver.

In "Point of Beginning Water Penetration" Subparagraph below, usually retain 900 to 1050 fpm (4.6 to 5.3 m/s) for 4-inch (100-mm) louvers and 950 to 1100 fpm (4.8 to 5.6 m/s) for 6-inch (150-mm) louvers.

b. Point of Beginning Water Penetration: Not less than [900 fpm (4.6 m/s)] [950 fpm (4.8 m/s)] [1000 fpm (5.1 m/s)] [1050 fpm (5.3 m/s)] [1100 fpm (5.6 m/s)] <Insert value>.

Retain one of two "Air Performance" subparagraphs below. If retaining first, usually retain 700 to 800 fpm (3.6 to 4.1 m/s) for 4-inch (100-mm) louvers and 750 to 850 fpm (3.8 to 4.3 m/s) for 6-inch (150-mm) louvers. Do not specify free-area velocity in either subparagraph that is greater than point of beginning water penetration specified in "Point of Beginning Water Penetration" Subparagraph above.

c. Air Performance: Not more than [0.10-inch wg (25-Pa)] <Insert value> static pressure drop at [700-fpm (3.6-m/s)] [750-fpm (3.8-m/s)] [800-fpm (4.1-m/s)] [850-fpm (4.3-m/s)] <Insert value> free-area [exhaust] [intake] velocity.

d. Air Performance: Not more than [0.15-inch wg (37-Pa)] <Insert value> static pressure drop at [900-fpm (4.6-m/s)] [950-fpm (4.8-m/s)] [1000-fpm (5.1-m/s)] <Insert value> free-area [exhaust] [intake] velocity.

Verify availability of seal in "AMCA Seal" Subparagraph below for louver sizes indicated. Delete if not required. Coordinate with product data submittal requirement.

7. AMCA Seal: Mark units with AMCA Certified Ratings Seal.

C. Horizontal, Wind-Driven-Rain-Resistant Louver <Insert drawing designation>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Air Balance Inc.; a Mestek company.

b. Air Flow Company, Inc.

c. Airolite Company, LLC (The).

d. All-Lite Architectural Products.

e. American Warming and Ventilating; a Mestek company.

f. Architectural Louvers; Harray, LLC.

g. Arrow United Industries; a division of Mestek, Inc.

h. Construction Specialties, Inc.

i. Greenheck Fan Corporation.

j. Industrial Louvers, Inc.

k. NCA Manufacturing, Inc.

l. Nystrom, Inc.

m. Pottorff.

n. Reliable Products, Inc.

o. Ruskin Company; Tomkins PLC.

p. United Enertech.

q. <Insert manufacturer's name>.

Requirements in "Louver Depth" and "Frame and Blade Nominal Thickness" subparagraphs below are based on products available from listed manufacturers. Revise to suit Project.

3. Louver Depth: [4 inches (100 mm)] [5 inches (125 mm)] [7 inches (175 mm)] [8 inches (200 mm)] [9 inches (225 mm)] <Insert dimension>.

Usually retain second option in "Frame and Blade Nominal Thickness" Subparagraph below; blades of wind-driven-rain-resistant louvers gain stiffness from their complex shapes and, therefore, do not need to be as thick as blades of some other louver types. If retaining first option, verify availability of louvers with performance requirements selected.

4. Frame and Blade Nominal Thickness: Not less than [0.080 inch (2.03 mm)] [0.060 inch (1.52 mm) for blades and 0.080 inch (2.03 mm) for frames].

5. Louver Performance Ratings:

Requirements in "Free Area" and "Air Performance" subparagraphs below are based on products available from listed manufacturers. If more than one choice is given for a requirement, the most lenient choice allows many products in the category to comply, resulting in competitive pricing; the most restrictive choice limits products to high-performance designs, potentially with higher costs.

a. Free Area: Not less than [5.0 sq. ft. (0.46 sq. m)] [6.0 sq. ft. (0.56 sq. m)] [7.0 sq. ft. (0.65 sq. m)] <Insert value> for 48-inch- (1220-mm-) wide by 48-inch- (1220-mm-) high louver.

b. Air Performance: Not more than [0.10-inch wg (25-Pa)] <Insert value> static pressure drop at [600-fpm (3.0-m/s)] [700-fpm (3.6-m/s)] [800-fpm (4.1-m/s)] <Insert value> free-area [exhaust] [intake] velocity.

c. Wind-Driven Rain Performance: Not less than [99] [95] [80] <Insert number> percent effectiveness when subjected to a rainfall rate of [3 inches (75 mm) per hour and a wind speed of 29 mph (13 m/s)] [8 inches (200 mm) per hour and a wind speed of 50 mph (22.4 m/s)] at a core-area intake velocity of [300 fpm (1.5 m/s)] [400 fpm (2.0 m/s)] [500 fpm (2.5 m/s)] <Insert value>.

Verify availability of seal in "AMCA Seal" Subparagraph below for louver sizes indicated. Delete if not required. Coordinate with product data submittal requirement.

6. AMCA Seal: Mark units with AMCA Certified Ratings Seal.

D. Vertical, Wind-Driven-Rain-Resistant Louver <Insert drawing designation>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Air Balance Inc.; a Mestek company.

b. Air Flow Company, Inc.

c. Airolite Company, LLC (The).

d. All-Lite Architectural Products.

e. American Warming and Ventilating; a Mestek company.

f. Arrow United Industries; a division of Mestek, Inc.

g. Cesco Products; a division of Mestek, Inc.

h. Construction Specialties, Inc.

i. Greenheck Fan Corporation.

j. Industrial Louvers, Inc.

k. Louvers & Dampers; a division of Mestek, Inc.

l. NCA Manufacturing, Inc.

m. Nystrom, Inc.

n. Pottorff.

o. Reliable Products, Inc.

p. Ruskin Company; Tomkins PLC.

q. United Enertech.

r. <Insert manufacturer's name>.

Requirements in "Louver Depth" and "Frame and Blade Nominal Thickness" subparagraphs below are based on products available from listed manufacturers. Revise to suit Project.

3. Louver Depth: [4 inches (100 mm)] [6 inches (150 mm)] [8 inches (200 mm)] [9 inches (225 mm)] [12 inches (300 mm)] <Insert dimension>.

Usually retain second option in "Frame and Blade Nominal Thickness" Subparagraph below; blades of wind-driven-rain-resistant louvers gain stiffness from their complex shapes and, therefore, do not need to be as thick as blades of some other louver types. If retaining first option, verify availability of louvers with performance requirements selected.

4. Frame and Blade Nominal Thickness: Not less than [0.080 inch (2.03 mm)] [0.060 inch (1.52 mm) for blades and 0.080 inch (2.03 mm) for frames].

5. Louver Performance Ratings:

Requirements in "Free Air" and "Air Performance" subparagraphs below are based on products available from listed manufacturers. If more than one choice is given for a requirement, the most lenient choice allows many products in the category to comply, resulting in competitive pricing; the most restrictive choice limits products to high-performance designs, potentially with higher costs.

a. Free Area: Not less than [5.0 sq. ft. (0.46 sq. m)] [6.0 sq. ft. (0.56 sq. m)] [7.0 sq. ft. (0.65 sq. m)] <Insert value> for 48-inch- (1220-mm-) wide by 48-inch- (1220-mm-) high louver.

b. Air Performance: Not more than [0.10-inch wg (25-Pa)] <Insert value> static pressure drop at [600-fpm (3.0-m/s)] [700-fpm (3.6-m/s)] [800-fpm (4.1-m/s)] <Insert value> free-area [exhaust] [intake] velocity.

Most vertical wind-driven-rain-resistant louvers provide 99 percent effectiveness under the most severe conditions.

c. Wind-Driven Rain Performance: Not less than 99 percent effectiveness when subjected to a rainfall rate of [3 inches (75 mm) per hour and a wind speed of 29 mph (13 m/s)] [8 inches (200 mm) per hour and a wind speed of 50 mph (22.4 m/s)] at a core-area intake velocity of [300 fpm (1.5 m/s)] [400 fpm (2.0 m/s)] [500 fpm (2.5 m/s)] <Insert value>.

Verify availability of seal in "AMCA Seal" Subparagraph below for louver sizes indicated. Delete if not required. Coordinate with product data submittal requirement.

6. AMCA Seal: Mark units with AMCA Certified Ratings Seal.

2.3 FIXED, FORMED-METAL LOUVERS

Copy paragraphs below and re-edit for each product.

Insert drawing designation for each product required. Use these designations on Drawings to identify each product.

A. Horizontal, Nondrainable-Blade Louver <Insert drawing designation>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Air Balance Inc.; a Mestek company.

b. Air Flow Company, Inc.

c. Airolite Company, LLC (The).

d. All-Lite Architectural Products.

e. American Warming and Ventilating; a Mestek company.

f. Arrow United Industries; a division of Mestek, Inc.

g. Cesco Products; a division of Mestek, Inc.

h. Construction Specialties, Inc.

i. Dowco Products Group; Safe Air of Illinois.

j. Greenheck Fan Corporation.

k. Industrial Louvers, Inc.

l. Metal Form Manufacturing, Inc.

m. NCA Manufacturing, Inc.

n. Pottorff.

o. Ruskin Company; Tomkins PLC.

p. United Enertech.

q. Vent Products Co., Inc.

r. <Insert manufacturer's name>.

Requirements in first four subparagraphs below are based on products available from listed manufacturers. Revise to suit Project.

3. Louver Depth: [4 inches (100 mm)] [6 inches (150 mm)] <Insert dimension>.

4. Blade Profile: [Plain blade without] [Blade with] center baffle.

Insert descriptive requirements below that relate to appearance, such as blade spacing and angle, if required. If inserting such requirements, verify that louvers are available that comply with these requirements and with performance requirements selected.

5. Frame and Blade Material and Nominal Thickness: Galvanized-steel sheet, not less than [0.052 inch (1.32 mm) for frames and 0.040 inch (1.02 mm) for blades] [0.052 inch (1.32 mm)] [0.064 inch (1.63 mm)].

6. Frame and Blade Material and Nominal Thickness: Stainless-steel sheet, not less than [0.050 inch (1.27 mm)] [0.062 inch (1.59 mm)].

7. Mullion Type: [Exposed] [Semirecessed] [Fully recessed].

8. Louver Performance Ratings:

Requirements for free area, point of beginning water penetration, and air performance in three subparagraphs below are based on products available from listed manufacturers. If more than one choice is given for a requirement, the most lenient choice allows many products in the category to comply, resulting in competitive pricing; the most restrictive choice limits products to high-performance designs, potentially with higher costs.

a. Free Area: Not less than [6.5 sq. ft. (0.60 sq. m)] [7.0 sq. ft. (0.65 sq. m)] [7.5 sq. ft. (0.70 sq. m)] [8.0 sq. ft. (0.74 sq. m)] <Insert value> for 48-inch- (1220-mm-) wide by 48-inch- (1220-mm-) high louver.

b. Point of Beginning Water Penetration: Not less than [550 fpm (2.8 m/s)] [600 fpm (3.0 m/s)] [650 fpm (3.3 m/s)] [700 fpm (3.6 m/s)] <Insert value>.

Do not specify free-area velocity in "Air Performance" Subparagraph below that is greater than point of beginning water penetration specified in "Point of Beginning Water Penetration" Subparagraph above.

c. Air Performance: Not more than [0.10-inch wg (25-Pa)] <Insert value> static pressure drop at [550-fpm (2.8-m/s)] [600-fpm (3.0-m/s)] [650-fpm (3.3-m/s)] [700-fpm (3.6-m/s)] <Insert value> free-area [exhaust] [intake] velocity.

B. Horizontal, Drainable-Blade Louver <Insert drawing designation>:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Air Balance Inc.; a Mestek company.

b. Air Flow Company, Inc.

c. Airolite Company, LLC (The).

d. All-Lite Architectural Products.

e. American Warming and Ventilating; a Mestek company.

f. Arrow United Industries; a division of Mestek, Inc.

g. Cesco Products; a division of Mestek, Inc.

h. Construction Specialties, Inc.

i. Dowco Products Group; Safe Air of Illinois.

j. Greenheck Fan Corporation.

k. Industrial Louvers, Inc.

l. Metal Form Manufacturing, Inc.

m. NCA Manufacturing, Inc.

n. Pottorff.

o. Ruskin Company; Tomkins PLC.

p. United Enertech.

q. Vent Products Co., Inc.

r. <Insert manufacturer's name>.

Requirements in first three subparagraphs below are based on products available from listed manufacturers. Revise to suit Project.

3. Louver Depth: [4 inches (100 mm)] [6 inches (150 mm)] <Insert dimension>.

Insert descriptive requirements below that relate to appearance, such as blade spacing and angle, if required. If inserting such requirements, verify that louvers are available that comply with these requirements and with performance requirements selected.

4. Frame and Blade Material and Nominal Thickness: Galvanized-steel sheet, not less than [0.052 inch (1.32 mm) for frames and 0.040 inch (1.02 mm) for blades] [0.052 inch (1.32 mm)] [0.064 inch (1.63 mm)].

5. Frame and Blade Material and Nominal Thickness: Stainless-steel sheet, not less than [0.050 inch (1.27 mm)] [0.062 inch (1.59 mm)].

6. Mullion Type: Exposed.

7. Louver Performance Ratings:

Requirements for free area, point of beginning water penetration, and air performance in first four subparagraphs below are based on products available from listed manufacturers. If more than one choice is given for a requirement, the most lenient choice allows many products in the category to comply, resulting in competitive pricing; the most restrictive choice limits products to high-performance designs, potentially with higher costs.

a. Free Area: Not less than [7.0 sq. ft. (0.65 sq. m)] [7.5 sq. ft. (0.70 sq. m)] [8.0 sq. ft. (0.74 sq. m)] [8.5 sq. ft. (0.79 sq. m)] <Insert value> for 48-inch- (1220-mm-) wide by 48-inch- (1220-mm-) high louver.

b. Point of Beginning Water Penetration: Not less than [800 fpm (4.1 m/s)] [850 fpm (4.3 m/s)] [900 fpm (4.6 m/s)] [950 fpm (4.8 m/s)] [1000 fpm (5.1 m/s)] <Insert value>.

Retain one of two "Air Performance" subparagraphs below. Do not specify free-area velocity in either subparagraph that is greater than point of beginning water penetration specified in "Point of Beginning Water Penetration" Subparagraph above.

c. Air Performance: Not more than [0.10-inch wg (25-Pa)] <Insert value> static pressure drop at [700-fpm (3.6-m/s)] [750-fpm (3.8-m/s)] [800-fpm (4.1-m/s)] [850-fpm (4.3-m/s)] <Insert value> free-area [exhaust] [intake] velocity.

d. Air Performance: Not more than [0.15-inch wg (37-Pa)] <Insert value> static pressure drop at [900-fpm (4.6-m/s)] [950-fpm (4.8-m/s)] [1000-fpm (5.1-m/s)] <Insert value> free-area velocity.

Verify availability of seal in "AMCA Seal" Subparagraph below for louver sizes indicated. Delete if not required. Coordinate with product data submittal requirement.

8. AMCA Seal: Mark units with AMCA Certified Ratings Seal.

2.4 LOUVER SCREENS

Retain one of two options in "General" Paragraph below. If retaining second option, indicate locations on Drawings.

A. General: Provide screen at [each exterior louver] [louvers indicated].

Retain applicable requirements in "Screen Location for Fixed Louvers" and "Screening Type" subparagraphs below to suit louver locations, types, and functions. See Evaluations.

1. Screen Location for Fixed Louvers: Interior face.

The International Mechanical Code requires that openings in louvers or screens for exhaust openings or intake openings in residential occupancies be 1/4 to 1/2 inch (6 to 12 mm); for intake openings in nonresidential occupancies, 1/4 to 1 inch (6 to 25 mm).

2. Screening Type: Bird screening.

B. Louver Screen Frames: Same type and form of metal as indicated for louver to which screens are attached.

If more than one screen type is required, coordinate selection with Drawings and with mechanical engineer for required percentage of open area. Retain one of three louver screening paragraphs below for louver material selected. Delete all three if manufacturer's standard screening is acceptable.

C. Louver Screening for Aluminum Louvers:

Retain one or more of three "Bird Screening" subparagraphs below, or insert another mesh or wire size.

1. Bird Screening: Aluminum, 1/2-inch- (13-mm-) square mesh, 0.063-inch (1.60-mm) wire.

2. Bird Screening: Stainless steel, 1/2-inch- (13-mm-) square mesh, 0.047-inch (1.19-mm) wire.

3. Bird Screening: Flattened, expanded aluminum, 3/4 by 0.050 inch (19 by 1.27 mm) thick.

D. Louver Screening for Galvanized-Steel Louvers:

Retain one or more of two "Bird Screening" subparagraphs below, or insert another mesh or wire size.

1. Bird Screening: Galvanized steel, 1/2-inch- (13-mm-) square mesh, 0.041-inch (1.04-mm) wire.

2. Bird Screening: Stainless steel, 1/2-inch- (13-mm-) square mesh, 0.047-inch (1.19-mm) wire.

E. Louver Screening for Stainless-Steel Louvers:

1. Bird Screening: Stainless steel, 1/2-inch- (13-mm-) square mesh, 0.047-inch (1.19-mm) wire.

Insert other screening materials as required, including bronze and glass fiber.

2.5 MATERIALS

A. Aluminum Extrusions: ASTM B 221 (ASTM B 221M), Alloy 6063-T5, T-52, or T6.

B. Aluminum Sheet: ASTM B 209 (ASTM B 209M), Alloy 3003 or 5005 with temper as required for forming, or as otherwise recommended by metal producer for required finish.

C. Galvanized-Steel Sheet: ASTM A 653/A 653M, [G60 (Z180)] [G90 (Z275)] zinc coating, mill phosphatized.

D. Stainless-Steel Sheet: ASTM A 240/A 240M, Type 304, [No. 2B finish] [No. 2D finish] [No. 4 finish, with grain running parallel to length of blades and frame members] [No. 4 finish, with grain running perpendicular to length of blades and frame members] [No. 4 finish, with grain running perpendicular to length of blades and parallel to length of frame members] [No. 6 finish].

E. Fasteners: Use types and sizes to suit unit installation conditions.

First option in first subparagraph below specifies flush heads; second option specifies raised heads.

1. Use [Phillips flat-head] [hex-head or Phillips pan-head] [tamper-resistant] screws for exposed fasteners unless otherwise indicated.

2. For fastening aluminum, use aluminum or 300 series stainless-steel fasteners.

3. For fastening galvanized steel, use hot-dip-galvanized steel or 300 series stainless-steel fasteners.

4. For fastening stainless steel, use 300 series stainless-steel fasteners.

5. For color-finished louvers, use fasteners with heads that match color of louvers.

F. Bituminous Paint: Cold-applied asphalt emulsion complying with ASTM D 1187.

2.6 FABRICATION

A. Fabricate frames, including integral sills, to fit in openings of sizes indicated, with allowances made for fabrication and installation tolerances, adjoining material tolerances, and perimeter sealant joints.

B. Join frame members to each other and to fixed louver blades with fillet welds [concealed from view] [, threaded fasteners, or both, as standard with louver manufacturer] unless otherwise indicated or size of louver assembly makes bolted connections between frame members necessary.

2.7 ALUMINUM FINISHES

Retain finishes in paragraphs below to suit Project. If retaining more than one, indicate location of each on Drawings or by inserts.

Retain one of two options in "Clear Anodic Finish" Paragraph below. Class II finish is standard with many manufacturers; Class I finish is heavy anodized. Verify availability with manufacturers.

A. Clear Anodic Finish: AAMA 611, [AA-M12C22A41, Class I, 0.018 mm] [AA-M12C22A31, Class II, 0.010 mm] or thicker.

Retain one of two options in "Color Anodic Finish" Paragraph below. Verify availability with manufacturers.

B. Color Anodic Finish: AAMA 611, [AA-M12C22A42/A44, Class I, 0.018 mm] [AA-M12C22A32/A34, Class II, 0.010 mm] or thicker.

1. Color: [Champagne] [Light bronze] [Medium bronze] [Dark bronze] [Black] <Insert color>.

Options in "Color" Subparagraph above are examples only and may vary in color range and availability among manufacturers. Retain one or delete all above and retain one of two options in "Color" Subparagraph below.

2. Color: [Match Architect's sample] [As selected by Architect from full range of industry colors and color densities].

Retain one of two "High-Performance Organic Finish" paragraphs below; if both are required, indicate location of each system on Drawings, in schedules, or by inserts. Retain AAMA 2604 or AAMA 2605 for high- or superior-performance organic coatings, respectively, on extrusions and panels. If specific products are required, name coating manufacturers and products.

C. High-Performance Organic Finish: Two-coat fluoropolymer finish complying with [AAMA 2604] [AAMA 2605] and containing not less than [50] [70] percent PVDF resin by weight in color coat. Prepare, pretreat, and apply coating to exposed metal surfaces to comply with coating and resin manufacturers' written instructions.

1. Color and Gloss: [As indicated by manufacturer's designations] [Match Architect's sample] [As selected by Architect from manufacturer's full range] <Insert color and gloss>.

D. High-Performance Organic Finish: [Three] [Four]-coat fluoropolymer finish complying with AAMA 2605 and containing not less than [50] [70] percent PVDF resin by weight in both color coat and clear topcoat. Prepare, pretreat, and apply coating to exposed metal surfaces to comply with coating and resin manufacturers' written instructions.

1. Color and Gloss: [As indicated by manufacturer's designations] [Match Architect's sample] [As selected by Architect from manufacturer's full range] <Insert color and gloss>.

2.8 GALVANIZED-STEEL SHEET FINISHES

Some louvers are made from coil-coated metal sheet and are touched up after assembly. Finishing galvanized steel after fabrication provides better corrosion protection. Usually retain first paragraph below unless cost is primary consideration.

A. Finish louvers after assembly.

B. Surface Preparation: Clean surfaces with nonpetroleum solvent so surfaces are free of oil and other contaminants. After cleaning, apply a conversion coating compatible with the organic coating to be applied over it. Clean welds, mechanical connections, and abraded areas and repair according to ASTM A 780.

C. Baked-Enamel or Powder-Coat Finish: Immediately after cleaning and pretreating, apply manufacturer's standard two-coat, baked-on finish consisting of prime coat and thermosetting topcoat, with a minimum dry film thickness of 2 mils (0.05 mm).

1. Color and Gloss: [As indicated by manufacturer's designations] [Match Architect's sample] [As selected by Architect from manufacturer's full range] <Insert color and gloss>.

For exact finish, insert names of coating manufacturers and products.

2.9 STAINLESS-STEEL SHEET FINISHES

Delete this article if no stainless-steel, formed-metal louvers.

A. Repair sheet finish by grinding and polishing irregularities, weld spatter, scratches, and forming marks to match surrounding finish.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Locate and place louvers level, plumb, and at indicated alignment with adjacent work.

B. Use concealed anchorages where possible. Provide brass or lead washers fitted to screws where required to protect metal surfaces and to make a weathertight connection.

C. Provide perimeter reveals and openings of uniform width for sealants and joint fillers, as indicated.

D. Protect unpainted galvanized and nonferrous-metal surfaces that are in contact with concrete, masonry, or dissimilar metals from corrosion and galvanic action by applying a heavy coating of bituminous paint or by separating surfaces with waterproof gaskets or nonmetallic flashing.

3.2 ADJUSTING

A. Restore louvers damaged during installation and construction so no evidence remains of corrective work. If results of restoration are unsuccessful, as determined by Architect, remove damaged units and replace with new units.

END OF SECTION 089119

	FIXED LOUVERS
	089119 - 1



