Copyright 2011 AIA
MasterSpec Professional
02/11

Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 142100 - ELECTRIC TRACTION ELEVATORS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

Service elevators are elevators that are used both for passenger service and for moving freight. They are passenger elevators, even though car finishes may be similar to freight elevators. The term "freight elevator" is defined in ASME A17.1/CSA B44 to mean elevators used primarily for carrying freight and inaccessible to the general public. ASME A17.1/CSA B44 does not have the same requirements for freight elevators as for passenger elevators, so using the proper terminology is important.

A. Section includes electric traction [passenger] [and] [service] elevators.

1.2 ACTION SUBMITTALS

A. Product Data: Include capacities, sizes, performances, operations, safety features, finishes, and similar information.

B. Shop Drawings:

1. Include plans, elevations, sections, and large-scale details indicating service at each landing,[ machine room layout,] coordination with building structure, relationships with other construction, and locations of equipment.

2. Indicate maximum dynamic and static loads imposed on building structure at points of support, and maximum and average power demands.

C. Samples: For exposed finishes.

1.3 INFORMATIONAL SUBMITTALS

Retain "Seismic Qualification Certificates" Paragraph below if required by seismic criteria applicable to Project. See ASCE/SEI 7 for certification requirements for equipment and components.

A. Seismic Qualification Certificates: For elevator equipment, accessories, and components, from manufacturer.

B. Manufacturer Certificates: Signed by elevator manufacturer certifying that hoistway, pit, and [machine room] [control closet] layout and dimensions, as shown on Drawings, and electrical service[ including standby power generator], as shown and specified, are adequate for elevator system being provided.

1.4 CLOSEOUT SUBMITTALS

A. Operation and Maintenance Data: For elevators to include in emergency, operation, and maintenance manuals.

B. Inspection and Acceptance Certificates and Operating Permits: As required by authorities having jurisdiction for normal, unrestricted elevator use.

Usually retain "Continuing Maintenance Proposal" Paragraph below. If continuing maintenance proposal is submitted at time of bid, include that information in the Instructions to Bidders.

C. Continuing Maintenance Proposal: Submit a continuing maintenance proposal from Installer to Owner, in the form of a standard [one-year] [two-year] [five-year] <Insert agreement period> maintenance agreement, starting on date initial maintenance service is concluded.

1.5 WARRANTY

When warranties are required, verify with Owner's counsel that warranties stated in this article are not less than remedies available to Owner under prevailing local laws.

A. Manufacturer's Special Warranty: Manufacturer agrees to repair, restore, or replace elevator work that fails in materials or workmanship within specified warranty period.

Verify available warranties and warranty periods.

1. Warranty Period: <Insert number> year(s) from date of Substantial Completion.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see SECTION 016000 "Product Requirements."

2.1 MANUFACTURERS

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed.

B. Basis-of-Design Product: Subject to compliance with requirements, provide <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

Minnesota Elevator does not offer gearless traction elevators or machine-room-less elevators and Schumacher Elevator does not offer machine-room-less elevators.

1. Fujitec America, Inc.

2. KONE Inc.

3. Minnesota Elevator, Inc.

4. Mitsubishi Electric Corporation.

5. Otis Elevator Co.

6. Schindler Elevator Corp.

7. Schumacher Elevator Co.

8. ThyssenKrupp Elevator.

9. <Insert manufacturer's name>.

2.2 PERFORMANCE REQUIREMENTS

The International Building Code (IBC) requires compliance with ASME A17.1/CSA B44. Insert other requirements, if any, of authorities having jurisdiction.

A. Regulatory Requirements: Comply with ASME A17.1/CSA B44.

Usually retain both standards in "Accessibility Requirements" Paragraph below to comply with authorities having jurisdiction and other applicable laws and regulations.

B. Accessibility Requirements: Comply with Section 407 in the U.S. Architectural & Transportation Barriers Compliance Board's ADA-ABA Accessibility Guidelines and with ICC A117.1.

Retain "Seismic Performance" Paragraph below with "Seismic Qualification Certificates" Paragraph in "Informational Submittals" Article for projects requiring seismic design. The IBC and ASCE/SEI 7 establish criteria for buildings subject to earthquake motions; the IBC requires compliance with seismic structural-design requirements of ASCE/SEI 7. Coordinate requirements with structural engineer.

C. Seismic Performance: Elevator system shall withstand the effects of earthquake motions determined according to [ASCE/SEI 7] <Insert requirement> and shall comply with elevator safety requirements for seismic risk Zone 2 or greater in ASME A17.1/CSA B44.

Affected peak velocity acceleration (Av), or seismic risk zone, is needed to design elevator to comply with ASME A17.1/CSA B44. Av could be determined by elevator manufacturer, based on Project's address.

1. Affected peak velocity acceleration (Av) for Project's location is [less than 0.10 (seismic risk Zones 0 and 1)] [greater than or equal to 0.10, but less than 0.20 (seismic risk Zone 2)] [greater than or equal to 0.20 (seismic risk Zones 3 and 4)].

ASME A17.1/CSA B44 requires earthquake equipment for Av of 0.10 or greater (seismic risk Zones 2, 3, and 4).

2. Provide earthquake equipment required by ASME A17.1/CSA B44.

ASCE/SEI 7 requires a seismic switch for elevators with a speed of 150 fpm (0.76 m/s) or greater, except for seismic design Category B and seismic design Category C with component importance factor of 1.0.

3. Provide seismic switch required by ASCE/SEI 7.

Information in three subparagraphs below is needed to design elevator to comply with ASCE/SEI 7 or the IBC. Information in first two subparagraphs is typically included in structural notes on Drawings.

Design earthquake spectral response acceleration short period (Sds) is determined by Project's location and site classification.

4. Design earthquake spectral response acceleration short period (Sds) for Project is <Insert value>.

Seismic design category is determined by Project's occupancy category and design earthquake spectral response acceleration coefficients (Sds and Sd1).

5. Project Seismic Design Category: [A] [B] [C] [D] [E] [F].

Elevator component importance factor is 1.0 unless elevator is required to function for life-safety purposes after an earthquake, or structure is in occupancy Category IV and elevators are needed for continued operation of facility or elevator failure could impair continued operation of facility, in which case the elevator component importance factor is 1.5.

6. Elevator Component Importance Factor: [1.5] [1.0].

2.3 ELEVATORS

A. Elevator System, General: Manufacturer's standard elevator systems. Unless otherwise indicated, manufacturer's standard components shall be used, as included in standard elevator systems and as required for complete system.

Copy "Elevator Description" Paragraph below and re-edit for each elevator or group of elevators.

B. Elevator Description:

1. Group Number: <Insert a different number for each group of elevators that share a group operation system>.

2. Elevator Number(s): <Insert elevator number(s) as shown on Drawings>.

3. Emergency Elevator Number(s): <Insert elevator number(s) as shown on Drawings>.

4. Service Elevator Number(s): <Insert elevator number(s) as shown on Drawings>.

5. Machine Location: [Machine room above hoistway] [Hoistway; no machine room is provided].

Delete "Machine Type" Subparagraph below for machine-room-less elevators. Usually retain geared type for speeds up to 450 fpm (2.3 m/s); retain gearless type for speeds of 500 fpm (2.5 m/s) and higher.

6. Machine Type: [Geared] [Gearless] traction.

Usually delete "Rated Load" Subparagraph below if net platform size is shown on Drawings or if inside-car dimensions are included in "Car Enclosures" Subparagraph.

7. Rated Load: [2000 lb (908 kg)] [2100 lb (953 kg)] [2500 lb (1135 kg)] [3000 lb (1362 kg)] [3500 lb (1589 kg)] [4000 lb (1816 kg)] [4500 lb (2043 kg)] [5000 lb (2270 kg)] <Insert value>.

8. Freight Loading Class for Service Elevator(s): Class A.

9. Rated Speed: [200 fpm (1.0 m/s)] [350 fpm (1.8 m/s)] [400 fpm (2.0 m/s)] [450 fpm (2.3 m/s)] [500 fpm (2.5 m/s)] [700 fpm (3.6 m/s)] [800 fpm (4.1 m/s)] [1000 fpm (5.1 m/s)] [1200 fpm (6.1 m/s)] [1400 fpm (7.1 m/s)] <Insert value>.

First two options in "Operation System" Subparagraph below are defined in ASME A17.1/CSA B44; third option is described in "Operation Systems" Article. Revise descriptions as needed to suit specific manufacturers' systems. First option is for single elevator. Second option is basic group operation suitable for two or possibly three elevators. Third option is usually best choice for three or more elevators.

10. Operation System: [Selective-collective automatic operation] [Group automatic operation] [Group automatic operation with demand-based dispatching].

11. Auxiliary Operations:

Auxiliary operations in first two subparagraphs below are specified in more detail in "Operation Systems" Article.

a. Standby power operation.

b. Battery-powered lowering.

c. Automatic dispatching of loaded car.

d. Nuisance call cancel.

Auxiliary operations in first four subparagraphs below are not applicable to single elevators.

e. [Emergency hospital] [Priority] service at [all] <Insert floor designations> floors.

Always retain first subparagraph below if group includes a service elevator.

f. Independent service for [service elevator] [one car in group] [all cars in group].

g. Loaded-car bypass.

h. Distributed parking.

12. Security Feature: [Card-reader operation] [Keyswitch operation].

Two car-control stations are an extra-cost feature that may be retained with center-opening doors for large cars with heavy peak traffic, such as in an office building, and for hospital elevators. They may also be needed for service elevators with entrances at both front and rear.

13. Dual Car-Control Stations: Provide two car-control stations[ in each elevator]; equip only one with required keyswitches if any.

14. Car Enclosures:

If standard cars are unacceptable, detail cars on Drawings or use an allowance and retain only those subparagraphs specifying car dimensions and describing items not included in allowance.

Before retaining options in "Inside Width" and "Inside Depth" subparagraphs below, verify that selected configuration complies with requirements for providing accessibility to people with disabilities and to emergency stretchers, if required. Revise descriptions of width and depth if car has more than one entrance.

a. Inside Width: [64 inches (1626 mm)] [68 inches (1727 mm)] [80 inches (2032 mm)] [92 inches (2337 mm)] <Insert dimension> from side wall to side wall.

b. Inside Depth: [51 inches (1295 mm)] [53 inches (1346 mm)] [57 inches (1448 mm)] [65 inches (1651 mm)] [87-1/2 inches (2222 mm)] [90 inches (2286 mm)] [93 inches (2362 mm)] [93-1/2 inches (2375 mm)] [96 inches (2438 mm)] [101 inches (2565 mm)] [102 inches (2591 mm)] <Insert dimension> from back wall to front wall (return panels).

c. Inside Height: [88 inches (2235 mm)] [92 inches (2337 mm)] [94 inches (2388 mm)] [100 inches (2540 mm)] [104 inches (2642 mm)] [108 inches (2743 mm)] [112 inches (2845 mm)] <Insert dimension> to underside of ceiling.

d. Front Walls (Return Panels): [Polished stainless steel, No. 8 finish] [Satin stainless steel, No. 4 finish].

e. Car Fixtures: [Polished stainless steel, No. 8 finish] [Satin stainless steel, No. 4 finish].

f. Side and Rear Wall Panels: [Enameled steel] [Plastic laminate] [Satin stainless steel, No. 4 finish].

Plastic-laminate doors are about as expensive as stainless-steel doors but are not as durable.

g. Door Faces (Interior): [Enameled steel] [Primed steel] [Polished stainless steel, No. 8 finish] [Satin stainless steel, No. 4 finish] [Plastic laminate].

h. Ceiling: [Luminous ceiling] [Polished stainless steel, No. 8 finish] [Satin stainless steel, No. 4 finish] [Reflective metallic-finish, plastic-laminate, stainless steel] [Reflective metallic-finish, plastic-laminate, bronze].

i. Handrails: [1-1/2 inches (38 mm) round] [1/2 by 2 inches (13 by 50 mm) rectangular] <Insert dimension> [mirror-polished stainless steel, No. 8 finish] [satin stainless steel, No. 4 finish], at [sides] [and] [rear] of car.

j. Floor prepared to receive carpet (specified in Section 096816 "Sheet Carpeting").

k. Floor prepared to receive resilient flooring (specified in Section 096500 "Resilient Flooring").

15. Hoistway Entrances:

a. Width: [36 inches (914 mm)] [42 inches (1067 mm)] [48 inches (1219 mm)] [54 inches (1372 mm)] <Insert dimension>.

b. Height: [84 inches (2134 mm)] [96 inches (2438 mm)] <Insert dimension>.

c. Type: [Single-speed side sliding] [Two-speed side sliding] [Single-speed center opening] [Two-speed center opening].

Copy first subparagraph below and re-edit to suit Project.

d. Frames [at First Floor] [at Basement Floors] [at Other Floors]: [Enameled steel] [Primed steel] [Polished stainless steel, No. 8 finish] [Satin stainless steel, No. 4 finish].

Copy first subparagraph below and re-edit to suit Project. Plastic-laminate doors are about as expensive as stainless-steel doors but are not as durable.

e. Doors[ and Transoms] [at First Floor] [at Basement Floors] [at Other Floors]: [Enameled steel] [Primed steel] [Polished stainless steel, No. 8 finish] [Satin stainless steel, No. 4 finish] [Plastic laminate].

Copy first subparagraph below and re-edit to suit Project.

16. Hall Fixtures [at First Floor] [at Basement Floors] [at Other Floors]: [Polished stainless steel, No. 8 finish] [Satin stainless steel, No. 4 finish].

17. Additional Requirements:

a. Provide inspection certificate in each car, mounted under acrylic cover with frame made from [polished stainless steel, No. 8 finish] [satin stainless steel, No. 4 finish].

b. Provide hooks for protective pads[ in all cars] and [one] [two] <Insert number> complete set(s) of full-height protective pads.

2.4 TRACTION SYSTEMS

A. Elevator Machines: Variable-voltage, variable-frequency, ac-type hoisting machines[ or variable-voltage dc-type hoisting machines] and solid-state power converters.

1. Limit total harmonic distortion of regenerated power to 5 percent per IEEE 519.

Consider retaining subparagraph below if retaining regenerative system and standby power operation is required. Consult Project's electrical engineer and elevator manufacturers.

2. Provide means for absorbing regenerated power when elevator system is operating on standby power.

For sprinkler-protected buildings, NFPA 13 allows sprinkler in elevator pit to be eliminated for enclosed, noncombustible shafts that do not contain combustible hydraulic fluids. Low-speed elevators can use spring buffers, but higher-speed elevators typically require hydraulic (oil) buffers to reasonably decelerate the elevator if it overshoots the bottom floor.

B. Fluid for Hydraulic Buffers: If using hydraulic buffers, use only fire-resistant fluid.

C. Machine Beams: Provide framing to support elevator hoisting machine and deflector sheaves from the building structure. Comply with Section 055000 "Metal Fabrications" for materials and fabrication.

Usually retain all three options in "Guides" Paragraph below except for high-speed elevators.

D. Guides: [Roller guides] [or] [polymer-coated, nonlubricated sliding guides]. Provide guides at top and bottom of car and counterweight frames.

Revise remaining Part 2 articles by retaining requirements further defining items retained in "Elevators" Article and deleting those not required.

2.5 OPERATION SYSTEMS

A. General: Provide manufacturer's standard microprocessor operation systems as required to provide type of operation indicated.

Basic operation systems for a single car (selective-collective operation) and for two-car groups (group automatic operation) are defined in ASME 17.1/CSA B44 and do not require further specification. For groups of three or more cars, usually retain "Group Automatic Operation with Demand-Based Dispatching" Paragraph below. System in paragraph is not necessarily reprogrammable and provides better response time than standard group automatic system and does not add much cost. Revise to suit individual Project systems.

B. Group Automatic Operation with Demand-Based Dispatching: Provide[ reprogrammable] group automatic system that assigns cars to hall calls based on a dispatching program designed to minimize passenger waiting time. System automatically adjusts to demand changes for different traffic conditions including heavy incoming, heavy two-way, heavy outgoing, and light off-hours as variations of normal two-way traffic.

Retain "Products" Subparagraph and list of manufacturers and products below to require specific products or a comparable product from other manufacturers.

1. Products: Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

Systems listed below are not necessarily equal but are generally the most sophisticated standard systems currently available from these manufacturers. Verify trade-name designations with manufacturers.

a. Fujitec America, Inc.; Millennium.

b. KONE Inc.; KCM 831.

c. Mitsubishi Electric Corporation; Sigma AI-2200C.

d. Otis Elevator Co.; Elevonic.

e. Schindler Elevator Corp.; Miconic TX.

f. ThyssenKrupp Elevator; Traflomatic.

g. <Insert manufacturer's name; product name or designation>.

Retain "Auxiliary Operations" Paragraph below to define operations retained in "Elevators" Article.

C. Auxiliary Operations: In addition to primary operation system features, provide the following operational features for elevators where indicated:

Typical auxiliary operational features are described in subparagraphs below. Delete those not required; insert others as needed. Identify elevators that require features by listing in "Elevators" Article.

Caution: There are many possible definitions of "standby (emergency) power operation." Subparagraphs below are examples only; ensure that what is to be provided is clear both here and that emergency generators have adequate capacity for specified operation.

"Single-Car Standby Power Operation" and "Single-Car Battery-Powered Lowering" subparagraphs below are for projects that require only one elevator.

1. Single-Car Standby Power Operation: On activation of standby power, car is returned to a designated floor and parked with doors open. Car can be manually put in service on standby power, either for return operation or for regular operation, by switches in control panel located at [main lobby] [fire command station] <Insert location>.

2. Single-Car Battery-Powered Lowering: If power fails and car is at a floor, it remains at that floor, opens its doors, and shuts down. If car is between floors, it is lowered to the next floor below, opens its doors, and shuts down. System includes rechargeable battery and automatic recharging system.

"Group Standby Power Operation" and "Group Battery-Powered Lowering" subparagraphs below are for projects with more than one elevator.

3. Group Standby Power Operation: On activation of standby power, cars are returned, one at a time, to a designated floor and parked with doors open. If a car cannot be returned, it is removed from the system. When all cars have been returned or removed from the system, one car can be put in service on standby power by a selector switch in control panel located at [main lobby] [fire command station] <Insert location>.

4. Group Battery-Powered Lowering: If power fails, cars that are at a floor remain at that floor, open their doors, and shut down. Cars that are between floors are lowered one at a time to the next floor below, open their doors, and shut down. System includes rechargeable battery and automatic recharging system.

Always retain "Independent Service" Subparagraph below for service elevators that are part of a group.

5. Independent Service: Keyswitch in car-control station removes car from group operation and allows it to respond only to car calls.

If retaining "remote switch" option in "(Emergency Hospital) (Priority) Service" Subparagraph below, show location on Drawings. Note that there are no standard definitions for "emergency hospital service" and "priority service."

6. [Emergency Hospital] [Priority] Service: Service is initiated by a [keyswitch] [card reader] [remote switch] at designated floors. One elevator is removed from group operation and directed to the floor where service was initiated. Car is placed in operation by selecting a floor and pressing door close button or by operating keyswitch to put car in independent service. After responding to floor selected or being removed from independent service, car is returned to group operation.

If retaining "Security Feature" Paragraph below, indicate in "Elevators" Article which elevators require security feature.

D. Security Feature: Security feature shall not affect emergency firefighters' service.

1. Card-Reader Operation: System uses card readers at car-control stations to authorize calls. Security system determines which landings and at what times calls require authorization by card reader. [Allow space as indicated for card reader in car] [Provide stripe-swipe card reader integral with each car-control station].

a. Security access system equipment is [specified in Section 281300 "Access Control."] [not in the Contract.]

"Keyswitch Operation" Subparagraph below describes a simple security feature.

2. Keyswitch Operation: Push buttons are activated and deactivated by security keyswitches at car-control stations.

2.6 DOOR REOPENING DEVICES

Device in "Infrared Array" Paragraph below is standard with most manufacturers; delete paragraph and insert another if required.

A. Infrared Array: Provide door reopening device with uniform array of 36 or more microprocessor-controlled, infrared light beams projecting across car entrance. Interruption of one or more light beams shall cause doors to stop and reopen.

Generally retain "Nudging Feature" Paragraph below to minimize elevator delay; feature may be unnecessary for low-rise elevators.

B. Nudging Feature: After car doors are prevented from closing for predetermined adjustable time, through activating door reopening device, a loud buzzer shall sound and doors shall begin to close at reduced kinetic energy.

2.7 CAR ENCLOSURES

Removable wall panels are replaceable with little downtime and allow the car, with finished wall panels removed, to be used during construction. Cars with nonremovable panels are less expensive. Removable roof can be useful for moving large objects; before retaining, verify availability and cost.

A. General: Provide [enameled-steel car enclosures to receive removable] [steel-framed car enclosures with nonremovable] wall panels, with [removable ]car roof, access doors, power door operators, and ventilation.

1. Provide standard railings complying with ASME A17.1/CSA B44 on car tops where required by ASME A17.1/CSA B44.

B. Materials and Finishes: Manufacturer's standards, but not less than the following:

1. Enameled-Steel Wall Panels: Flush, hollow-metal construction; fabricated from cold-rolled steel sheet. Provide with factory-applied enamel finish; colors as selected by Architect from manufacturer's full range.

2. Stainless-Steel Wall Panels: Flush, hollow-metal construction; fabricated from stainless-steel sheet.

Particleboard and adhesive used for laminating panels in "Plastic-Laminate Wall Panels" Subparagraph below generally contain urea formaldehyde. If low-emitting materials are required for LEED-NC, LEED-CI, or LEED-CS Credit IEQ 4.4 or for LEED for Schools Credit IEQ 4, it is better to specify another wall panel finish, such as metal, rather than trying to specify plastic-laminate wall panels that will comply with ASME A17.1/CSA B44 and are made without urea formaldehyde.

3. Plastic-Laminate Wall Panels: Plastic laminate adhesively applied to [1/2-inch (13-mm) fire-retardant-treated particleboard] [manufacturer's standard honeycomb core] with[ plastic-laminate panel backing and] manufacturer's standard protective edge trim. Panels have a flame-spread index of [25] [75] or less, when tested according to ASTM E 84. Plastic-laminate color, texture, and pattern as selected by Architect from [plastic-laminate] [elevator] manufacturer's full range.

4. Enameled-Steel Doors: Flush, hollow-metal construction; fabricated from cold-rolled steel sheet. Provide with factory-applied enamel finish; colors as selected by Architect from manufacturer's full range.

5. Stainless-Steel Doors: Flush, hollow-metal construction; fabricated [from stainless-steel sheet] [or] [by laminating stainless-steel sheet to exposed faces and edges of enameled cold-rolled steel doors using adhesive that fully bonds metal to metal without telegraphing or oil-canning].

6. Plastic-Laminate Doors: Flush, hollow-metal construction; fabricated by laminating plastic laminate to exposed faces of enameled cold-rolled steel doors and covering edges with protective edge trim[ matching return panels]. Plastic-laminate color, texture, and pattern as selected by Architect from [plastic-laminate] [elevator] manufacturer's full range.

7. Sight Guards: Provide sight guards on car doors.

8. Sills: Extrudedaluminum, with grooved surface, 1/4 inch (6.4 mm) thick.

9. Luminous Ceiling: Fluorescent light fixtures and ceiling panels of translucent acrylic or other permanent rigid plastic.

Ceilings in "(Metal) (Metallic-Finish, Plastic-Laminate) Ceiling" Subparagraph below are offered by some manufacturers. Before retaining options, verify availability with manufacturers.

10. [Metal] [Metallic-Finish, Plastic-Laminate] Ceiling: Flush panels, with [incandescent downlights in the center of] [four low-voltage downlights in] each panel.[ Align ceiling panel joints with joints between wall panels.]

11. Handrails: Manufacturer's standard handrails, of shape, metal, and finish indicated.

2.8 HOISTWAY ENTRANCES

A. Hoistway Entrance Assemblies: Manufacturer's standard horizontal-sliding, door-and-frame hoistway entrances complete with track systems, hardware, sills, and accessories. Frame size and profile shall accommodate hoistway wall construction.

1. Where gypsum board wall construction is indicated, frames shall be self-supporting with reinforced head sections.

Note that elevator door and frame assemblies do not require positive-pressure testing because sliding doors cannot form an adequate seal to pass a positive-pressure test.

B. Fire-Rated Hoistway Entrance Assemblies: Door and frame assemblies shall comply with NFPA 80 and be listed and labeled by a testing and inspecting agency acceptable to authorities having jurisdiction based on testing at as close-to-neutral pressure as possible according to [NFPA 252] [or] [UL 10B].

1. Fire-Protection Rating: [1 hour] [1-1/2 hours] <Insert rating>[ with 30-minute temperature rise of 450 deg F (250 deg C)].

C. Materials and Fabrication: Manufacturer's standards, but not less than the following:

1. Enameled-Steel Frames: Formed from cold- or hot-rolled steel sheet. Provide with factory-applied enamel finish; colors as selected by Architect from manufacturer's full range.

2. Stainless-Steel Frames: Formed from stainless-steel sheet.

3. Star of Life Symbol: Identify emergency elevators with star of life symbol, not less than 3 inches (76 mm) high, on both inside surfaces of hoistway door frames.

4. Enameled-Steel Doors[ and Transoms]: Flush, hollow-metal construction; fabricated from cold-rolled steel sheet. Provide with factory-applied enamel finish; colors as selected by Architect from manufacturer's full range.

5. Stainless-Steel Doors[ and Transoms]: Flush, hollow-metal construction; fabricated [from stainless-steel sheet] [or] [by laminating stainless-steel sheet to exposed faces and edges of enameled cold-rolled steel doors using adhesive that fully bonds metal to metal without telegraphing or oil-canning].

6. Plastic-Laminate Doors[ and Transoms]: Flush, hollow-metal construction; fabricated by laminating plastic laminate to exposed faces of enameled cold-rolled steel doors and covering edges with protective edge trim[ matching door frames]. Plastic-laminate color, texture, and pattern as selected by Architect from [plastic-laminate] [elevator] manufacturer's full range.

7. Sight Guards: Provide sight guards on doors matching door edges.

8. Sills: Extruded aluminum, with grooved surface, 1/4 inch (6.4 mm) thick.

Retain "Nonshrink, Nonmetallic Grout" Subparagraph below for grouting door sills.

9. Nonshrink, Nonmetallic Grout: Factory-packaged, nonstaining, noncorrosive, nongaseous grout complying with ASTM C 1107/C 1107M.

2.9 SIGNAL EQUIPMENT

A. General: Provide hall-call and car-call buttons that light when activated and remain lit until call has been fulfilled. Fabricate lighted elements with [long-life lamps and acrylic or other permanent, non-yellowing translucent plastic diffusers] [or] [LEDs].

B. Car-Control Stations: Provide manufacturer's standard [recessed] [or] [semirecessed] car-control stations. Mount in return panel adjacent to car door unless otherwise indicated.

1. Provide "No Smoking" sign matching car-control station, with text and graphics as required by authorities having jurisdiction.

C. Emergency Communication System: Two-way voice communication system, with visible signal, which dials preprogrammed number of monitoring station and does not require handset use. System is contained in flush-mounted cabinet, with identification, instructions for use, and battery backup power supply.

Retain "Firefighters' Two-Way Telephone Communication Service" Paragraph below where required by authorities having jurisdiction.

D. Firefighters' Two-Way Telephone Communication Service: Provide [flush-mounted cabinet] [telephone jack] in each car and required conductors in traveling cable for firefighters' two-way telephone communication service specified in [Section 283111 "Digital, Addressable Fire-Alarm System."] [Section 283112 "Zoned (DC Loop) Fire-Alarm System."]

E. Car Position Indicator: Provide [illuminated, ]digital-type car position indicator, located above car door or above car-control station. Also, provide audible signal to indicate to passengers that car is either stopping at or passing each of the floors served. Include travel direction arrows if not provided in car-control station.

F. Hall Push-Button Stations: Provide hall push-button stations at each landing as indicated.

Possibly insert a provision for either an "In Use" signal or a digital display of car position for single elevators.

G. Hall Lanterns: Units with illuminated arrows; but provide single arrow at terminal landings. Provide[ one of] the following:

Retain one of two subparagraphs below.

1. Manufacturer's standard wall-mounted units, for mounting above entrance frames.

Retain subparagraph below if jamb-mounted lanterns are acceptable. Jamb-mounted lanterns may be invisible from some locations in elevator lobbies. Delete option if only one elevator.

2. Units mounted in both jambs of entrance frame[ for each elevator].

H. Hall Annunciator: With each hall lantern, provide audible signals indicating car arrival and direction of travel. Signals sound once for up and twice for down.

Retain "Standby Power Elevator Selector Switches" or "Fire-Command-Center Annunciator Panel" Paragraph below for elevators with standby power operation. Retain first paragraph if fire command center is not required by building code; retain option if elevator doors cannot be seen from switch location. Retain second paragraph if fire command center is required by building code.

I. Standby Power Elevator Selector Switches: Provide switches, as required by ASME A17.1/CSA B44, where indicated. Adjacent to switches, provide illuminated signal that indicates when normal power supply has failed.[ For each elevator, provide illuminated signals that indicate when they are operational and when they are at the designated emergency return level with doors open.]

J. Fire-Command-Center Annunciator Panel: Provide panel containing illuminated position indicators for each elevator, clearly labeled with elevator designation; include illuminated signal that indicates when elevator is operational and when it is at the designated emergency return level with doors open. Provide standby power elevator selector switch(es), as required by ASME A17.1/CSA B44, adjacent to position indicators. Provide illuminated signal that indicates when normal power supply has failed.

Retain "Emergency Pictorial Signs" Paragraph below if signs are not specified in another Section.

K. Emergency Pictorial Signs: Fabricate from materials matching hall push-button stations, with text and graphics as required by authorities having jurisdiction. Provide one sign at each hall push-button station unless otherwise indicated.

Insert other signals and graphics ("No Smoking," etc.) as applicable or required by authorities having jurisdiction.

2.10 FINISH MATERIALS

A. Cold-Rolled Steel Sheet: ASTM A 1008/A 1008M, commercial steel, Type B, exposed, matte finish.

B. Hot-Rolled Steel Sheet: ASTM A 1011/A 1011M, commercial steel, Type B, pickled.

C. Stainless-Steel Sheet: ASTM A 240/A 240M, Type 304.

Retain "Stainless-Steel Bars" or "Stainless-Steel Tubing" Paragraph below, or both if needed for handrails.

D. Stainless-Steel Bars: ASTM A 276, Type 304.

E. Stainless-Steel Tubing: ASTM A 554, Grade MT 304.

F. Aluminum Extrusions: ASTM B 221 (ASTM B 221M), Alloy 6063.

G. Plastic Laminate: High-pressure type complying with NEMA LD 3, Type HGS or Type HGL.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Sound Isolation: Mount rotating and vibrating equipment on vibration-isolating mounts to minimize vibration transmission to structure and structure-borne noise due to elevator system.

B. Lubricate operating parts of systems, including ropes, as recommended by manufacturers.

C. Leveling Tolerance: 1/8 inch (3 mm), up or down, regardless of load and travel direction.

D. Set sills flush with finished floor surface at landing. Fill space under sill solidly with nonshrink, nonmetallic grout.

E. Locate hall signal equipment for elevators as follows unless otherwise indicated:

Retain first subparagraph below if push-button stations are not shown on plans.

1. For groups of elevators, locate hall push-button stations between two elevators at center of group or at location most convenient for approaching passengers.

Delete first subparagraph below if using jamb-mounted lanterns.

2. Place hall lanterns either above or beside each hoistway entrance.

3. Mount hall lanterns at a minimum of 72 inches (1829 mm) above finished floor.

3.2 FIELD QUALITY CONTROL

Usually retain "Acceptance Testing" Paragraph below.

A. Acceptance Testing: On completion of elevator installation and before permitting elevator use (either temporary or permanent), perform acceptance tests as required and recommended by ASME A17.1/CSA B44 and by governing regulations and agencies.

3.3 PROTECTION

A. Temporary Use: [Limit temporary use for construction purposes to one elevator. ]Comply with the following requirements for[ each] elevator used for construction purposes:

1. Provide car with temporary enclosure, either within finished car or in place of finished car, to protect finishes from damage.

2. Provide other protective coverings, barriers, devices, signs, and procedures as needed to protect elevator and elevator equipment.

3. Engage elevator Installer to provide full maintenance service.

4. Engage elevator Installer to restore damaged work, if any, so no evidence remains of correction. Return items that cannot be refinished in the field to the shop, make required repairs and refinish entire unit, or provide new units as required.

3.4 DEMONSTRATION

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to operate[, adjust, and maintain] elevator(s).

3.5 MAINTENANCE

To avoid problems, initial maintenance service and warranty should run concurrently. Manufacturer's warranties typically cover only the cost of parts; "Initial Maintenance Service" Paragraph below covers the labor cost to replace defective, damaged, or worn parts as well as routine maintenance. Insert time period; 3 to 12 months is typical.

Verify with Owner that maintenance service is required for Project.

A. Initial Maintenance Service: Beginning at Substantial Completion, maintenance service shall include <Insert number> months' full maintenance by skilled employees of elevator Installer. Include monthly preventive maintenance, repair or replacement of worn or defective components, lubrication, cleaning, and adjusting as required for proper elevator operation at rated speed and capacity.

END OF SECTION 142100

	ELECTRIC TRACTION ELEVATORS
	142100 - 1



