Copyright 2012 AIA
MasterSpec Professional
05/12

Copyright 2012 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 149100 - FACILITY CHUTES
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section includes [waste] [and] [laundry] chutes.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product indicated.

B. Shop Drawings: For chutes. Include plans, elevations, sections, details, weights, operational clearances, and attachments to other work. Indicate method of field assembly.

1. Wiring Diagrams: Power, signal and control wiring.

1.3 INFORMATIONAL SUBMITTALS

A. Product certificates.

1.4 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

1.5 QUALITY ASSURANCE

A. Fire-Rated Door Assemblies: Assemblies complying with NFPA 80 that are listed and labeled by a testing and inspecting agency acceptable to authorities having jurisdiction, for fire ratings indicated.

1. Test Pressure: Test at atmospheric (neutral) pressure according to NFPA 252 or UL 10B.

2. Intake Door: Class B labeled; [1] [1-1/2]-hour fire rated[ with 30-minute temperature rise of 250 deg F (140 deg C)].

3. Discharge Door: Class B labeled; 1-hour fire rated[ with 30-minute temperature rise of 250 deg F (140 deg C)].

4. Access Door: Class B labeled; [1] [1-1/2]-hour fire rated[ with 30-minute temperature rise of 250 deg F (140 deg C)].

B. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

C. Standard: Provide chutes complying with NFPA 82.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain paragraph and list of manufacturers in this article. See Section 016000 "Product Requirements."

A. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

1. American Chute Systems, Inc.

2. Chutes International.

3. Midland Chutes.

4. U.S. Chutes.

5. Valiant Products, Inc.

6. Western Chutes; Div. of Buchanan Company, Inc.

7. Wilkinson Hi-Rise, LLC.

8. <Insert manufacturer's name>.

2.2 CHUTES

A. Chute Metal: [Aluminum-coated, cold-rolled, commercial steel sheet; ASTM A 463/A 463M, Type 1 with not less than T1-40 (T1M-120) coating] [Type 430 stainless steel, ASTM A 240/A 240M] [Type 304 stainless steel, ASTM A 240/A 240M].

1. Thickness: [0.060 inch (1.6 mm)] [0.075 inch (1.9 mm)].

B. Size: [24-inch (610-mm) diameter] [As indicated on Drawings] <Insert dimension>.

2.3 DOORS

A. Intake Door Assemblies: ASTM A 240/A 240M, Type 304 stainless-steel, self-closing units with positive latch and latch handle; as required to provide fire-protection[ and temperature-rise] ratings indicated; and with frame suitable for enclosing chase construction.

Generally, retain hopper-type doors for waste chutes and hinged-type doors for laundry chutes.

1. Door Type: [Hopper] [Hopper, limited access] [Side hinged, limited access, 180-degree swing, square] [Type as indicated on Drawings] <Insert description>.

2. Size: Manufacturer's standard size for door type, chute type, and diameter indicated.

3. Finish: Manufacturer's standard satin or No. 3 directional polish.

Retain locks for hopper or side-hinged, limited-access doors. Chute door locks are required by NFPA 82 if door to chute compartment is not locked.

4. Locks: Cylinder locks with keys that are removable only when cylinder is locked. For each chute, key locks [keyed alike] [to master key system]. For each door, furnish [four] <Insert number> keys.

5. Baffles: Rubber-back draft baffles at each intake.

6. Foot Operators: Hopper-type door operators that unlatch and open door when foot pedal is depressed.

7. Accessible Automatic Door Operating System: Manufacturer's standard system complying with applicable provisions in [the U.S. Architectural & Transportation Barriers Compliance Board's ADA-ABA Accessibility Guidelines] [and] [ICC/ANSI A117.1].

8. Mechanical Interlocks: Interlock system operated from discharge door to automatically lock intake doors.

Retain last subparagraph above or subparagraph below, or both, to close intake doors for system service or to limit intake to one door at a time.

9. Electrical Interlocks: Interlock system that is energized by opening one intake door; remaining doors automatically lock when system is energized.

B. Discharge-Door Assemblies: Aluminum-coated-steel doors as required to provide fire-protection[ and temperature-rise] ratings indicated; equipped with fusible links that cause doors to close in the event of fire.

1. Direct Vertical Discharge: Provide inclined, horizontally rolling, shutter-type unit.

Usually retain horizontal discharge doors for laundry chutes only.

2. Horizontal Discharge: Provide top-hinged, self-closing, hopper door with self-latching hardware; floor-mounted leg brace designed to absorb impact of material dropping against chute; and minimum NPS 2 (DN 50) drain pipe connection.

C. Heat-[ and Smoke-]Detector System: Interlock system with temperature-rise elements that locks chute doors when temperature in chute reaches a predetermined, adjustable temperature.

1. Locate smoke detector outside discharge door with solenoid to close discharge door.

D. Access Door Assemblies: Manufacturer's standard ASTM A 240/A 240M, Type 302/304 stainless-steel doors; as required to provide fire-protection[ and temperature-rise] ratings indicated; with frame suitable for enclosing chase construction; and in satin or No. 3 directional polish finish.

Indicate locations of manual control stations on Drawings.

E. Manual Control System: Control system with manual switches that lock doors of chute during shutdown hours and service operations.

2.4 ACCESSORIES

Retain first paragraph below if fire sprinklers for chutes are specified in this Section and are not specified with building fire sprinklers in Section 211313 "Wet-Pipe Sprinkler Systems"

A. Fire Sprinklers: Manufacturer's standard NPS 1/2 (DN 13) fire sprinklers ready for piping connections.

Flushing units are standard equipment but may be inadequate for chutes that handle wet trash; consider specifying sanitizing units for these applications.

B. Flushing Spray Unit: NPS 3/4 (DN 19) spray head unit located in chute above highest intake door, ready for hot-water piping connection, and with access for head and piping maintenance.

C. Sanitizing Unit: NPS 3/4 (DN 19) disinfecting and sanitizing spray head unit located in chute above highest intake door, including 1-gal. (3.8-L) tank and adjustable proportioning valve with bypass for manual control of sanitizing and flushing operation, ready for hot-water piping connection, and with access for head and piping maintenance.

D. Intake Door Baffles: Rubber baffles, 1/8 inch (3 mm) thick.

E. Sound Dampening: Manufacturer's standard [sound deadening coating on exterior of chute] [and] [sound and vibration isolator pads at floor supporting frames].

2.5 FABRICATION

A. General: Factory assemble chutes to greatest extent practical with continuously welded or lock-seamed joints without bolts, rivets, or clips projecting on chute interior. Include intake door assemblies and metal supporting framing at each floor, and chute expansion joints between each support point.

B. Roof Vent: Fabricate vent unit to extend [36 inches (910 mm)] [48 inches (1200 mm)] <Insert dimension> above roof with full-diameter, screened vent and metal safety cap or glass explosion-release cap. Fabricate with roof-deck flange, counterflashing, and clamping ring of nonferrous metal compatible with chute metal.

C. Fire Sprinklers: Comply with NFPA 13. Locate fire sprinklers at or above the top service opening of chutes, within the chute at alternate floor levels in buildings more than two stories tall, and at the lowest service level.

D. Equipment Access: Fabricate chutes with access for maintaining equipment located within the chute, such as flushing and sanitizing units, fire sprinklers, and plumbing and electrical connections.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. General: Comply with NFPA 82 requirements and with chute manufacturer's written instructions. Assemble components with tight, nonleaking joints. Anchor securely to supporting structure to withstand impact and stresses on vent units. Install chute and components to maintain fire-resistive construction of chute and enclosing chase.

B. Install chutes plumb, without offsets or obstructions that might prevent materials from free falling within chutes.

Generally, roof curbs are recommended by chute manufacturer. Detail roof-curb requirements on Drawings or insert in first paragraph below.

C. Anchor roof flanges of chute vents before installing roofing and flashing. Install chute-vent counterflashing after roofing and roof-penetration flashing are installed.

D. Intake and Discharge Doors: Interface door units with throat sections of chutes for safe, snag-resistant, sanitary depositing of materials in chutes by users.

1. Coordinate installation of foot-pedal door operator with installation of door and enclosing chase.

2. Interconnect sanitizer control with door interlock system.

E. Electrical Interlock System: Comply with applicable NECA 1 recommendations.

F. Test chute components after installation. Operate doors, locks, and interlock systems to demonstrate that hardware is adjusted and electrical wiring is connected correctly. Complete test operations before installing chase enclosures.

G. Test heat- [and smoke-]sensing devices for proper operation.

H. Operate sanitizing unit through one complete cycle of chute use and cleanup, and replenish chemicals or cleaning fluids in unit containers.

I. After completing chase enclosure, clean exposed surfaces of chute system's components. Do not remove labels of independent testing and inspecting agencies.

3.2 DEMONSTRATION

A. Demonstrate use of chute and equipment to Owner's personnel.

Retain paragraph below if applicable.

B. Demonstrate replenishment of sanitizing-unit chemicals or cleaning fluids.

END OF SECTION 149100

	FACILITY CHUTES
	149100 - 1



