Copyright 2011 AIA
MasterSpec Professional
12/11

Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 220516 - EXPANSION FITTINGS AND LOOPS FOR PLUMBING PIPING
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Metal-bellows packless expansion joints.

2. Pipe loops and swing connections.

3. Alignment guides and anchors.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product indicated.

Paragraph below is defined in Section 013300 "Submittal Procedures" as a "Delegated-Design Submittal." Retain if Work of this Section is required to withstand specific design loads and design responsibilities have been delegated to Contractor or if structural data are required as another way to verify compliance with performance requirements. Professional engineer qualifications are specified in Section 014000 "Quality Requirements."

B. Delegated-Design Submittal: For each anchor and alignment guide indicated to comply with performance requirements and design criteria, including analysis data signed and sealed by the qualified professional engineer responsible for their preparation.

1. Design Calculations: Calculate requirements for thermal expansion of piping systems and for selecting and designing expansion joints, loops, and swing connections.

2. Anchor Details: Detail fabrication of each anchor indicated. Show dimensions and methods of assembly and attachment to building structure.

3. Alignment Guide Details: Detail field assembly and attachment to building structure.

4. Schedule: Indicate type, manufacturer's number, size, material, pressure rating, end connections, and location for each expansion joint.

1.3 INFORMATIONAL SUBMITTALS

A. Welding certificates.

B. Product certificates.

1.4 CLOSEOUT SUBMITTALS

A. Maintenance data.

1.5 QUALITY ASSURANCE

Retain "Welding Qualifications" Paragraph below if shop or field welding is required. If retaining, also retain "Welding certificates" Paragraph in "Informational Submittals" Article.

A. Welding Qualifications: Qualify procedures and personnel according to the following:

Retain applicable subparagraphs below.

1. AWS D1.1/D1.1M, "Structural Welding Code - Steel."

2. ASME Boiler and Pressure Vessel Code: Section IX.

PART 2 -  PRODUCTS

2.1 PACKLESS EXPANSION JOINTS

A. Metal-Bellows Packless Expansion Joints:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Adsco Manufacturing LLC.

b. American BOA, Inc.

c. Badger Industries, Inc.

d. Expansion Joint Systems, Inc.

e. Flex Pression Ltd.

f. Flex-Hose Co., Inc.

g. Flex-Weld, Inc.

h. Flexicraft Industries.

i. Flo Fab inc.

j. Hyspan Precision Products, Inc.

k. Mason Industries, Inc.

l. Metraflex Company (The).

m. Proco Products, Inc.

n. Senior Flexonics Pathway.

o. Tozen Corporation.

p. U.S. Bellows, Inc.

q. Unaflex.

r. Unisource Manufacturing, Inc.

s. Universal Metal Hose.

t. WahlcoMetroflex.

u. <Insert manufacturer's name>.

3. Standards: ASTM F 1120 and EJMA's "Standards of the Expansion Joint Manufacturers Association, Inc."

4. Type: Circular, corrugated bellows with external tie rods.

5. Minimum Pressure Rating: [150 psig (1035 kPa)] [175 psig (1200 kPa)] <Insert value> unless otherwise indicated.

6. Configuration: [Single joint] [Single joint with base] [and] [double joint with base] class(es) unless otherwise indicated.

7. Expansion Joints for Copper Tubing: [Single] [Single- or multi] [Multi]-ply phosphor-bronze bellows, copper pipe ends, and brass shrouds.

a. End Connections for Copper Tubing NPS 2 (DN 50) and Smaller: [Solder joint] [or] [threaded].

b. End Connections for Copper Tubing NPS 2-1/2 to NPS 4 (DN 65 to DN 100): [Solder joint] [or] [threaded].

c. End Connections for Copper Tubing NPS 5 (DN 125) and Larger: Flanged.

2.2 ALIGNMENT GUIDES AND ANCHORS

A. Alignment Guides:

Indicate alignment-guide length and maximum spider travel on Drawings.

1. Description: Steel, factory-fabricated alignment guide, with bolted two-section outer cylinder and base for attaching to structure; with two-section guiding spider for bolting to pipe.

B. Anchor Materials:

1. Steel Shapes and Plates: ASTM A 36/A 36M.

2. Bolts and Nuts: ASME B18.10 or ASTM A 183, steel hex head.

3. Washers: ASTM F 844, steel, plain, flat washers.

4. Mechanical Fasteners: Insert-wedge-type stud with expansion plug anchor for use in hardened portland cement concrete, with tension and shear capacities appropriate for application.

Stainless-steel studs are available.

a. Stud: Threaded, zinc-coated carbon steel.

b. Expansion Plug: Zinc-coated steel.

c. Washer and Nut: Zinc-coated steel.

5. Chemical Fasteners: Insert-type-stud, bonding-system anchor for use with hardened portland cement concrete, with tension and shear capacities appropriate for application.

a. Bonding Material: ASTM C 881/C 881M, Type IV, Grade 3, two-component epoxy resin suitable for surface temperature of hardened concrete where fastener is to be installed.

Stainless-steel studs are available.

b. Stud: ASTM A 307, zinc-coated carbon steel with continuous thread on stud unless otherwise indicated.

c. Washer and Nut: Zinc-coated steel.

PART 3 -  EXECUTION

3.1 EXPANSION-JOINT INSTALLATION

A. Install expansion joints of sizes matching sizes of piping in which they are installed.

B. Install metal-bellows expansion joints according to EJMA's "Standards of the Expansion Joint Manufacturers Association, Inc."

3.2 PIPE LOOP AND SWING CONNECTION INSTALLATION

If retaining first paragraph below, indicate dimensions of loops and swing connections and locations of guides and anchors on Drawings.

A. Install pipe loops cold-sprung in tension or compression as required to partly absorb tension or compression produced during anticipated change in temperature.

B. Connect risers and branch connections to mains with at least [five] <Insert number> pipe fittings including tee in main.

C. Connect risers and branch connections to terminal units with at least [four] <Insert number> pipe fittings including tee in riser.

D. Connect mains and branch connections to terminal units with at least [four] <Insert number> pipe fittings including tee in main.

3.3 ALIGNMENT-GUIDE AND ANCHOR INSTALLATION

A. Install alignment guides to guide expansion and to avoid end-loading and torsional stress.

Indicate locations and number of guides on Drawings.

B. Install [one] [two] guide(s) on each side of pipe expansion fittings and loops. Install guides nearest to expansion joint not more than [four] <Insert number> pipe diameters from expansion joint.

Coordinate first paragraph below with structural Drawings if welding is included in structural work.

C. Attach guides to pipe and secure guides to building structure.

D. Install anchors at locations to prevent stresses from exceeding those permitted by ASME B31.9 and to prevent transfer of loading and stresses to connected equipment.

E. Anchor Attachments:

Coordinate first subparagraph below with structural Drawings if welding is included in structural work.

1. Anchor Attachment to Black-Steel Pipe: Attach by welding. Comply with ASME B31.9 and ASME Boiler and Pressure Vessel Code: Section IX, "Welding and Brazing Qualifications."

2. Anchor Attachment to Galvanized-Steel Pipe: Attach with pipe hangers. Use MSS SP-69, Type 42, riser clamp welded to anchor.

3. Anchor Attachment to Copper Tubing: Attach with pipe hangers. Use MSS SP-69, Type 24, U-bolts bolted to anchor.

Coordinate first paragraph below with structural Drawings if welding is included in structural work.

F. Fabricate and install steel anchors by welding steel shapes, plates, and bars. Comply with ASME B31.9 and AWS D1.1/D1.1M.

1. Anchor Attachment to Steel Structural Members: Attach by welding.

2. Anchor Attachment to Concrete Structural Members: Attach by fasteners. Follow fastener manufacturer's written instructions.

G. Use grout to form flat bearing surfaces for guides and anchors attached to concrete.

END OF SECTION 220516

	EXPANSION FITTINGS AND LOOPS FOR PLUMBING PIPING
	220516 - 1



