Copyright 2010 AIA
MasterSpec Professional
03/10

Copyright 2010 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 220533 - HEAT TRACING FOR PLUMBING PIPING
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section includes plumbing piping heat tracing for freeze prevention, domestic hot-water-temperature maintenance, and snow and ice melting on roofs and in gutters and downspouts with the following electric heating cables:

1. Plastic insulated, series resistance.

2. Self-regulating, parallel resistance.

B. Related Requirements:

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

1. Section 210533 "Heat Tracing for Fire-Suppression Piping."

2. Section 230533 "Heat Tracing for HVAC Piping."

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product.

B. Shop Drawings: For electric heating cable.

1.3 INFORMATIONAL SUBMITTALS

A. Field quality-control reports.

B. Sample Warranty: For special warranty.

1.4 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

1.5 WARRANTY

When warranties are required, verify with Owner's counsel that warranties stated in this article are not less than remedies available to Owner under prevailing local laws.

A. Special Warranty: Manufacturer agrees to repair or replace electric heating cable that fails in materials or workmanship within specified warranty period.

Verify available warranties and warranty periods for electric heating cable. Special warranties often exclude labor.

1. Warranty Period: [Three] [Five] <Insert number> years from date of Substantial Completion.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

2.1 PLASTIC-INSULATED, SERIES-RESISTANCE HEATING CABLES

Retain this article for pipe-mounted freeze protection or for snow and ice melting on roofs and in gutters and downspouts. Some manufacturers limit use of this product to stone, ceramic tile, or concrete floors.

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Delta-Therm Corporation.

2. Easy Heat; a division of EGS Electrical Group LLC.

3. Orbit Manufacturing.

4. Pyrotenax; a brand of Tyco Thermal Controls LLC.

5. Raychem; a brand of Tyco Thermal Controls LLC.

6. WarmlyYours Inc.

7. Watts Radiant, Inc.; a subsidiary of Watts Water Technologies, Inc.

8. <Insert manufacturer's name>.

C. Comply with IEEE 515.1.

D. Heating Element: Single- or dual-stranded resistor wire. Terminate with waterproof, factory-assembled, nonheating leads with connectors at both ends.

E. Electrical Insulating Jacket: Minimum 4.0-mil (0.10-mm) Kapton with silicone, Tefzel, or polyolefin.

Outer jacket in "Cable Cover" Paragraph below is optional feature and is required for waterproof applications; verify availability with manufacturer.

F. Cable Cover: Aluminum braid[ and silicone or Hylar outer jacket].

G. Maximum Operating Temperature (Power On): [300 deg F (150 deg C)] <Insert temperature>.

H. Maximum Exposure Temperature (Power Off): [185 deg F (85 deg C)] <Insert temperature>.

I. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

If Project has more than one type or configuration of electric heating cable, delete "Capacities and Characteristics" Paragraph below and schedule on Drawings. See Evaluations for a sample schedule.

J. Capacities and Characteristics:

1. Maximum Heat Output: [6 W/ft. (19.7 W/m)] [7.5 W/ft. (24.6 W/m)] <Insert value>.

2. Piping Diameter: <Insert NPS (DN)>.

3. Number of Parallel Cables: <Insert number>.

4. Spiral Wrap Pitch: <Insert inches (mm)>.

5. Electrical Characteristics for Single-Circuit Connection:

Verify available voltages and heat-output ratings with manufacturer.

a. Volts: [120] [208] [240] [277] [480] <Insert value>.

b. Phase: <Insert value>.

c. Hertz: <Insert value>.

d. Full-Load Amperes: <Insert value>.

e. Minimum Circuit Ampacity: <Insert value>.

f. Maximum Overcurrent Protection: <Insert amperage>.

2.2 SELF-REGULATING, PARALLEL-RESISTANCE HEATING CABLES

Retain this article for pipe-mounted freeze protection, domestic hot-water-temperature maintenance, or snow and ice melting on roofs and in gutters and downspouts.

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. BriskHeat.

2. Chromalox.

3. Delta-Therm Corporation.

4. Easy Heat; a division of EGS Electrical Group LLC.

5. Nelson Heat Trace; a division of EGS Electrical Group LLC.

6. Pyrotenax; a brand of Tyco Thermal Controls LLC.

7. Raychem; a brand of Tyco Thermal Controls LLC.

8. Thermon Americas Inc.

9. Trasor Corp.

10. <Insert manufacturer's name>.

C. Comply with IEEE 515.1.

D. Heating Element: Pair of parallel [No. 16] [No. 18] AWG, [tinned] [nickel-coated], stranded copper bus wires embedded in crosslinked conductive polymer core, which varies heat output in response to temperature along its length. Terminate with waterproof, factory-assembled, nonheating leads with connectors at one end, and seal the opposite end watertight. Cable shall be capable of crossing over itself once without overheating.

E. Electrical Insulating Jacket: Flame-retardant polyolefin.

Outer jacket in "Cable Cover" Paragraph below is optional feature and is required for waterproof applications; verify availability with manufacturer.

F. Cable Cover: [Tinned-copper] [Stainless-steel] braid[ and polyolefin outer jacket with ultraviolet inhibitor].

G. Maximum Operating Temperature (Power On): [150 deg F (65 deg C)] <Insert temperature>.

Verify temperature of circulated media in freeze-protected piping in "Maximum Exposure Temperature (Power Off)" Paragraph below.

H. Maximum Exposure Temperature (Power Off): [185 deg F (85 deg C)] <Insert temperature>.

I. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

If Project has more than one type or configuration of electric heating cable, delete "Capacities and Characteristics" Paragraph below and schedule on Drawings. See Evaluations for a sample schedule.

J. Capacities and Characteristics:

1. Maximum Heat Output: [3 W/ft. (9.8 W/m)] [5 W/ft. (16.4 W/m)] [8 W/ft. (26 W/m)] [10 W/ft. (32.8 W/m)] [12 W/ft. (39.4 W/m)] <Insert value>.

2. Piping Diameter: <Insert NPS (DN)>.

3. Number of Parallel Cables: <Insert number>.

4. Spiral Wrap Pitch: <Insert inches (mm)>.

5. Electrical Characteristics for Single-Circuit Connection:

Verify available voltages and heat-output ratings with manufacturer.

a. Volts: [120] [208] [240] [277] [480] <Insert value>.

b. Phase: <Insert value>.

c. Hertz: <Insert value>.

d. Full-Load Amperes: <Insert value>.

e. Minimum Circuit Ampacity: <Insert value>.

f. Maximum Overcurrent Protection: <Insert amperage>.

2.3 CONTROLS

Retain "Pipe-Mounted Thermostats for Freeze Protection" Paragraph below to control electric heating cable for pipe-mounted freeze protection.

A. Pipe-Mounted Thermostats for Freeze Protection:

1. Remote bulb unit with adjustable temperature range from [30 to 50 deg F (minus 1 to plus 10 deg C)] <Insert temperature range>.

2. Snap action; open-on-rise, single-pole switch with minimum current rating adequate for connected cable.

3. Remote bulb on capillary, resistance temperature device, or thermistor for directly sensing pipe-wall temperature.

4. Corrosion-resistant, waterproof control enclosure.

Retain "Precipitation and Temperature Sensor for Snow Melting on Roofs and in Gutters" Paragraph below to operate electric heating cable for snow melting on roofs and in gutters.

B. Precipitation and Temperature Sensor for Snow Melting on Roofs and in Gutters:

1. [Microprocessor-based] [Automatic] control with manual on, automatic, and standby/reset switch.

2. Precipitation and temperature sensors shall sense the surface conditions of roof and gutters and shall be programmed to energize the cable as follows:

Retain and revise features in "Temperature Span," "Adjustable Delay-Off Span," "Energize Cables," and "De-Energize Cables" subparagraphs below to suit Project. Verify available features with manufacturer.

a. Temperature Span: [34 to 44 deg F (1 to 7 deg C)] <Insert temperature range>.

b. Adjustable Delay-Off Span: [30 to 90] <Insert time> minutes.

c. Energize Cables: Following [two] <Insert time>-minute delay if ambient temperature is below set point and precipitation is detected.

d. De-Energize Cables: On detection of a dry surface plus time delay.

3. Corrosion-proof and waterproof enclosure suitable for outdoor mounting, for controls and precipitation and temperature sensors.

4. Minimum 30-A contactor to energize cable or close other contactors.

Freestanding sensor can be used for snow and ice melting on roofs and in gutters.

5. Precipitation sensor shall be freestanding.

6. Provide relay with contacts to indicate operational status, on or off, for interface with central HVAC control-system workstation.

Programmable timer operates domestic hot-water-temperature-maintenance cable during occupied periods.

C. Programmable Timer for Domestic Hot-Water-Temperature Maintenance:

1. Microprocessor based.

2. Minimum of four separate schedules.

3. Minimum 24-hour battery carryover.

4. On-off-auto switch.

5. 365-day calendar with 20 programmable holidays.

6. Relays with contacts to indicate operational status, on or off, and for interface with central HVAC control-system workstation.

2.4 ACCESSORIES

A. Cable Installation Accessories: Fiberglass tape, heat-conductive putty, cable ties, silicone end seals and splice kits, and installation clips all furnished by manufacturer, or as recommended in writing by manufacturer.

Retain "Warning Labels" or "Warning Tape" Paragraph below.

B. Warning Labels: Refer to Section 220553 "Identification for Plumbing Piping and Equipment."

C. Warning Tape: Continuously printed "Electrical Tracing"; vinyl, at least 3 mils (0.08 mm) thick, and with pressure-sensitive, permanent, waterproof, self-adhesive back.

1. Width for Markers on Pipes with OD, Including Insulation, Less Than 6 Inches (150 mm): 3/4 inch (19 mm) minimum.

2. Width for Markers on Pipes with OD, Including Insulation, 6 Inches (150 mm) or Larger: 1-1/2 inches (38 mm) minimum.

PART 3 -  EXECUTION

3.1 APPLICATIONS

Applications in this article are typical uses for each type of electric heating cable. Consult manufacturers for other applications and for applications of other electric heating cables.

A. Install the following types of electric heating cable for the applications described:

1. Snow and Ice Melting on Roofs and in Gutters and Downspouts: [Plastic-insulated, series-resistance] [Self-regulating, parallel-resistance] heating cable.

2. Temperature Maintenance for Domestic Hot Water: Self-regulating, parallel-resistance heating cable.

3.2 INSTALLATION

Indicate location of controls on Drawings.

A. Install electric heating cable across expansion, construction, and control joints according to manufacturer's written instructions; use cable-protection conduit and slack cable to allow movement without damage to cable.

B. Electric Heating-Cable Installation for Snow and Ice Melting on Roofs and in Gutters and Downspouts: Install on roof and in gutters and downspouts with clips furnished by manufacturer that are compatible with roof, gutters, and downspouts.

C. Electric Heating-Cable Installation for Freeze Protection for Piping:

1. Install electric heating cables after piping has been tested and before insulation is installed.

2. Install electric heating cables according to IEEE 515.1.

3. Install insulation over piping with electric cables according to Section 220719 "Plumbing Piping Insulation."

4. Install warning tape on piping insulation where piping is equipped with electric heating cables.

D. Electric Heating-Cable Installation for Temperature Maintenance for Domestic Hot Water:

1. Install electric heating cables after piping has been tested and before insulation is installed.

2. Install insulation over piping with electric heating cables according to Section 220719 "Plumbing Piping Insulation."

3. Install warning tape on piping insulation where piping is equipped with electric heating cables.

E. Set field-adjustable switches and circuit-breaker trip ranges.

F. Ground equipment according to Section 260526 "Grounding and Bonding for Electrical Systems."

G. Connect wiring according to Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

3.3 FIELD QUALITY CONTROL

A. Perform the following tests and inspections[ with the assistance of a factory-authorized service representative]:

1. Perform tests after cable installation but before application of coverings such as insulation, wall or ceiling construction, or concrete.

2. Test cables for electrical continuity and insulation integrity before energizing.

3. Test cables to verify rating and power input. Energize and measure voltage and current simultaneously.

Retain first paragraph below for pipe-mounted freeze protection and for domestic hot-water-temperature maintenance.

B. Repeat tests for continuity, insulation resistance, and input power after applying thermal insulation on pipe-mounted cables.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

C. Cables will be considered defective if they do not pass tests and inspections.

D. Prepare test and inspection reports.

E. Remove and replace damaged heat-tracing cables.

END OF SECTION 220533

	HEAT TRACING FOR PLUMBING PIPING
	220533 - 1



