Copyright 2010 AIA
MasterSpec Professional
03/10

Copyright 2010 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 220553 - IDENTIFICATION FOR PLUMBING PIPING AND EQUIPMENT
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Equipment labels.

2. Warning signs and labels.

3. Pipe labels.

1.2 ACTION SUBMITTAL

A. Product Data: For each type of product indicated.

PART 2 -  PRODUCTS

2.1 EQUIPMENT LABELS

A. Metal Labels for Equipment:

Retain and punctuate multiple material options in first subparagraph below to allow Contractor to select most cost-effective material.

1. Material and Thickness: [Brass, 0.032-inch (0.8-mm)] [Stainless steel, 0.025-inch (0.64-mm)] [Aluminum, 0.032-inch (0.8-mm)] [or] [anodized aluminum, 0.032-inch (0.8-mm)] minimum thickness, and having predrilled or stamped holes for attachment hardware.

2. Minimum Label Size: Length and width vary for required label content, but not less than 2-1/2 by 3/4 inch (64 by 19 mm).

3. Minimum Letter Size: 1/4 inch (6.4 mm) for name of units if viewing distance is less than 24 inches (600 mm), 1/2 inch (13 mm) for viewing distances up to 72 inches (1830 mm), and proportionately larger lettering for greater viewing distances. Include secondary lettering two-thirds to three-fourths the size of principal lettering.

4. Fasteners: Stainless-steel [rivets] [rivets or self-tapping screws] [self-tapping screws].

5. Adhesive: Contact-type permanent adhesive, compatible with label and with substrate.

B. Plastic Labels for Equipment:

1. Material and Thickness: Multilayer, multicolor, plastic labels for mechanical engraving, [1/16 inch (1.6 mm)] [1/8 inch (3.2 mm)] <Insert dimension> thick, and having predrilled holes for attachment hardware.

2. Letter Color: [Black] [Blue] [Red] [White] [Yellow] <Insert color>.

3. Background Color: [Black] [Blue] [Red] [White] [Yellow] <Insert color>.

4. Maximum Temperature: Able to withstand temperatures up to 160 deg F (71 deg C).

5. Minimum Label Size: Length and width vary for required label content, but not less than 2-1/2 by 3/4 inch (64 by 19 mm).

6. Minimum Letter Size: 1/4 inch (6.4 mm) for name of units if viewing distance is less than 24 inches (600 mm), 1/2 inch (13 mm) for viewing distances up to 72 inches (1830 mm), and proportionately larger lettering for greater viewing distances. Include secondary lettering two-thirds to three-fourths the size of principal lettering.

7. Fasteners: Stainless-steel [rivets] [rivets or self-tapping screws] [self-tapping screws].

8. Adhesive: Contact-type permanent adhesive, compatible with label and with substrate.

In first paragraph below, describe required label content. The objective of labeling equipment is to coordinate it with Drawings, including plans, details, and schedules. This will allow other information, such as capacities and operating characteristics, to be obtained.

C. Label Content: Include equipment's Drawing designation or unique equipment number, Drawing numbers where equipment is indicated (plans, details, and schedules), plus the Specification Section number and title where equipment is specified.

D. Equipment Label Schedule: For each item of equipment to be labeled, on 8-1/2-by-11-inch (A4) bond paper. Tabulate equipment identification number and identify Drawing numbers where equipment is indicated (plans, details, and schedules), plus the Specification Section number and title where equipment is specified. Equipment schedule shall be included in operation and maintenance data.

2.2 WARNING SIGNS AND LABELS

A. Material and Thickness: Multilayer, multicolor, plastic labels for mechanical engraving, [1/16 inch (1.6 mm)] [1/8 inch (3.2 mm)] <Insert dimension> thick, and having predrilled holes for attachment hardware.

B. Letter Color: [Black] [Blue] [Red] [White] [Yellow] <Insert color>.

C. Background Color: [Black] [Blue] [Red] [White] [Yellow] <Insert color>.

D. Maximum Temperature: Able to withstand temperatures up to 160 deg F (71 deg C).

E. Minimum Label Size: Length and width vary for required label content, but not less than 2-1/2 by 3/4 inch (64 by 19 mm).

F. Minimum Letter Size: 1/4 inch (6.4 mm) for name of units if viewing distance is less than 24 inches (600 mm), 1/2 inch (13 mm) for viewing distances up to 72 inches (1830 mm), and proportionately larger lettering for greater viewing distances. Include secondary lettering two-thirds to three-fourths the size of principal lettering.

G. Fasteners: Stainless-steel [rivets] [rivets or self-tapping screws] [self-tapping screws].

H. Adhesive: Contact-type permanent adhesive, compatible with label and with substrate.

In paragraph below, describe required label content. The objective of labeling equipment is to coordinate it with Drawings, including plans, details, and schedules. This will allow other information, such as capacities and operating characteristics, to be obtained.

I. Label Content: Include caution and warning information, plus emergency notification instructions.

2.3 PIPE LABELS

Retain this article if these devices will identify some or all piping. Identification of piping by color-coded painting is covered in "Pipe Label Installation" Article.

Do not use pipe labels or plastic tapes for bare pipes conveying fluids at temperatures of 125 deg F (52 deg C) or higher.

A. General Requirements for Manufactured Pipe Labels: Preprinted, color-coded, with lettering indicating service, and showing flow direction.

B. Pretensioned Pipe Labels: Precoiled, semirigid plastic formed to [partially cover] [cover full] circumference of pipe and to attach to pipe without fasteners or adhesive.

C. Self-Adhesive Pipe Labels: Printed plastic with contact-type, permanent-adhesive backing.

D. Pipe Label Contents: Include identification of piping service using same designations or abbreviations as used on Drawings, pipe size, and an arrow indicating flow direction.

1. Flow-Direction Arrows: Integral with piping system service lettering to accommodate both directions, or as separate unit on each pipe label to indicate flow direction.

2. Lettering Size: At least 1-1/2 inches (38 mm) high.

PART 3 -  EXECUTION

3.1 PREPARATION

A. Clean piping and equipment surfaces of substances that could impair bond of identification devices, including dirt, oil, grease, release agents, and incompatible primers, paints, and encapsulants.

3.2 EQUIPMENT LABEL INSTALLATION

A. Install or permanently fasten labels on each major item of mechanical equipment.

B. Locate equipment labels where accessible and visible.

3.3 PIPE LABEL INSTALLATION

Retain first paragraph below to identify piping systems by color-coded painting. Labels will still be required to identify service, pipe size, and flow direction.

A. Piping Color-Coding: Painting of piping is specified in [Section 099123 "Interior Painting."] [Section 099600 "High-Performance Coatings."]

Revise first paragraph below to suit Project.

B. Locate pipe labels where piping is exposed or above accessible ceilings in finished spaces; machine rooms; accessible maintenance spaces such as shafts, tunnels, and plenums; and exterior exposed locations as follows:

1. Near each valve and control device.

2. Near each branch connection, excluding short takeoffs for fixtures and terminal units. Where flow pattern is not obvious, mark each pipe at branch.

3. Near penetrations through walls, floors, ceilings, and inaccessible enclosures.

4. At access doors, manholes, and similar access points that permit view of concealed piping.

5. Near major equipment items and other points of origination and termination.

6. Spaced at maximum intervals of [50 feet (15 m)] <Insert dimension> along each run. Reduce intervals to [25 feet (7.6 m)] <Insert dimension> in areas of congested piping and equipment.

7. On piping above removable acoustical ceilings. Omit intermediately spaced labels.

C. Pipe Label Color Schedule:

1. Low-Pressure, Compressed-Air Piping:

a. Background Color: [Black] [Blue] [Red] [White] [Yellow] <Insert color>.

b. Letter Color: [Black] [Blue] [Red] [White] [Yellow] <Insert color>.

2. Medium-Pressure, Compressed-Air Piping:

a. Background Color: [Black] [Blue] [Red] [White] [Yellow] <Insert color>.

b. Letter Color: [Black] [Blue] [Red] [White] [Yellow] <Insert color>.

3. Domestic Water Piping:

a. Background Color: [Black] [Blue] [Red] [White] [Yellow] <Insert color>.

b. Letter Color: [Black] [Blue] [Red] [White] [Yellow] <Insert color>.

4. [Sanitary Waste] [and] [Storm Drainage] Piping:

a. Background Color: [Black] [Blue] [Red] [White] [Yellow] <Insert color>.

b. Letter Color: [Black] [Blue] [Red] [White] [Yellow] <Insert color>.

END OF SECTION 220553

	IDENTIFICATION FOR PLUMBING PIPING AND EQUIPMENT
	220553 - 1



