Copyright 2011 AIA
MasterSpec Professional
03/11

Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 224216.16 - COMMERCIAL SINKS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Service basins.

2. Service sinks.

3. Utility sinks.

4. Handwash sinks.

5. Sink faucets.

6. Laminar-flow, faucet-spout outlets.

7. Supply fittings.

8. Waste fittings.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product.

B. LEED Submittals:

Retain "Product Data for Prerequisite WE 1 ( and Credit WE 3) (, Credit WE 2, and Credit WE 3)" Subparagraph below for LEED-NC, LEED-CS, and LEED for Schools for fixtures and equipment that consume water.

1. Product Data for Prerequisite WE 1[ and Credit WE 3] [, Credit WE 2, and Credit WE 3]: Documentation indicating flow and water consumption requirements.

Retain "Product Data for Prerequisite WE 1" Subparagraph below for LEED-CI for fixtures and equipment that consume water.

2. Product Data for Prerequisite WE 1: Documentation indicating flow and water consumption requirements.

Retain "Product Data for Prerequisite WE 1( and Credit WE 2)" Subparagraph below for LEED-EB for fixtures and equipment that consume water.

3. Product Data for Prerequisite WE 1[ and Credit WE 2]: Documentation indicating flow and water consumption requirements.

1.3 INFORMATIONAL SUBMITTALS

Retain "Coordination Drawings" Paragraph below if coordination is required for installation of products and materials by separate installers.

A. Coordination Drawings: Counter cutout templates for mounting of counter-mounted lavatories.

1.4 CLOSEOUT SUBMITTALS

A. Maintenance data.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see SECTION 016000 "Product Requirements."

2.1 SERVICE BASINS

Caution: Service basins in this article require a drainage piping trap under the fixture. The trap is not part of the fixture fittings.

Copy "Service Basins" Paragraph below and re-edit for each type of plastic, floor-mounted service basin required.

Insert number to complete drawing designation. Use these designations on Drawings to identify each service basin.

A. Service Basins <Insert drawing designation>: Plastic, floor mounted.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Crane Plumbing, L.L.C.

b. Ferguson Enterprises, Inc.; ProFlo Brand.

c. Florestone Products Co., Inc.

d. Mustee, E. L., & Sons, Inc.

e. Swan Corporation (The).

f. Zurn Industries, LLC; Light Commercial Specialty Plumbing Products.

g. <Insert manufacturer's name>.

3. Fixture:

a. Standard: IAPMO/ANSI Z124.6.

b. Material: [Cast polymer] <Insert material>.

c. Nominal Size: [24 by 36 by 10 inches (610 by 915 mm by 255 mm)] [36 by 36 by 10 inches (915 by 915 by 255 mm)] <Insert dimensions>.

In "Tiling Flange" Subparagraph below, verify availability if required and indicate side(s) if basin is rectangular.

d. Tiling Flange: [Not required] [On one side] [On two sides] [On three sides].

Indicate front dimension on rectangular basins if rim guard is to be only on one side.

e. Rim Guard: On [front] [all] top surfaces.

f. Color: [Not applicable] <Insert color>.

g. Drain: Grid with [NPS 2 (DN 50)] [NPS 3 (DN 80)] outlet.

4. Mounting: On floor and flush to wall.

A faucet with integral stops in shanks, vacuum breaker, hose-thread outlet, wall brace, and pail hook is recommended.

5. Faucet: <Insert sink-faucet designation from "Sink Faucets" Article>.

2.2 SERVICE SINKS

Copy "Service Sinks" Paragraph below and re-edit for each type of enameled, cast-iron, trap-standard-mounted service sink required.

Insert number to complete drawing designation. Use these designations on Drawings to identify each service sink.

A. Service Sinks <Insert drawing designation>: Enameled, cast iron, trap standard mounted.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. American Standard America.

b. Commercial Enameling Company.

c. Gerber Plumbing Fixtures LLC.

d. Kohler Co.

e. Zurn Industries, LLC; Commercial Brass and Fixtures.

f. <Insert manufacturer's name>.

3. Fixture:

a. Standard: ASME A112.19.1/CSA B45.2.

b. Type: Service sink with back.

c. Back: [Two faucet holes] [Plain].

d. Nominal Size: [22 by 18 inches (560 by 457 mm)] [24 by 20 inches (610 by 508 mm)].

e. Color: White.

f. Mounting: [NPS 2 (DN 50)] [NPS 3 (DN 80)] P-trap standard with grid strainer inlet, cleanout, and floor flange.

g. Rim Guard: On front and sides.

A faucet with integral stops in shanks, vacuum breaker, hose-thread outlet, and pail hook is recommended. If retaining "Plain" option in "Back" Subparagraph above, specify a wall-mounted faucet below and include a wall brace.

4. Faucet: <Insert sink-faucet designation from "Sink Faucets" Article>.

5. Support: ASME A112.6.1M, Type II, sink carrier.

2.3 UTILITY SINKS

Copy "Utility Sinks" Paragraph below and re-edit for each type of stainless-steel, counter-mounted utility sink required.

Insert number to complete drawing designation. Use these designations on Drawings to identify each utility sink.

A. Utility Sinks <Insert drawing designation>: Stainless steel, counter mounted.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Advance Tabco.

b. Eagle Group; Foodservice Equipment Division.

c. Elkay Manufacturing Co.

d. Griffin Products, Inc.

e. Just Manufacturing.

f. <Insert manufacturer's name>.

3. Fixture:

a. Standard: ASME A112.19.3/CSA B45.4.

b. Type: Ledge back.

c. Number of Compartments: [One] [Two] [Three].

d. Overall Dimensions: <Insert dimensions>.

e. Metal Thickness: [0.050 inch (1.3 mm)] <Insert dimension>.

Retain "Compartment" Subparagraph below for single-compartment sinks.

f. Compartment:

1) Dimensions: <Insert dimensions>.

2) Drain: [Grid with NPS 1-1/2 (DN 40) tailpiece and twist drain] [Grid with NPS 2 (DN 50) tailpiece and twist drain] [NPS 1-1/2 (DN 40) tailpiece with stopper] <Insert drain>.

3) Drain Location: [Centered in compartment] [Near back of compartment] [Near left side of compartment] [Near right side of compartment] <Insert location>.

Retain "Each Compartment" Subparagraph below for multiple-compartment sinks.

g. Each Compartment:

1) Dimensions: <Insert dimensions>.

2) Drains: [Grid with NPS 1-1/2 (DN 40) tailpiece and twist drain] [Grid with NPS 2 (DN 50) tailpiece and twist drain] [NPS 1-1/2 (DN 40) tailpiece with stopper] <Insert drain>.

3) Drain Location: [Centered in compartment] [Near back of compartment] <Insert location>.

4. Faucet(s): <Insert sink-faucet designation from "Sink Faucets" Article>.

a. Number Required: [One] [Two].

b. Mounting: On ledge.

5. Supply Fittings:

a. Standard: ASME A112.18.1/CSA B125.1.

b. Supplies: Chrome-plated brass compression stop with inlet connection matching water-supply piping type and size.

1) Operation: [Loose key] [Wheel handle] <Insert type>.

2) Risers: NPS 1/2 (DN 15), [chrome-plated, rigid-copper pipe] [chrome-plated, soft-copper flexible tube] [ASME A112.18.6, braided or corrugated stainless-steel flexible hose].

6. Waste Fittings:

a. Standard: ASME A112.18.2/CSA B125.2.

b. Trap(s):

1) Size: [NPS 1-1/2 (DN 40)] [NPS 2 (DN 50)].

Retain one of two "Material" subparagraphs below. First subparagraph is for NPS 1-1/2 or NPS 2 (DN 40 or DN 50) traps.

2) Material: Chrome-plated, [two-piece, cast-brass trap and swivel elbow with 0.032-inch- (0.83-mm-) thick brass tube to wall] [two-piece, cast-brass trap and ground-joint swivel elbow with 0.032-inch- (0.83-mm-) thick brass tube to wall] <Insert trap type>; and chrome-plated brass or steel wall flange.

Retain "Material" Subparagraph below only for NPS 1-1/2 (DN 40) traps.

3) Material: Stainless-steel, two-piece trap and swivel elbow with 0.012-inch- (0.30-mm-) thick stainless-steel tube to wall; and stainless-steel wall flange.

If retaining "Continuous Waste" Subparagraph below, show arrangement on Drawings.

c. Continuous Waste:

1) Size: [NPS 1-1/2 (DN 40)] [NPS 2 (DN 50)].

2) Material: Chrome-plated, 0.032-inch- (0.83-mm-) thick brass tube.

7. Mounting: On counter with sealant.

2.4 HANDWASH SINKS

Copy "Handwash Sinks" Paragraph below and re-edit for each type of stainless-steel, wall-mounted handwash sink required.

Insert number to complete drawing designation. Use these designations on Drawings to identify each handwash sink.

A. Handwash Sinks <Insert drawing designation>: Stainless steel, wall mounted.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Advance Tabco.

b. AERO Manufacturing Company.

c. Amtekco Industries, Inc.

d. Eagle Group; Foodservice Equipment Division.

e. Elkay Manufacturing Co.

f. Griffin Products, Inc.

g. Just Manufacturing.

h. <Insert manufacturer's name>.

3. Fixture:

a. Standards: ASME A112.19.3/CSA B45.4 and NSF/ANSI 2.

b. Type: Basin with radius corners, back for faucet, and support brackets.

c. Nominal Size: 17 by 16 by 5 inches (432 by 406 by 127 mm).

4. Faucet: <Insert sink-faucet designation from "Sink Faucets" Article>.

5. Supply Fittings: Comply with requirements in "Supply Fittings" Article.

6. Waste Fittings: Comply with requirements in "Waste Fittings" Article.

7. Support: ASME A112.6.1M, Type II, sink carrier.

2.5 SINK FAUCETS

A. NSF Standard: Comply with NSF/ANSI 61, "Drinking Water System Components - Health Effects," for faucet-spout materials that will be in contact with potable water.

Copy "Sink Faucets" Paragraph below and re-edit for each type of manual-type, single-control and two-lever-handle mixing valve sink faucet required.

Insert number to complete drawing designations. Use these designations on Drawings to identify each sink faucet.

B. Sink Faucets <Insert drawing designation>: Manual type, [single-control] [two-lever-handle] <Insert type> mixing valve.

1. Commercial, Solid-Brass Faucets:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

a. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

b. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

See discussion of faucets and manufacturers in the Evaluations.

1) American Standard America.

2) Bradley Corporation.

3) Chicago Faucets.

4) Delta Faucet Company.

5) Elkay Manufacturing Co.

6) GROHE America, Inc.

7) Just Manufacturing.

8) Kohler Co.

9) Moen Incorporated.

10) Speakman Company.

11) T & S Brass and Bronze Works, Inc.

12) Zurn Plumbing Products Group.

13) <Insert manufacturer's name>.

2. General-Duty, Solid-Brass Faucets:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

a. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

b. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1) American Standard America.

2) Bradley Corporation.

3) BrassTech Inc.

4) Central Brass Company.

5) Chicago Faucets.

6) Danze, Inc.

7) Delta Faucet Company.

8) Eljer, Inc.

9) Elkay Manufacturing Co.

10) Franke Consumer Products, Inc.

11) Gerber Plumbing Fixtures LLC.

12) Griffin Products, Inc.

13) GROHE America, Inc.

14) Hansgrohe USA.

15) Hydrotek International, Inc.

16) Intersan Manufacturing Company.

17) Just Manufacturing.

18) Kohler Co.

19) Matco-Norca.

20) Moen Incorporated.

21) Price Pfister, Inc.

22) Speakman Company.

23) T & S Brass and Bronze Works, Inc.

24) WhiteRock Corp.

25) Wolverine Brass, Inc.

26) Zurn Plumbing Products Group.

27) <Insert manufacturer's name>.

3. Copper- or Brass-Underbody Faucets:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

a. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

b. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1) American Standard America.

2) Briggs Plumbing Products, Inc.

3) Danze, Inc.

4) Delta Faucet Company.

5) Eljer, Inc.

6) Ferguson Enterprises, Inc.

7) Gerber Plumbing Fixtures LLC.

8) Matco-Norca.

9) Moen Incorporated.

10) Sterling.

11) WhiteRock Corp.

12) Wolverine Brass, Inc.

13) <Insert manufacturer's name>.

4. Standard: ASME A112.18.1/CSA B125.1.

5. General: Include hot- and cold-water indicators; coordinate faucet inlets with supplies and fixture hole punchings; coordinate outlet with spout and sink receptor.

Option in "Body Type" Subparagraph below must match fixture hole punching.

6. Body Type: [Centerset] [Widespread] [Single hole] <Insert type>.

7. Body Material: [Commercial, solid brass] [General-duty, solid brass] [Copper or brass underbody].

8. Finish: [Chrome plated] [Polished chrome plate] <Insert finish>.

First option in "Maximum Flow Rate" Subparagraph below generally applies to sinks. Second option applies to service sinks.

9. Maximum Flow Rate: [2.2 gpm (8.3 L/min.)] [4.0 gpm (15 L/min.)] <Insert value>.

10. Handle(s): [Lever] [Cross, four arm] [Wrist blade, 4 inches (102 mm)] [Elbow, 6 inches (152 mm)] [Not applicable] <Insert handles>.

11. Mounting Type: [Deck, concealed] [Deck, exposed] [Back/wall, exposed].

12. Spout Type: [Rigid, solid brass] [Rigid, solid brass with wall brace] [Swing, round tubular] [Swing, shaped tube] [Swing, solid brass] [Rigid gooseneck] [Swivel gooseneck] <Insert type>.

Retain first option in "Vacuum Breaker" Subparagraph below for service-sink and other faucets with hose-thread outlet.

13. Vacuum Breaker: [Required] [Not required] for hose outlet.

14. Spout Outlet: [Aerator] [Laminar flow] [Hose thread according to ASME B1.20.7] [Plain end] [Spray] <Insert type>.

2.6 LAMINAR-FLOW, FAUCET-SPOUT OUTLETS

Spout outlets in this article are non-aerating, produce less splashing than conventional faucet spouts, and help reduce bacteria growth.

A. NSF Standard: Comply with NSF/ANSI 61, "Drinking Water System Components - Health Effects," for faucet-spout-outlet materials that will be in contact with potable water.

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

B. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

C. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. AM Conservation Group, Inc.

2. Chronomite Laboratories, Inc.

3. NEOPERL, Inc.

4. <Insert manufacturer's name>.

D. Description: Chrome-plated brass, faucet-spout outlet that produces non-aerating, laminar stream. Include external or internal thread that mates with faucet outlet for attachment to faucets where indicated and flow-rate range that includes flow of faucet.

2.7 SUPPLY FITTINGS

A. NSF Standard: Comply with NSF/ANSI 61, "Drinking Water System Components - Health Effects," for supply-fitting materials that will be in contact with potable water.

B. Standard: ASME A112.18.1/CSA B125.1.

C. Supply Piping: Chrome-plated brass pipe or chrome-plated copper tube matching water-supply piping size. Include chrome-plated brass or stainless-steel wall flange.

D. Supply Stops: Chrome-plated brass, one-quarter-turn, ball-type or compression valve with inlet connection matching supply piping.

Retain "Wheel handle" option in "Operation" Paragraph below for one-quarter-turn, ball-type stops.

E. Operation: [Loose key] [Wheel handle] <Insert type>.

F. Risers:

1. [NPS 3/8 (DN 10)] [NPS 1/2 (DN 15)]

2. [Chrome-plated, rigid-copper pipe] [Chrome-plated, soft-copper flexible tube] [ASME A112.18.6, braided or corrugated stainless-steel flexible hose].

2.8 WASTE FITTINGS

A. Standard: ASME A112.18.2/CSA B125.2.

B. Drain: Grid type with NPS 1-1/2 (DN 40) offset and straight tailpiece.

C. Trap:

1. Size: NPS 1-1/2 (DN 40).

Retain one of two "Material" subparagraphs below.

2. Material: Chrome-plated, [two-piece, cast-brass trap and swivel elbow with 0.032-inch- (0.83-mm-) thick brass tube to wall] [two-piece, cast-brass trap and ground-joint swivel elbow with 0.032-inch- (0.83-mm-) thick brass tube to wall] [one-piece, cast-brass trap with swivel 0.029-inch- (73-mm-) thick tubular brass wall bend] <Insert trap type>; and chrome-plated brass or steel wall flange.

3. Material: Stainless-steel, two-piece trap and swivel elbow with 0.012-inch- (0.30-mm-) thick stainless-steel tube to wall; and stainless-steel wall flange.

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Examine roughing-in of water supply and sanitary drainage and vent piping systems to verify actual locations of piping connections before sink installation.

B. Examine walls, floors, and counters for suitable conditions where sinks will be installed.

C. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 INSTALLATION

A. Install sinks level and plumb according to roughing-in drawings.

B. Install supports, affixed to building substrate, for wall-hung sinks.

Indicate on Drawings those sinks that are required to be accessible.

C. Install accessible wall-mounted sinks at handicapped/elderly mounting height according to ICC/ANSI A117.1.

D. Set floor-mounted sinks in leveling bed of cement grout.

E. Install water-supply piping with stop on each supply to each sink faucet.

1. Exception: Use ball, gate, or globe valves if supply stops are not specified with sink. Comply with valve requirements specified in Section 220523 "General-Duty Valves for Plumbing Piping."

2. Install stops in locations where they can be easily reached for operation.

F. Install wall flanges or escutcheons at piping wall penetrations in exposed, finished locations. Use deep-pattern escutcheons if required to conceal protruding fittings. Comply with escutcheon requirements specified in Section 220518 "Escutcheons for Plumbing Piping."

G. Seal joints between sinks and counters, floors, and walls using sanitary-type, one-part, mildew-resistant silicone sealant. Match sealant color to fixture color. Comply with sealant requirements specified in Section 079200 "Joint Sealants."

Indicate on Drawings those sinks that are required to be accessible.

H. Install protective shielding pipe covers and enclosures on exposed supplies and waste piping of accessible sinks. Comply with requirements in Section 220719 "Plumbing Piping Insulation."

3.3 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Connect sinks with water supplies, stops, and risers, and with traps, soil, waste, and vent piping. Use size fittings required to match fixtures.

B. Comply with water piping requirements specified in Section 221116 "Domestic Water Piping."

C. Comply with soil and waste piping requirements specified in Section 221316 "Sanitary Waste and Vent Piping."

3.4 ADJUSTING

A. Operate and adjust sinks and controls. Replace damaged and malfunctioning sinks, fittings, and controls.

B. Adjust water pressure at faucets to produce proper flow.

3.5 CLEANING AND PROTECTION

A. After completing installation of sinks, inspect and repair damaged finishes.

B. Clean sinks, faucets, and other fittings with manufacturers' recommended cleaning methods and materials.

C. Provide protective covering for installed sinks and fittings.

D. Do not allow use of sinks for temporary facilities unless approved in writing by Owner.

END OF SECTION 224216.16

	COMMERCIAL SINKS
	224216.16 - 1



