Copyright 2011 AIA
MasterSpec Professional
09/11

Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 231123 - FACILITY NATURAL-GAS PIPING
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Pipes, tubes, and fittings.

2. Piping specialties.

3. Piping and tubing joining materials.

4. Valves.

5. Pressure regulators.

1.2 PERFORMANCE REQUIREMENTS

A. Minimum Operating-Pressure Ratings:

1. Piping and Valves: [100 psig (690 kPa)] <Insert value> minimum unless otherwise indicated.

2. Service Regulators: [65 psig (450 kPa)] [100 psig (690 kPa)] <Insert value> minimum unless otherwise indicated.

Retain one of first two paragraphs below.

B. Natural-Gas System Pressure within Buildings: [0.5 psig (3.45 kPa) or less] [More than 0.5 psig (3.45 kPa) but not more than 2 psig (13.8 kPa)] <Insert pressure range>.

C. Natural-Gas System Pressures within Buildings: Two pressure ranges. Primary pressure is more than 0.5 psig (3.45 kPa) but not more than 2 psig (13.8 kPa), and is reduced to secondary pressure of 0.5 psig (3.45 kPa) or less.

D. Delegated Design: Design restraints and anchors for natural-gas piping and equipment, including comprehensive engineering analysis by a qualified professional engineer, using performance requirements and design criteria indicated.

1.3 ACTION SUBMITTALS

A. Product Data: For each type of product indicated.

B. Shop Drawings: For facility natural-gas piping layout. Include plans, piping layout and elevations, sections, and details for fabrication of pipe anchors, hangers, supports for multiple pipes, alignment guides, expansion joints and loops, and attachments of the same to building structure. Detail location of anchors, alignment guides, and expansion joints and loops.

Paragraph below is defined in Section 013300 "Submittal Procedures" as a "Delegated-Design Submittal." Retain if Work of this Section is required to withstand specific design loads and design responsibilities have been delegated to Contractor or if structural data are required as another way to verify compliance with performance requirements. Professional engineer qualifications are specified in Section 014000 "Quality Requirements."

C. Delegated-Design Submittal: For natural-gas piping and equipment indicated to comply with performance requirements and design criteria, including analysis data signed and sealed by the qualified professional engineer responsible for their preparation.

1. Detail fabrication and assembly of seismic restraints.

2. Design Calculations: Calculate requirements for selecting seismic restraints.

1.4 INFORMATIONAL SUBMITTALS

Retain first paragraph below if retaining procedures for welder certification in "Quality Assurance" Article.

A. Welding certificates.

B. Field quality-control reports.

1.5 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

1.6 QUALITY ASSURANCE

Retain one or both of first two paragraphs below for welding supports. Retain first for welded piping supports and retain second for welded steel pipe joints. If retaining, also retain "Welding certificates" Paragraph in "Informational Submittals" Article.

A. Steel Support Welding Qualifications: Qualify procedures and personnel according to AWS D1.1/D1.1M, "Structural Welding Code - Steel."

B. Pipe Welding Qualifications: Qualify procedures and operators according to ASME Boiler and Pressure Vessel Code.

C. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

PART 2 -  PRODUCTS

2.1 PIPES, TUBES, AND FITTINGS

This article includes examples of materials listed in NFPA 54, "National Fuel Gas Code"; and the International Fuel Gas Code, which has been jointly adopted by AGA and ICC. Coordinate piping materials in this article with piping schedules in Part 3. See "Writing Guide" Article in the Evaluations for a discussion of how this Section is organized and the most efficient way to edit this Section.

See Part 3 piping schedule articles to determine where pipes, tubes, fittings, and joining materials are applied in various services.

A. Steel Pipe: ASTM A 53/A 53M, black steel, Schedule 40, Type E or S, Grade B.

1. Malleable-Iron Threaded Fittings: ASME B16.3, Class 150, standard pattern.

2. Wrought-Steel Welding Fittings: ASTM A 234/A 234M for butt welding and socket welding.

3. Unions: ASME B16.39, Class 150, malleable iron with brass-to-iron seat, ground joint, and threaded ends.

Retain first subparagraph below for underground steel piping. Cathodic protection may be required in addition to protective coating. Coordinate with requirements in Section 264200 "Cathodic Protection."

4. Protective Coating for Underground Piping: Factory-applied, three-layer coating of epoxy, adhesive, and PE.

a. Joint Cover Kits: Epoxy paint, adhesive, and heat-shrink PE sleeves.

Tubing in first paragraph below is limited in application to 0.5 psig (3.45 kPa) and less and NPS 1 (DN 25) and smaller. Verify acceptability with authorities having jurisdiction before retaining.

B. Corrugated, Stainless-Steel Tubing: Comply with ANSI/IAS LC 1.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain first subparagraph and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. OmegaFlex, Inc.

b. Parker Hannifin Corporation; Parflex Division.

c. Titeflex.

d. Tru-Flex Metal Hose Corp.

e. <Insert manufacturer's name>.

2. Tubing: ASTM A 240/A 240M, corrugated, Series 300 stainless steel.

3. Coating: PE with flame retardant.

a. Surface-Burning Characteristics: As determined by testing identical products according to ASTM E 84 by a qualified testing agency. Identify products with appropriate markings of applicable testing agency.

1) Flame-Spread Index: [25] <Insert value> or less.

2) Smoke-Developed Index: [50] [450] <Insert value> or less.

4. Fittings: Copper-alloy mechanical fittings with ends made to fit and listed for use with corrugated stainless-steel tubing and capable of metal-to-metal seal without gaskets. Include brazing socket or threaded ends complying with ASME B1.20.1.

5. Striker Plates: Steel, designed to protect tubing from penetrations.

6. Manifolds: Malleable iron or steel with factory-applied protective coating. Threaded connections shall comply with ASME B1.20.1 for pipe inlet and corrugated tubing outlets.

7. Operating-Pressure Rating: 5 psig (34.5 kPa).

In first paragraph below, CSA B149.1 allows the use of ASTM B 837 copper tubing, which defines "Type G."

C. Annealed-Temper Copper Tube: Comply with [ASTM B 88, Type K (ASTM B 88M, Type A)] [ASTM B 88, Type L (ASTM B 88M, Type B)] [ASTM B 837, Type G].

1. Copper Fittings: ASME B16.22, wrought copper, and streamlined pattern.

Verify acceptability of fittings in first subparagraph below with authorities having jurisdiction before retaining.

2. Flare Fittings: Comply with ASME B16.26 and SAE J513.

a. Copper fittings with long nuts.

b. Metal-to-metal compression seal without gasket.

c. Dryseal threads complying with ASME B1.20.3.

Retain subparagraph below for underground copper tubing. Cathodic protection may be required in addition to protective coating. Coordinate with requirements in Section 264200 "Cathodic Protection."

3. Protective Coating for Underground Tubing: Factory-applied, extruded PE a minimum of 0.022 inch (0.56 mm) thick.

Some sizes of PE pipe may not be available in SDR 11.

D. PE Pipe: ASTM D 2513, SDR 11.

1. PE Fittings: ASTM D 2683, socket-fusion type or ASTM D 3261, butt-fusion type with dimensions matching PE pipe.

2. PE Transition Fittings: Factory-fabricated fittings with PE pipe complying with ASTM D 2513, SDR 11; and steel pipe complying with ASTM A 53/A 53M, black steel, Schedule 40, Type E or S, Grade B.

See Evaluations for discussion of service-line risers. Retain one of first two subparagraphs below for anodeless or transition service-line risers for PE pipe.

3. Anodeless Service-Line Risers: Factory fabricated and leak tested.

a. Underground Portion: PE pipe complying with ASTM D 2513, SDR 11 inlet.

b. Casing: Steel pipe complying with ASTM A 53/A 53M, Schedule 40, black steel, Type E or S, Grade B, with corrosion-protective coating covering.[ Vent casing aboveground.]

c. Aboveground Portion: PE transition fitting.

d. Outlet shall be threaded or suitable for welded connection.

e. Tracer wire connection.

f. Ultraviolet shield.

g. Stake supports with factory finish to match steel pipe casing or carrier pipe.

4. Transition Service-Line Risers: Factory fabricated and leak tested.

a. Underground Portion: PE pipe complying with ASTM D 2513, SDR 11 inlet connected to steel pipe complying with ASTM A 53/A 53M, Schedule 40, Type E or S, Grade B, with corrosion-protective coating for aboveground outlet.

b. Outlet shall be threaded or suitable for welded connection.

c. Bridging sleeve over mechanical coupling.

d. Factory-connected anode.

e. Tracer wire connection.

f. Ultraviolet shield.

g. Stake supports with factory finish to match steel pipe casing or carrier pipe.

2.2 PIPING SPECIALTIES

Detail flexible connectors on Drawings for specific gas appliances.

A. Appliance Flexible Connectors:

1. Indoor, Fixed-Appliance Flexible Connectors: Comply with ANSI Z21.24.

2. Indoor, Movable-Appliance Flexible Connectors: Comply with ANSI Z21.69.

3. Outdoor, Appliance Flexible Connectors: Comply with ANSI Z21.75.

4. Corrugated stainless-steel tubing with polymer coating.

5. Operating-Pressure Rating: 0.5 psig (3.45 kPa).

6. End Fittings: Zinc-coated steel.

7. Threaded Ends: Comply with ASME B1.20.1.

8. Maximum Length: 72 inches (1830 mm.)
Detail quick-disconnect devices on Drawings for specific gas appliances.

B. Quick-Disconnect Devices: Comply with ANSI Z21.41.

1. Copper-alloy convenience outlet and matching plug connector.

2. Nitrile seals.

3. Hand operated with automatic shutoff when disconnected.

4. For indoor or outdoor applications.

5. Adjustable, retractable restraining cable.

C. Y-Pattern Strainers:

1. Body: ASTM A 126, Class B, cast iron with bolted cover and bottom drain connection.

2. End Connections: Threaded ends for NPS 2 (DN 50) and smaller.

3. Strainer Screen: [40] [60]-mesh startup strainer, and perforated stainless-steel basket with 50 percent free area.

4. CWP Rating: 125 psig (862 kPa).

D. Weatherproof Vent Cap: Cast- or malleable-iron increaser fitting with corrosion-resistant wire screen, with free area at least equal to cross-sectional area of connecting pipe and threaded-end connection.

2.3 JOINING MATERIALS

A. Joint Compound and Tape: Suitable for natural gas.

B. Welding Filler Metals: Comply with AWS D10.12/D10.12M for welding materials appropriate for wall thickness and chemical analysis of steel pipe being welded.

C. Brazing Filler Metals: Alloy with melting point greater than 1000 deg F (540 deg C) complying with AWS A5.8/A5.8M. Brazing alloys containing more than 0.05 percent phosphorus are prohibited.

2.4 MANUAL GAS SHUTOFF VALVES

Coordinate valve materials in this article with "Underground Manual Gas Shutoff Valve Schedule" and "Aboveground Manual Gas Shutoff Valve Schedule" Articles. See "Writing Guide" Article in the Evaluations for a discussion of how this Section is organized and the most efficient way to edit this Section.

Shutoff valves for natural-gas service must comply with one or more standards. Revise this article if compliance with specific standards apply. If locking devices are required, verify that they are available from listed manufacturers.

A. See "Underground Manual Gas Shutoff Valve Schedule" and "Aboveground Manual Gas Shutoff Valve Schedule" Articles for where each valve type is applied in various services.

B. General Requirements for Metallic Valves, NPS 2 (DN 50) and Smaller: Comply with ASME B16.33.

1. CWP Rating: [125 psig (862 kPa)] <Insert pressure>.

2. Threaded Ends: Comply with ASME B1.20.1.

3. Dryseal Threads on Flare Ends: Comply with ASME B1.20.3.

4. Tamperproof Feature: Locking feature for valves indicated in "Underground Manual Gas Shutoff Valve Schedule" and "Aboveground Manual Gas Shutoff Valve Schedule" Articles.

5. Listing: Listed and labeled by an NRTL acceptable to authorities having jurisdiction for valves 1 inch (25 mm) and smaller.

6. Service Mark: Valves 1-1/4 inches (32 mm) to NPS 2 (DN 50) shall have initials "WOG" permanently marked on valve body.

Caution: Two-piece ball valves with a full or regular port are recommended for most services. One-piece ball valves have a reduced port but one fewer leak paths.

C. One-Piece, Bronze Ball Valve with Bronze Trim: MSS SP-110.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain first subparagraph and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. BrassCraft Manufacturing Company; a Masco company.

b. Conbraco Industries, Inc.; Apollo Div.

c. Lyall, R. W. & Company, Inc.

d. McDonald, A. Y. Mfg. Co.

e. Perfection Corporation; a subsidiary of American Meter Company.

f. <Insert manufacturer's name>.

2. Body: Bronze, complying with ASTM B 584.

3. Ball: Chrome-plated brass.

4. Stem: Bronze; blowout proof.

5. Seats: Reinforced TFE; blowout proof.

6. Packing: Separate packnut with adjustable-stem packing threaded ends.

7. Ends: Threaded, flared, or socket as indicated in "Underground Manual Gas Shutoff Valve Schedule" and "Aboveground Manual Gas Shutoff Valve Schedule" Articles.

8. CWP Rating: 600 psig (4140 kPa).

9. Listing: Valves NPS 1 (DN 25) and smaller shall be listed and labeled by an NRTL acceptable to authorities having jurisdiction.

10. Service: Suitable for natural-gas service with "WOG" indicated on valve body.

Where pressure drop is a concern, use full-port ball valves. For corrosive or high-temperature applications, use stainless-steel trim ball valves.

D. Two-Piece, Full-Port, Bronze Ball Valves with Bronze Trim: MSS SP-110.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain first subparagraph and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. BrassCraft Manufacturing Company; a Masco company.

b. Conbraco Industries, Inc.; Apollo Div.

c. Lyall, R. W. & Company, Inc.

d. McDonald, A. Y. Mfg. Co.

e. Perfection Corporation; a subsidiary of American Meter Company.

f. <Insert manufacturer's name>.

2. Body: Bronze, complying with ASTM B 584.

3. Ball: Chrome-plated bronze.

4. Stem: Bronze; blowout proof.

5. Seats: Reinforced TFE; blowout proof.

6. Packing: Threaded-body packnut design with adjustable-stem packing.

7. Ends: Threaded, flared, or socket as indicated in "Underground Manual Gas Shutoff Valve Schedule" and "Aboveground Manual Gas Shutoff Valve Schedule" Articles.

8. CWP Rating: 600 psig (4140 kPa).

9. Listing: Valves NPS 1 (DN 25) and smaller shall be listed and labeled by an NRTL acceptable to authorities having jurisdiction.

10. Service: Suitable for natural-gas service with "WOG" indicated on valve body.

E. Two-Piece, Regular-Port Bronze Ball Valves with Bronze Trim: MSS SP-110.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain first subparagraph and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. BrassCraft Manufacturing Company; a Masco company.

b. Conbraco Industries, Inc.; Apollo Div.

c. Lyall, R. W. & Company, Inc.

d. McDonald, A. Y. Mfg. Co.

e. Perfection Corporation; a subsidiary of American Meter Company.

f. <Insert manufacturer's name>.

2. Body: Bronze, complying with ASTM B 584.

3. Ball: Chrome-plated bronze.

4. Stem: Bronze; blowout proof.

5. Seats: Reinforced TFE.

6. Packing: Threaded-body packnut design with adjustable-stem packing.

7. Ends: Threaded, flared, or socket as indicated in "Underground Manual Gas Shutoff Valve Schedule" and "Aboveground Manual Gas Shutoff Valve Schedule" Articles.

8. CWP Rating: 600 psig (4140 kPa).

9. Listing: Valves NPS 1 (DN 25) and smaller shall be listed and labeled by an NRTL acceptable to authorities having jurisdiction.

10. Service: Suitable for natural-gas service with "WOG" indicated on valve body.

F. Bronze Plug Valves: MSS SP-78.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain first subparagraph and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Lee Brass Company.

b. McDonald, A. Y. Mfg. Co.

c. <Insert manufacturer's name>.

2. Body: Bronze, complying with ASTM B 584.

3. Plug: Bronze.

4. Ends: Threaded, socket, as indicated in "Underground Manual Gas Shutoff Valve Schedule" and "Aboveground Manual Gas Shutoff Valve Schedule" Articles.

5. Operator: Square head or lug type with tamperproof feature where indicated.

6. Pressure Class: 125 psig (862 kPa).

7. Listing: Valves NPS 1 (DN 25) and smaller shall be listed and labeled by an NRTL acceptable to authorities having jurisdiction.

8. Service: Suitable for natural-gas service with "WOG" indicated on valve body.

G. PE Ball Valves: Comply with ASME B16.40.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain first subparagraph and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Kerotest Manufacturing Corp.

b. Lyall, R. W. & Company, Inc.

c. Perfection Corporation; a subsidiary of American Meter Company.

d. <Insert manufacturer's name>.

2. Body: PE.

3. Ball: PE.

4. Stem: Acetal.

5. Seats and Seals: Nitrile.

6. Ends: Plain or fusible to match piping.

7. CWP Rating: [80 psig (552 kPa)] <Insert pressure>.

8. Operating Temperature: [Minus 20 to plus 140 deg F (Minus 29 to plus 60 deg C)] <Insert temperature range>.

9. Operator: Nut or flat head for key operation.

10. Include plastic valve extension.

11. Include tamperproof locking feature for valves where indicated on Drawings.

H. Valve Boxes:

1. Cast-iron, two-section box.

2. Top section with cover with "GAS" lettering.

3. Bottom section with base to fit over valve and barrel a minimum of 5 inches (125 mm) in diameter.

4. Adjustable cast-iron extensions of length required for depth of bury.

5. Include tee-handle, steel operating wrench with socket end fitting valve nut or flat head, and with stem of length required to operate valve.

2.5 MOTORIZED GAS VALVES

Valves in paragraph below are solenoid type and are used in natural-gas piping for automatic shutoff service when interlocked with a hazard-condition initiating device.

A. Electrically Operated Valves: Comply with UL 429.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. ASCO Power Technologies, LP; Division of Emerson.

b. Dungs, Karl, Inc.

c. Eclipse Combustion, Inc.

d. Goyen Valve Corp.; Tyco Environmental Systems.

e. Magnatrol Valve Corporation.

f. Parker Hannifin Corporation; Climate & Industrial Controls Group; Skinner Valve Div.

g. Watts Regulator Co.; Division of Watts Water Technologies, Inc.

h. <Insert manufacturer's name>.

3. Pilot operated.

4. Body: Brass or aluminum.

5. Seats and Disc: Nitrile rubber.

6. Springs and Valve Trim: Stainless steel.

7. 120-V ac, 60 Hz, Class B, continuous-duty molded coil, and replaceable.

8. NEMA ICS 6, Type 4, coil enclosure.

9. Normally closed.

10. Visual position indicator.

2.6 EARTHQUAKE VALVES

Retain one of two "Earthquake Valves" paragraphs below.

A. Earthquake Valves: Comply with ASCE 25.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Vanguard Valves, Inc.

b. <Insert manufacturer's name>.

3. Listing: Listed and labeled by an NRTL acceptable to authorities having jurisdiction.

4. Maximum Operating Pressure: 5 psig (34.5 kPa).

5. Cast-aluminum body with nickel-plated chrome steel internal parts.

6. Nitrile-rubber valve washer.

7. Sight windows for visual indication of valve position.

8. Threaded end connections complying with ASME B1.20.1.

9. Wall mounting bracket with bubble level indicator.

B. Earthquake Valves: Comply with ASCE 25.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Pacific Seismic Products, Inc.

b. <Insert manufacturer's name>.

3. Listing: Listed and labeled by an NRTL acceptable to authorities having jurisdiction.

4. Maximum Operating Pressure: [0.5 psig (3.45 kPa)] [7 psig (48 kPa)] [60 psig (414 kPa)].

5. Cast-aluminum body with stainless-steel internal parts.

6. Nitrile-rubber, reset-stem o-ring seal.

7. Valve position, open or closed, indicator.

8. Composition valve seat with clapper held by spring or magnet locking mechanism.

9. Level indicator.

10. End Connections: Threaded for valves NPS 2 (DN 50) and smaller.

2.7 PRESSURE REGULATORS

A. General Requirements:

1. Single stage and suitable for natural gas.

2. Steel jacket and corrosion-resistant components.

3. Elevation compensator.

4. End Connections: Threaded for regulators NPS 2 (DN 50) and smaller.

B. Line Pressure Regulators: Comply with ANSI Z21.80.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Actaris.

b. American Meter Company.

c. Eclipse Combustion, Inc.

d. Fisher Control Valves and Regulators; Division of Emerson Process Management.

e. Invensys.

f. Maxitrol Company.

g. Richards Industries; Jordan Valve Div.

h. <Insert manufacturer's name>.

3. Body and Diaphragm Case: Cast iron or die-cast aluminum.

4. Springs: Zinc-plated steel; interchangeable.

5. Diaphragm Plate: Zinc-plated steel.

6. Seat Disc: Nitrile rubber resistant to gas impurities, abrasion, and deformation at the valve port.

7. Orifice: Aluminum; interchangeable.

8. Seal Plug: Ultraviolet-stabilized, mineral-filled nylon.

9. Single-port, self-contained regulator with orifice no larger than required at maximum pressure inlet, and no pressure sensing piping external to the regulator.

10. Pressure regulator shall maintain discharge pressure setting downstream, and not exceed 150 percent of design discharge pressure at shutoff.

Overpressure protection device is optional feature. See Evaluations.

11. Overpressure Protection Device: Factory mounted on pressure regulator.

12. Atmospheric Vent: Factory- or field-installed, stainless-steel screen in opening if not connected to vent piping.

13. Maximum Inlet Pressure: [2 psig (13.8 kPa)] [5 psig (34.5 kPa)] [10 psig (69 kPa)] <Insert pressure>.

C. Appliance Pressure Regulators: Comply with ANSI Z21.18.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Canadian Meter Company Inc.

b. Eaton Corporation; Controls Div.

c. Harper Wyman Co.

d. Maxitrol Company.

e. SCP, Inc.

f. <Insert manufacturer's name>.

3. Body and Diaphragm Case: Die-cast aluminum.

4. Springs: Zinc-plated steel; interchangeable.

5. Diaphragm Plate: Zinc-plated steel.

6. Seat Disc: Nitrile rubber.

7. Seal Plug: Ultraviolet-stabilized, mineral-filled nylon.

8. Factory-Applied Finish: Minimum three-layer polyester and polyurethane paint finish.

9. Regulator may include vent limiting device, instead of vent connection, if approved by authorities having jurisdiction.

10. Maximum Inlet Pressure: [1 psig (6.9 kPa)] [2 psig (13.8 kPa)] [5 psig (34.5 kPa)] <Insert pressure>.

2.8 DIELECTRIC UNIONS

Unions in paragraph below are available in at least NPS 1/2 to NPS 2 (DN 15 to DN 50).

A. Dielectric Unions:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Capitol Manufacturing Company.

b. Central Plastics Company.

c. Hart Industries International, Inc.

d. Jomar International Ltd.

e. Matco-Norca, Inc.

f. McDonald, A. Y. Mfg. Co.

g. Watts Regulator Co.; a division of Watts Water Technologies, Inc.

h. Wilkins; a Zurn company.

i. <Insert manufacturer's name>.

2. Description:

a. Standard: ASSE 1079.

Revise pressure rating and temperature in first subparagraph below to suit Project, or insert other options for specific applications.

b. Pressure Rating: [125 psig (860 kPa) minimum at 180 deg F (82 deg C)] [150 psig (1035 kPa)] [250 psig (1725 kPa)].

c. End Connections: Solder-joint copper alloy and threaded ferrous.

2.9 LABELING AND IDENTIFYING

A. Detectable Warning Tape: Acid- and alkali-resistant, PE film warning tape manufactured for marking and identifying underground utilities, a minimum of 6 inches (150 mm) wide and 4 mils (0.1 mm) thick, continuously inscribed with a description of utility, with metallic core encased in a protective jacket for corrosion protection, detectable by metal detector when tape is buried up to 30 inches (750 mm) deep; colored yellow.

PART 3 -  EXECUTION

3.1 OUTDOOR PIPING INSTALLATION

A. Comply with [NFPA 54] [the International Fuel Gas Code] for installation and purging of natural-gas piping.

NFPA 54 requires a minimum of 18 inches (450 mm) of cover over buried natural-gas piping, or 12 inches (300 mm) with shielding. Pipe with less than 12 inches (300 mm) of cover must be installed in a containment conduit.

B. Install underground, natural-gas piping buried at least [36 inches (900 mm)] <Insert value> below finished grade. Comply with requirements in Section 312000 "Earth Moving" for excavating, trenching, and backfilling.

1. If natural-gas piping is installed less than 36 inches (900 mm) below finished grade, install it in containment conduit.

C. Install underground, PE, natural-gas piping according to ASTM D 2774.

D. Steel Piping with Protective Coating:

Retain first two subparagraphs below for steel pipe protected from corrosion by PE coating.

1. Apply joint cover kits to pipe after joining to cover, seal, and protect joints.

Retain one of two subparagraphs below. Verify acceptability of repaired coating systems with authorities having jurisdiction.

2. Repair damage to PE coating on pipe as recommended in writing by protective coating manufacturer.

3. Replace pipe having damaged PE coating with new pipe.

CSA B149.1 requires protective coating for Type G and Type L (Type B) copper pipe and tube installed underground.

E. Copper Tubing with Protective Coating:

Retain both subparagraphs below for copper tubing protected from corrosion by PE coating.

1. Apply joint cover kits over tubing to cover, seal, and protect joints.

2. Repair damage to PE coating on pipe as recommended in writing by protective coating manufacturer.

F. Install fittings for changes in direction and branch connections.

G. Install pressure gage [downstream] [upstream and downstream] from each service regulator. Pressure gages are specified in Section 230519 "Meters and Gages for HVAC Piping."

3.2 INDOOR PIPING INSTALLATION

A. Comply with [NFPA 54] [the International Fuel Gas Code] for installation and purging of natural-gas piping.

B. Drawing plans, schematics, and diagrams indicate general location and arrangement of piping systems. Indicated locations and arrangements are used to size pipe and calculate friction loss, expansion, and other design considerations. Install piping as indicated unless deviations to layout are approved on Coordination Drawings.

C. Arrange for pipe spaces, chases, slots, sleeves, and openings in building structure during progress of construction, to allow for mechanical installations.

D. Install piping in concealed locations unless otherwise indicated and except in equipment rooms and service areas.

E. Install piping indicated to be exposed and piping in equipment rooms and service areas at right angles or parallel to building walls. Diagonal runs are prohibited unless specifically indicated otherwise.

F. Install piping above accessible ceilings to allow sufficient space for ceiling panel removal.

G. Locate valves for easy access.

Retain first paragraph below for other than dry gas.

H. Install natural-gas piping at uniform grade of 2 percent down toward drip and sediment traps.

I. Install piping free of sags and bends.

J. Install fittings for changes in direction and branch connections.

K. Verify final equipment locations for roughing-in.

L. Comply with requirements in Sections specifying gas-fired appliances and equipment for roughing-in requirements.

M. Drips and Sediment Traps: Install drips at points where condensate may collect, including service-meter outlets. Locate where accessible to permit cleaning and emptying. Do not install where condensate is subject to freezing.

1. Construct drips and sediment traps using tee fitting with bottom outlet plugged or capped. Use nipple a minimum length of 3 pipe diameters, but not less than 3 inches (75 mm) long and same size as connected pipe. Install with space below bottom of drip to remove plug or cap.

N. Extend relief vent connections for service regulators, line regulators, and overpressure protection devices to outdoors and terminate with weatherproof vent cap.

O. Conceal pipe installations in walls, pipe spaces, utility spaces, above ceilings, below grade or floors, and in floor channels unless indicated to be exposed to view.

P. Use eccentric reducer fittings to make reductions in pipe sizes. Install fittings with level side down.

Q. Connect branch piping from top or side of horizontal piping.

R. Install unions in pipes NPS 2 (DN 50) and smaller, adjacent to each valve, at final connection to each piece of equipment.

S. Do not use natural-gas piping as grounding electrode.

T. Install strainer on inlet of each line-pressure regulator and automatic or electrically operated valve.

U. Install pressure gage [downstream] [upstream and downstream] from each line regulator. Pressure gages are specified in Section 230519 "Meters and Gages for HVAC Piping."

V. Install sleeves for piping penetrations of walls, ceilings, and floors. Comply with requirements for sleeves specified in Section 230517 "Sleeves and Sleeve Seals for HVAC Piping."

Retain first paragraph below for piping that penetrates an exterior concrete wall or concrete slab.

W. Install sleeve seals for piping penetrations of concrete walls and slabs. Comply with requirements for sleeve seals specified in Section 230517 "Sleeves and Sleeve Seals for HVAC Piping."

X. Install escutcheons for piping penetrations of walls, ceilings, and floors. Comply with requirements for escutcheons specified in Section 230518 "Escutcheons for HVAC Piping."

3.3 VALVE INSTALLATION

A. Install manual gas shutoff valve for each gas appliance ahead of corrugated stainless-steel tubing or copper connector.

B. Install underground valves with valve boxes.

C. Install regulators and overpressure protection devices with maintenance access space adequate for servicing and testing.

D. Install earthquake valves aboveground outside buildings according to listing.

E. Install anode for metallic valves in underground PE piping.

3.4 PIPING JOINT CONSTRUCTION

A. Ream ends of pipes and tubes and remove burrs.

B. Remove scale, slag, dirt, and debris from inside and outside of pipe and fittings before assembly.

C. Threaded Joints:

1. Thread pipe with tapered pipe threads complying with ASME B1.20.1.

2. Cut threads full and clean using sharp dies.

3. Ream threaded pipe ends to remove burrs and restore full inside diameter of pipe.

4. Apply appropriate tape or thread compound to external pipe threads unless dryseal threading is specified.

5. Damaged Threads: Do not use pipe or pipe fittings with threads that are corroded or damaged. Do not use pipe sections that have cracked or open welds.

D. Welded Joints:

1. Construct joints according to AWS D10.12/D10.12M, using qualified processes and welding operators.

2. Bevel plain ends of steel pipe.

3. Patch factory-applied protective coating as recommended by manufacturer at field welds and where damage to coating occurs during construction.

E. Brazed Joints: Construct joints according to AWS's "Brazing Handbook," "Pipe and Tube" Chapter.

F. Flared Joints: Cut tubing with roll cutting tool. Flare tube end with tool to result in flare dimensions complying with SAE J513. Tighten finger tight, then use wrench. Do not overtighten.

G. PE Piping Heat-Fusion Joints: Clean and dry joining surfaces by wiping with clean cloth or paper towels. Join according to ASTM D 2657.

1. Plain-End Pipe and Fittings: Use butt fusion.

2. Plain-End Pipe and Socket Fittings: Use socket fusion.

3.5 HANGER AND SUPPORT INSTALLATION

A. Install seismic restraints on piping. Comply with requirements for seismic-restraint devices specified in Section 230548 "Vibration and Seismic Controls for HVAC."

B. Comply with requirements for pipe hangers and supports specified in Section 230529 "Hangers and Supports for HVAC Piping and Equipment."

Maximum spans below are from NFPA 54 or MSS SP-69. Copper-tube sizes were adjusted to ASTM B 88 (ASTM B 88M).

C. Install hangers for horizontal steel piping with the following maximum spacing and minimum rod sizes:

1. NPS 1 (DN 25) and Smaller: Maximum span, 96 inches (2438 mm); minimum rod size, 3/8 inch (10 mm).

2. NPS 1-1/4 (DN 32): Maximum span, 108 inches (2743 mm); minimum rod size, 3/8 inch (10 mm).

3. NPS 1-1/2 and NPS 2 (DN 40 and DN 50): Maximum span, 108 inches (2743 mm); minimum rod size, 3/8 inch (10 mm).

D. Install hangers for horizontal, corrugated stainless-steel tubing with the following maximum spacing and minimum rod sizes:

1. NPS 3/8 (DN 10): Maximum span, 48 inches (1220 mm); minimum rod size, 3/8 inch (10 mm).

2. NPS 1/2 (DN 15): Maximum span, 72 inches (1830 mm); minimum rod size, 3/8 inch (10 mm).

3. NPS 3/4 (DN 20) and Larger: Maximum span, 96 inches (2440 mm); minimum rod size, 3/8 inch (10 mm).

3.6 CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings. If Drawings are explicit enough, these requirements may be reduced or omitted.

Delete first two paragraphs below if utility makes connection to its gas main, or retain one of two paragraphs and revise to suit Project.

A. Connect to utility's gas main according to utility's procedures and requirements.

B. Install natural-gas piping electrically continuous, and bonded to gas appliance equipment grounding conductor of the circuit powering the appliance according to NFPA 70.

C. Install piping adjacent to appliances to allow service and maintenance of appliances.

D. Connect piping to appliances using manual gas shutoff valves and unions. Install valve within 72 inches (1800 mm) of each gas-fired appliance and equipment. Install union between valve and appliances or equipment.

E. Sediment Traps: Install tee fitting with capped nipple in bottom to form drip, as close as practical to inlet of each appliance.

3.7 LABELING AND IDENTIFYING

Retain one of two paragraphs in this article.

A. Comply with requirements in Section 230553 "Identification for HVAC Piping and Equipment" for piping and valve identification.

B. Install detectable warning tape directly above gas piping, 12 inches (300 mm) below finished grade, except 6 inches (150 mm) below subgrade under pavements and slabs.

3.8 FIELD QUALITY CONTROL

A. Test, inspect, and purge natural gas according to [NFPA 54] [the International Fuel Gas Code] and authorities having jurisdiction.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

B. Natural-gas piping will be considered defective if it does not pass tests and inspections.

C. Prepare test and inspection reports.

3.9 OUTDOOR PIPING SCHEDULE

Retain and revise applicable piping applications. Coordinate with materials specified in Part 2. Retain multiple materials for Contractor's option.

Retain "one of" option in first paragraph below to allow Contractor to select piping materials from those retained.

A. Underground natural-gas piping shall be[ one of] the following:

PE pipe is available in NPS 1/2 to NPS 16 (DN 15 to DN 400), maximum NPS 2 (DN 50) in 1000-foot (305-m) rolls.

1. PE pipe and fittings joined by heat fusion; service-line risers with tracer wire terminated in an accessible location.

2. Steel pipe with wrought-steel fittings and welded joints. Coat pipe and fittings with protective coating for steel piping.

Practical size limit for copper is NPS 4 (DN 100) as joints are difficult to heat evenly for brazing.

3. Annealed-temper copper tube with wrought-copper fittings and brazed joints. Coat pipe and fittings with protective coating for copper tubing.

Retain "one of" option in first paragraph below to allow Contractor to select piping materials from those retained.

B. Aboveground natural-gas piping shall be[ one of] the following:

1. Steel pipe with malleable-iron fittings and threaded joints.

2. Steel pipe with wrought-steel fittings and welded joints.

Practical size limit for copper is NPS 4 (DN 100) because joints are difficult to heat evenly for brazing.

3. Annealed-temper copper tube with wrought-copper fittings and brazed joints.

C. Branch Piping in Cast-in-Place Concrete to Single Appliance: Annealed-temper copper tube with wrought-copper fittings and [brazed] [flared] joints. Install piping embedded in concrete with no joints in concrete.

Indicate extent of containment conduit on Drawings. Containment conduit is required for piping with insufficient depth of bury.

D. Containment Conduit: Steel pipe with wrought-steel fittings and welded joints. Coat pipe and fittings with protective coating for steel piping.

3.10 INDOOR PIPING SCHEDULE

Retain and revise applicable piping applications. Coordinate with materials specified in Part 2.

Retain "one of" option in first paragraph below to allow Contractor to select piping materials from those retained.

A. Aboveground, branch piping [NPS 1 (DN 25)] <Insert pipe size> and smaller shall be[ one of] the following:

Contact authorities having jurisdiction and verify approval before specifying corrugated stainless-steel tubing.

1. Corrugated stainless-steel tubing with mechanical fittings having socket or threaded ends to match adjacent piping.

2. Annealed-temper copper tube with wrought-copper fittings and [brazed] [flared] joints.

3. Steel pipe with malleable-iron fittings and threaded joints.

Retain "one of" option in first paragraph below to allow Contractor to select piping materials from those retained.

B. Aboveground, distribution piping shall be[ one of] the following:

Authorities having jurisdiction may require welded steel pipe at different sizes and pressures.

1. Steel pipe with malleable-iron fittings and threaded joints.

2. Steel pipe with wrought-steel fittings and welded joints.

Retain "one of" option in first paragraph below to allow Contractor to select piping materials from those retained.

C. Underground, below building, piping shall be[ one of] the following:

1. Steel pipe with malleable-iron fittings and threaded joints.

2. Steel pipe with wrought-steel fittings and welded joints.

Retain both paragraphs below for piping below building.

Indicate extent of containment conduit on Drawings. Containment conduit is required for piping under buildings.

D. Containment Conduit: Steel pipe with wrought-steel fittings and welded joints. Coat pipe and fittings with protective coating for steel piping.

E. Containment Conduit Vent Piping: Steel pipe with malleable-iron fittings and threaded or wrought-steel fittings with welded joints. Coat underground pipe and fittings with protective coating for steel piping.

3.11 UNDERGROUND MANUAL GAS SHUTOFF VALVE SCHEDULE

Retain and revise applicable piping applications. Coordinate with materials specified in Part 2.

A. Connections to Existing Gas Piping: Use valve and fitting assemblies made for tapping utility's gas mains and listed by an NRTL.

In paragraph below, PE valve option can only be applied in PE piping; bronze plug valve option can be applied in PE, steel, or copper piping.

B. Underground: [PE] [Bronze plug] valves.

3.12 ABOVEGROUND MANUAL GAS SHUTOFF VALVE SCHEDULE

Retain and revise applicable piping applications. Coordinate with materials specified in Part 2.

Retain "one of" option in first paragraph below to allow Contractor to select piping materials from those retained.

A. Valves for pipe sizes NPS 2 (DN 50) and smaller at service meter shall be[ one of] the following:

1. One-piece, bronze ball valve with bronze trim.

2. Two-piece, [full] [regular]-port, bronze ball valves with bronze trim.

3. Bronze plug valve.

Retain "one of" option in first paragraph below to allow Contractor to select piping materials from those retained.

B. Distribution piping valves for pipe sizes NPS 2 (DN 50) and smaller shall be[ one of] the following:

1. One-piece, bronze ball valve with bronze trim.

2. Two-piece, [full] [regular]-port, bronze ball valves with bronze trim.

3. Bronze plug valve.

Retain "one of" option in paragraph below to allow Contractor to select piping materials from those retained.

C. Valves in branch piping for single appliance shall be[ one of] the following:

1. One-piece, bronze ball valve with bronze trim.

2. Two-piece, [full] [regular]-port, bronze ball valves with bronze trim.

3. Bronze plug valve.

END OF SECTION 231123

	FACILITY NATURAL-GAS PIPING
	231123 - 1



