Copyright 2011 AIA
MasterSpec Professional
09/11

Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 232123 - HYDRONIC PUMPS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Close-coupled, in-line centrifugal pumps.

2. Close-coupled, end-suction centrifugal pumps.

3. Separately coupled, horizontally mounted, in-line centrifugal pumps.

4. Separately coupled, vertically mounted, in-line centrifugal pumps.

5. Separately coupled, base-mounted, end-suction centrifugal pumps.

6. Automatic condensate pump units.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of pump.

B. Shop Drawings: For each pump.

1. Show pump layout and connections.

2. Include setting drawings with templates for installing foundation and anchor bolts and other anchorages.

3. Include diagrams for power, signal, and control wiring.

1.3 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

2.1 CLOSE-COUPLED, IN-LINE CENTRIFUGAL PUMPS

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Armstrong Pumps Inc.

2. Aurora Pump; Division of Pentair Pump Group.

3. Crane Pumps & Systems.

4. Flowserve Corporation.

5. Grundfos Pumps Corporation.

6. ITT Corporation; Bell & Gossett.

7. Mepco, LLC.

8. PACO Pumps.

9. Patterson Pump Co.; a subsidiary of the Gorman-Rupp Co.

10. Peerless Pump Company.

11. TACO Incorporated.

12. Thrush Company Inc.

13. <Insert manufacturer's name>.

C. Description: Factory-assembled and -tested, centrifugal, overhung-impeller, close-coupled, in-line pump as defined in HI 1.1-1.2 and HI 1.3; designed for installation with pump and motor shafts mounted horizontally or vertically.

D. Pump Construction:

1. Casing: Radially split, cast iron, with threaded gage tappings at inlet and outlet[, replaceable bronze wear rings,] and threaded [companion-flange] [union-end] connections.

2. Impeller: ASTM B 584, cast bronze; statically and dynamically balanced, keyed to shaft, and secured with a locking cap screw. For constant-speed pumps, trim impeller to match specified performance.

3. Pump Shaft: [Steel, with copper-alloy shaft sleeve] [Stainless steel].

Retain one of two "Seal" subparagraphs below. Retain first subparagraph for service temperatures above 200 deg F (93 deg C); retain second subparagraph for service temperatures 200 deg F (93 deg C) or lower. In first subparagraph, retain "Buna-N" option for temperature rating of 225 deg F (107 deg C); retain "EPT" option for 250 deg F (120 deg C) and for glycol solutions.

4. Seal: Mechanical seal consisting of carbon rotating ring against a ceramic seat held by a stainless-steel spring, and [Buna-N] [EPT] bellows and gasket. Include water slinger on shaft between motor and seal.

5. Seal: Packing seal consisting of stuffing box with a minimum of four rings of graphite-impregnated braided yarn with bronze lantern ring between center two graphite rings, and bronze packing gland.

6. Pump Bearings: [Permanently lubricated ball bearings] [Oil lubricated; bronze-journal or thrust type].

E. Motor: Single speed and rigidly mounted to pump casing.

1. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

Default motor characteristics are specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

2. Comply with NEMA designation, temperature rating, service factor, and efficiency requirements for motors specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

Verify enclosure types with manufacturer of specified equipment. Delete "Enclosure" Subparagraph below if included in schedule on Drawings or in "Capacities and Characteristics" Paragraph below.

a. Enclosure: [Open, dripproof] [Totally enclosed, fan cooled] [Totally enclosed, air over] [Open, externally ventilated] [Totally enclosed, nonventilated] [Severe duty] [Explosion proof] [Dust-ignition-proof machine].

Retain "Enclosure Materials," "Motor Bearings," "Unusual Service Conditions," "Efficiency," "NEMA Design," and "Service Factor" subparagraphs below if options are available from pump manufacturers and are different from default requirements specified in Section 230513 "Common Motor Requirements for HVAC Equipment." Consider each subparagraph and retain only those that vary from default requirements.

b. Enclosure Materials: [Cast iron] [Cast aluminum] [Rolled steel].

Permanently lubricated ball bearings are available up through 5 hp. Larger motors have grease-lubricated ball bearings.

c. Motor Bearings: [Permanently lubricated] [Grease-lubricated] ball bearings.

d. Unusual Service Conditions:

1) Ambient Temperature: <Insert deg C>.

2) Altitude: <Insert feet (meters)> above sea level.

3) High humidity.

4) <Insert conditions>.

e. Efficiency: Premium efficient.

f. NEMA Design: <Insert designation>.

g. Service Factor: <Insert value>.

If Project has more than one type or configuration of close-coupled, in-line centrifugal pump, delete "Capacities and Characteristics" Paragraph below and schedule pumps on Drawings.

F. Capacities and Characteristics:

1. Capacity: <Insert gpm (L/s)>.

2. Total Dynamic Head: <Insert feet (kPa)>.

3. Maximum Operating Pressure: [175 psig (1204 kPa)] [250 psig (1720 kPa)].

4. Maximum Continuous Operating Temperature: [225 deg F (107 deg C)] [250 deg F (120 deg C)].

5. Inlet and Outlet Size: <Insert NPS (DN)>.

6. Impeller Size: <Insert inches (mm)>.

7. Motor Speed: <Insert rpm>.

8. Motor Horsepower: <Insert value>.

9. Electrical Characteristics:

a. Volts: [120] [240] [208] [460] <Insert value>.

b. Phase: [Single] [Three].

c. Hertz: 60.

d. Full-Load Amperes: <Insert value>.

e. Minimum Circuit Ampacity: <Insert value>.

f. Maximum Overcurrent Protection: <Insert amperage>.

2.2 CLOSE-COUPLED, END-SUCTION CENTRIFUGAL PUMPS

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. American-Marsh Pumps.

2. Armstrong Pumps Inc.

3. Aurora Pump; Division of Pentair Pump Group.

4. Buffalo Pumps, Inc.

5. Crane Pumps & Systems.

6. Flowserve Corporation.

7. ITT Corporation; Bell & Gossett.

8. ITT Corporation; Goulds Pumps.

9. Lancaster Pump.

10. Mepco, LLC.

11. PACO Pumps.

12. Patterson Pump Co.; a subsidiary of the Gorman-Rupp Co.

13. Peerless Pump Company.

14. Scot Pump; Div. of Ardox Corp.

15. TACO Incorporated.

16. Thrush Company Inc.

17. <Insert manufacturer's name>.

C. Description: Factory-assembled and -tested, centrifugal, overhung-impeller, close-coupled, end-suction pump as defined in HI 1.1-1.2 and HI 1.3; designed for installation with pump and motor shafts mounted horizontally.

D. Pump Construction:

1. Casing: Radially split, cast iron, with[ replaceable bronze wear rings,] drain plug at bottom and air vent at top of volute, threaded gage tappings at inlet and outlet, and [threaded companion-flange] [flanged] connections.

2. Impeller: ASTM B 584, cast bronze; statically and dynamically balanced, keyed to shaft, and secured with a locking cap screw. For constant-speed pumps, trim impeller to match specified performance.

3. Pump Shaft: [Steel, with copper-alloy shaft sleeve] [Stainless steel].

In "Mechanical Seal" Subparagraph below, retain "Buna-N" option for temperature rating of 225 deg F (107 deg C); retain "EPT" option for 250 deg F (120 deg C).

4. Mechanical Seal: Carbon rotating ring against a ceramic seat held by a stainless-steel spring, and [Buna-N] [EPT] bellows and gasket. Include water slinger on shaft between motor and seal.

5. Pump Bearings: [Permanently lubricated ball bearings] [Oil lubricated; bronze-journal or thrust type].

E. Motor: Single speed and rigidly mounted to pump casing with integral pump support.

1. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

Default motor characteristics are specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

2. Comply with NEMA designation, temperature rating, service factor, and efficiency requirements for motors specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

Verify enclosure types with manufacturer of specified equipment. Delete "Enclosure" Subparagraph below if included in schedule on Drawings or in "Capacities and Characteristics" Paragraph below.

a. Enclosure: [Open, dripproof] [Totally enclosed, fan cooled] [Totally enclosed, air over] [Open, externally ventilated] [Totally enclosed, nonventilated] [Severe duty] [Explosion proof] [Dust-ignition-proof machine].

Retain "Enclosure Materials," "Motor Bearings," "Unusual Service Conditions," "Efficiency," "NEMA Design," and "Service Factor" subparagraphs below if options are available from pump manufacturers and are different from default requirements specified in Section 230513 "Common Motor Requirements for HVAC Equipment." Consider each subparagraph and retain only those that vary from default requirements.

b. Enclosure Materials: [Cast iron] [Cast aluminum] [Rolled steel].

Permanently lubricated ball bearings are available up through 5 hp. Larger motors have grease-lubricated ball bearings.

c. Motor Bearings: [Permanently lubricated] [Grease-lubricated] ball bearings.

d. Unusual Service Conditions:

1) Ambient Temperature: <Insert deg C>.

2) Altitude: <Insert feet (meters)> above sea level.

3) High humidity.

4) <Insert conditions>.

e. Efficiency: Premium efficient.

f. NEMA Design: <Insert designation>.

g. Service Factor: <Insert value>.

If Project has more than one type or configuration of close-coupled, end-suction centrifugal pump, delete "Capacities and Characteristics" Paragraph below and schedule pumps on Drawings.

F. Capacities and Characteristics:

1. Capacity: <Insert gpm (L/s)>.

2. Total Dynamic Head: <Insert feet (kPa)>.

3. Maximum Operating Pressure: 175 psig (1204 kPa).

4. Maximum Continuous Operating Temperature: [225 deg F (107 deg C)] [250 deg F (120 deg C)].

5. Inlet and Outlet Size: <Insert NPS (DN)>.

6. Impeller Size: <Insert inches (mm)>.

7. Motor Speed: <Insert rpm>.

8. Motor Horsepower: <Insert value>.

9. Electrical Characteristics:

a. Volts: [120] [240] [208] [460] <Insert value>.

b. Phase: [Single] [Three].

c. Hertz: 60.

d. Full-Load Amperes: <Insert value>.

e. Minimum Circuit Ampacity: <Insert value>.

f. Maximum Overcurrent Protection: <Insert amperage>.

2.3 SEPARATELY COUPLED, HORIZONTALLY MOUNTED, IN-LINE CENTRIFUGAL PUMPS

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Armstrong Pumps Inc.

2. Aurora Pump; Division of Pentair Pump Group.

3. Flowserve Corporation.

4. Grundfos Pumps Corporation.

5. ITT Corporation; Bell & Gossett.

6. Mepco, LLC.

7. PACO Pumps.

8. Scot Pump; Div. of Ardox Corp.

9. TACO Incorporated.

10. Thrush Company Inc.

11. <Insert manufacturer's name>.

C. Description: Factory-assembled and -tested, centrifugal, overhung-impeller, separately coupled, in-line pump as defined in HI 1.1-1.2 and HI 1.3; designed for installation with pump and motor shafts mounted horizontally.

D. Pump Construction:

1. Casing: Radially split, cast iron, with threaded gage tappings at inlet and outlet, and threaded [companion-flange] [union-end] connections.

2. Impeller: ASTM B 584, cast bronze; statically and dynamically balanced, and keyed to shaft. For pumps not frequency-drive controlled, trim impeller to match specified performance.

3. Pump Shaft: [Steel, with copper-alloy shaft sleeve] [Stainless steel].

In "Mechanical Seal" Subparagraph below, retain "Buna-N" option for temperature rating of 225 deg F (107 deg C); retain "EPT" option for 250 deg F (120 deg C).

4. Mechanical Seal: Carbon rotating ring against a ceramic seat held by a stainless-steel spring, and [Buna-N] [EPT] bellows and gasket. Include water slinger on shaft between motor and seal.

5. Pump Bearings: [Permanently lubricated ball bearings] [Oil lubricated; bronze-journal or thrust type].

E. Shaft Coupling: [Molded-rubber insert with interlocking spider] [Interlocking frame with interconnecting springs] capable of absorbing vibration.

F. Motor: Single speed and [resiliently] [rigidly] mounted to pump casing.

1. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

Default motor characteristics are specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

2. Comply with NEMA designation, temperature rating, service factor, and efficiency requirements for motors specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

Verify enclosure types with manufacturer of specified equipment. Delete "Enclosure" Subparagraph below if included in schedule on Drawings or in "Capacities and Characteristics" Paragraph below.

a. Enclosure: [Open, dripproof] [Totally enclosed, fan cooled] [Totally enclosed, air over] [Open, externally ventilated] [Totally enclosed, nonventilated] [Severe duty] [Explosion proof] [Dust-ignition-proof machine].

Retain "Enclosure Materials," "Motor Bearings," "Unusual Service Conditions," "Efficiency," "NEMA Design," and "Service Factor" subparagraphs below if options are available from pump manufacturers and are different from default requirements specified in Section 230513 "Common Motor Requirements for HVAC Equipment." Consider each subparagraph and retain only those that vary from default requirements.

b. Enclosure Materials: [Cast iron] [Cast aluminum] [Rolled steel].

Permanently lubricated ball bearings are available up through 5 hp. Larger motors have grease-lubricated ball bearings.

c. Motor Bearings: [Permanently lubricated] [Grease-lubricated] ball bearings.

d. Unusual Service Conditions:

1) Ambient Temperature: <Insert deg C>.

2) Altitude: <Insert feet (meters)> above sea level.

3) High humidity.

4) <Insert conditions>.

e. Efficiency: Premium efficient.

f. NEMA Design: <Insert designation>.

g. Service Factor: <Insert value>.

If Project has more than one type or configuration of separately coupled, horizontally mounted, in-line centrifugal pump, delete "Capacities and Characteristics" Paragraph below and schedule pumps on Drawings.

G. Capacities and Characteristics:

1. Capacity: <Insert gpm (L/s)>.

2. Total Dynamic Head: <Insert feet (kPa)>.

3. Maximum Operating Pressure: 175 psig (1204 kPa).

4. Maximum Continuous Operating Temperature: [225 deg F (107 deg C)] [250 deg F (120 deg C)].

5. Inlet and Outlet Size: <Insert NPS (DN)>.

6. Impeller Size: <Insert inches (mm)>.

7. Motor Speed: <Insert rpm>.

8. Motor Horsepower: <Insert value>.

9. Electrical Characteristics:

a. Volts: [120] [240] [208] [460] <Insert value>.

b. Phase: [Single] [Three].

c. Hertz: 60.

d. Full-Load Amperes: <Insert value>.

e. Minimum Circuit Ampacity: <Insert value>.

f. Maximum Overcurrent Protection: <Insert amperage>.

2.4 SEPARATELY COUPLED, VERTICALLY MOUNTED, IN-LINE CENTRIFUGAL PUMPS

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Armstrong Pumps Inc.

2. Aurora Pump; Division of Pentair Pump Group.

3. Crane Pumps & Systems.

4. Flowserve Corporation.

5. ITT Corporation; Bell & Gossett.

6. Mepco, LLC.

7. PACO Pumps.

8. Peerless Pump Company.

9. Patterson Pump Co.; a subsidiary of the Gorman-Rupp Co.

10. TACO Incorporated.

11. Thrush Company Inc.

12. <Insert manufacturer's name>.

C. Description: Factory-assembled and -tested, centrifugal, overhung-impeller, separately coupled, in-line pump as defined in HI 1.1-1.2 and HI 1.3; designed for installation with pump and motor shafts mounted vertically.

D. Pump Construction:

1. Casing: Radially split, cast iron, with threaded gage tappings at inlet and outlet[, replaceable bronze wear rings,] and threaded [companion-flange] [union-end] connections.

2. Impeller: ASTM B 584, cast bronze; statically and dynamically balanced, keyed to shaft, and secured with a locking cap screw. For pumps not frequency-drive controlled, trim impeller to match specified performance.

3. Pump Shaft: [Steel, with copper-alloy shaft sleeve] [Stainless steel].

Retain one of two "Seal" subparagraphs below. Retain first subparagraph for service temperatures above 200 deg F (93 deg C); retain second subparagraph for service temperatures 200 deg F (93 deg C) or lower. In first subparagraph, retain "Buna-N" option for temperature rating of 225 deg F (107 deg C); retain "EPT" option for 250 deg F (120 deg C) and for glycol solutions.

4. Seal: Mechanical seal consisting of carbon rotating ring against a ceramic seat held by a stainless-steel spring, and [Buna-N] [EPT] bellows and gasket. Include water slinger on shaft between motor and seal.

5. Seal: Packing seal consisting of stuffing box with a minimum of four rings of graphite-impregnated braided yarn with bronze lantern ring between center two graphite rings, and bronze packing gland.

6. Pump Bearings: [Permanently lubricated ball bearings] [Oil lubricated; bronze-journal or thrust type].

E. Shaft Coupling: Axially split spacer coupling.

F. Motor: Single speed and rigidly mounted to pump casing with lifting eyebolt and supporting lugs in motor enclosure.

1. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

Default motor characteristics are specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

2. Comply with NEMA designation, temperature rating, service factor, and efficiency requirements for motors specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

Verify enclosure types with manufacturer of specified equipment. Delete "Enclosure" Subparagraph below if included in schedule on Drawings or in "Capacities and Characteristics" Paragraph below.

a. Enclosure: [Open, dripproof] [Totally enclosed, fan cooled] [Totally enclosed, air over] [Open, externally ventilated] [Totally enclosed, nonventilated] [Severe duty] [Explosion proof] [Dust-ignition-proof machine].

Retain "Enclosure Materials," "Motor Bearings," "Unusual Service Conditions," "Efficiency," "NEMA Design," and "Service Factor" subparagraphs below if options are available from pump manufacturers and are different from default requirements specified in Section 230513 "Common Motor Requirements for HVAC Equipment." Consider each subparagraph and retain only those that vary from default requirements.

b. Enclosure Materials: [Cast iron] [Cast aluminum] [Rolled steel].

Permanently lubricated ball bearings are available up through 5 hp. Larger motors have grease-lubricated ball bearings.

c. Motor Bearings: [Permanently lubricated] [Grease-lubricated] ball bearings.

d. Unusual Service Conditions:

1) Ambient Temperature: <Insert deg C>.

2) Altitude: <Insert feet (meters)> above sea level.

3) High humidity.

4) <Insert conditions>.

e. Efficiency: Premium efficient.

f. NEMA Design: <Insert designation>.

g. Service Factor: <Insert value>.

If Project has more than one type or configuration of separately coupled, vertically mounted, in-line centrifugal pump, delete "Capacities and Characteristics" Paragraph below and schedule pumps on Drawings.

G. Capacities and Characteristics:

1. Capacity: <Insert gpm (L/s)>.

2. Total Dynamic Head: <Insert feet (kPa)>.

3. Maximum Operating Pressure: [175 psig (1204 kPa)] [250 psig (1720 kPa)].

4. Maximum Continuous Operating Temperature: [225 deg F (107 deg C)] [250 deg F (120 deg C)].

5. Inlet and Outlet Size: <Insert NPS (DN)>.

6. Impeller Size: <Insert inches (mm)>.

7. Motor Speed: <Insert rpm>.

8. Motor Horsepower: <Insert value>.

9. Electrical Characteristics:

a. Volts: [120] [240] [208] [460] <Insert value>.

b. Phase: [Single] [Three].

c. Hertz: 60.

d. Full-Load Amperes: <Insert value>.

e. Minimum Circuit Ampacity: <Insert value>.

f. Maximum Overcurrent Protection: <Insert amperage>.

2.5 SEPARATELY COUPLED, BASE-MOUNTED, END-SUCTION CENTRIFUGAL PUMPS

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. American-Marsh Pumps.

2. Armstrong Pumps Inc.

3. Aurora Pump; Division of Pentair Pump Group.

4. Buffalo Pumps, Inc.

5. Crane Pumps & Systems.

6. Flowserve Corporation.

7. ITT Corporation; Bell & Gossett.

8. Mepco, LLC.

9. PACO Pumps.

10. Peerless Pump Company.

11. Scot Pump; Div. of Ardox Corp.

12. TACO Incorporated.

13. Thrush Company Inc.

14. <Insert manufacturer's name>.

C. Description: Factory-assembled and -tested, centrifugal, overhung-impeller, separately coupled, end-suction pump as defined in HI 1.1-1.2 and HI 1.3; designed for base mounting, with pump and motor shafts horizontal.

D. Pump Construction:

Not all manufacturers provide volute supports that allow removal and replacement of impeller without disconnecting piping.

1. Casing: Radially split, cast iron, with[ replaceable bronze wear rings,] threaded gage tappings at inlet and outlet, drain plug at bottom and air vent at top of volute, and [threaded companion-flange] [flanged] connections.[ Provide integral mount on volute to support the casing, and provide attached piping to allow removal and replacement of impeller without disconnecting piping or requiring the realignment of pump and motor shaft.]

2. Impeller: ASTM B 584, cast bronze; statically and dynamically balanced, keyed to shaft, and secured with a locking cap screw. For pumps not frequency-drive controlled, trim impeller to match specified performance.

3. Pump Shaft: [Steel, with copper-alloy shaft sleeve] [Stainless steel].

Retain one of two "Seal" subparagraphs below. Retain first subparagraph for service temperatures above 200 deg F (93 deg C); retain second subparagraph for service temperatures 200 deg F (93 deg C) or lower. In first subparagraph, retain "Buna-N" option for temperature rating of 225 deg F (107 deg C); retain "EPT" option for 250 deg F (120 deg C) and for glycol solutions.

4. Seal: Mechanical seal consisting of carbon rotating ring against a ceramic seat held by a stainless-steel spring, and [Buna-N] [EPT] bellows and gasket.

5. Seal: Packing seal consisting of stuffing box with a minimum of four rings of graphite-impregnated braided yarn with bronze lantern ring between center two graphite rings, and bronze packing gland.

6. Pump Bearings: Grease-lubricated ball bearings in cast-iron housing with grease fittings.

Not all manufacturers provide drop-out coupling that allows removal and replacement of impeller without disconnecting piping. This device is required with volute support described in "Casing" Subparagraph above.

E. Shaft Coupling: Molded-rubber insert and interlocking spider capable of absorbing vibration. [Couplings shall be drop-out type to allow disassembly and removal without removing pump shaft or motor.] [EPDM coupling sleeve for variable-speed applications.]

F. Coupling Guard: Dual rated; ANSI B15.1, Section 8; OSHA 1910.219 approved; steel; removable; attached to mounting frame.

G. Mounting Frame: Welded-steel frame and cross members, factory fabricated from ASTM A 36/A 36M channels and angles. Fabricate to mount pump casing, coupling guard, and motor.

H. Motor: Single speed, secured to mounting frame, with adjustable alignment.

1. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

Default motor characteristics are specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

2. Comply with NEMA designation, temperature rating, service factor, and efficiency requirements for motors specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

Verify enclosure types with manufacturer of specified equipment. Delete "Enclosure" Subparagraph below if included in schedule on Drawings or in "Capacities and Characteristics" Paragraph below.

a. Enclosure: [Open, dripproof] [Totally enclosed, fan cooled] [Totally enclosed, air over] [Open, externally ventilated] [Totally enclosed, nonventilated] [Severe duty] [Explosion proof] [Dust-ignition-proof machine].

Retain "Enclosure Materials," "Motor Bearings," "Unusual Service Conditions," "Efficiency," "NEMA Design," and "Service Factor" subparagraphs below if options are available from pump manufacturers and are different from default requirements specified in Section 230513 "Common Motor Requirements for HVAC Equipment." Consider each subparagraph and retain only those that vary from default requirements.

b. Enclosure Materials: [Cast iron] [Cast aluminum] [Rolled steel].

Permanently lubricated ball bearings are available up through 5 hp. Larger motors have grease-lubricated ball bearings.

c. Motor Bearings: [Permanently lubricated] [Grease-lubricated] ball bearings.

d. Unusual Service Conditions:

1) Ambient Temperature: <Insert deg C>.

2) Altitude: <Insert feet (meters)> above sea level.

3) High humidity.

4) <Insert conditions>.

e. Efficiency: Premium efficient.

f. NEMA Design: <Insert designation>.

g. Service Factor: <Insert value>.

If Project has more than one type or configuration of separately coupled, base-mounted, end-suction centrifugal pump, delete "Capacities and Characteristics" Paragraph below and schedule pumps on Drawings.

I. Capacities and Characteristics:

1. Capacity: <Insert gpm (L/s)>.

2. Total Dynamic Head: <Insert feet (kPa)>.

3. Maximum Operating Pressure: [175 psig (1204 kPa)] [250 psig (1720 kPa)].

4. Maximum Continuous Operating Temperature: [225 deg F (107 deg C)] [250 deg F (120 deg C)].

5. Inlet and Outlet Size: <Insert NPS (DN)>.

6. Impeller Size: <Insert inches (mm)>.

7. Motor Speed: <Insert rpm>.

8. Motor Horsepower: <Insert value>.

9. Electrical Characteristics:

a. Volts: [120] [240] [208] [460] <Insert value>.

b. Phase: [Single] [Three].

c. Hertz: 60.

d. Full-Load Amperes: <Insert value>.

e. Minimum Circuit Ampacity: <Insert value>.

f. Maximum Overcurrent Protection: <Insert amperage>.

2.6 AUTOMATIC CONDENSATE PUMP UNITS

Units in this article are complete with pump, basin, and controls and have limited applications and small capacity.

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Beckett Corporation.

2. Hartell Pumps Div.; Milton Roy Co.

3. Little Giant Pump Co.

4. Mepco, LLC.

5. <Insert manufacturer's name>.

C. Description: Packaged units with corrosion-resistant pump, plastic tank with cover, and automatic controls. Include factory- or field-installed check valve and a 72-inch- (1800-mm-) minimum, electrical power cord with plug.

If Project has more than one type or configuration of automatic condensate pump unit, delete "Capacities and Characteristics" Paragraph below and schedule pumps on Drawings.

D. Capacities and Characteristics:

1. Capacity: <Insert gpm (L/s)>.

2. Total Dynamic Head: <Insert feet (kPa)>.

3. Maximum Height to Inlet: <Insert inches (mm)>.

4. Inlet and Outlet Size: <Insert NPS (DN)>.

5. Motor Speed: <Insert rpm>.

6. Motor Horsepower: <Insert value>.

7. Electrical Characteristics:

a. Volts: [120] <Insert value>.

b. Phase: Single.

c. Hertz: 60.

d. Full-Load Amperes: <Insert value>.

e. Minimum Circuit Ampacity: <Insert value>.

f. Maximum Overcurrent Protection: <Insert amperage>.

2.7 PUMP SPECIALTY FITTINGS

See the Evaluations for cautions about pump specialty fittings. In this article, retain ductile-iron body for 300-psig (2060-kPa) pressure rating; retain stainless-steel strainer for condenser water usage.

A. Suction Diffuser:

1. Angle pattern.

2. [175-psig (1204-kPa)] [300-psig (2060-kPa)] pressure rating, [cast] [ductile]-iron body and end cap, pump-inlet fitting.

3. Bronze startup and bronze or stainless-steel permanent strainers.

4. Bronze or stainless-steel straightening vanes.

5. Drain plug.

6. Factory-fabricated support.

B. Triple-Duty Valve:

1. Angle or straight pattern.

2. [175-psig (1204-kPa)] [300-psig (2060-kPa)] pressure rating, [cast] [ductile]-iron body, pump-discharge fitting.

3. Drain plug and bronze-fitted shutoff, balancing, and check valve features.

4. Brass gage ports with integral check valve and orifice for flow measurement.

PART 3 -  EXECUTION

3.1 PUMP INSTALLATION

Retain first paragraph below for centrifugal pumps.

A. Comply with HI 1.4.

B. Install pumps to provide access for periodic maintenance including removing motors, impellers, couplings, and accessories.

C. Independently support pumps and piping so weight of piping is not supported by pumps and weight of pumps is not supported by piping.

D. Automatic Condensate Pump Units: Install units for collecting condensate and extend to open drain.

E. Equipment Mounting:

Retain first subparagraph below to require equipment to be installed on cast-in-place concrete equipment bases.

1. Install base-mounted pumps on cast-in-place concrete equipment base(s). Comply with requirements for equipment bases and foundations specified in [Section 033000 "Cast-in-Place Concrete."] [Section 033053 "Miscellaneous Cast-in-Place Concrete."]

Retain one of two subparagraphs below if vibration isolation is required. Retain first for projects in seismic areas; retain second for projects not in seismic areas. Indicate vibration isolation and seismic-control device type and minimum deflection in supported equipment schedule on Drawings.

2. Comply with requirements for vibration isolation and seismic control devices specified in Section 230548 "Vibration and Seismic Controls for HVAC."

3. Comply with requirements for vibration isolation devices specified in Section 230548.13 "Vibration Controls for HVAC."

Retain "Equipment Mounting" Paragraph below for in-line pumps suspended from structure.

F. Equipment Mounting: Install in-line pumps with continuous-thread hanger rods and [elastomeric hangers] [spring hangers] [spring hangers with vertical-limit stop] of size required to support weight of in-line pumps.

1. Comply with requirements for seismic-restraint devices specified in Section 230548 "Vibration and Seismic Controls for HVAC."

2. Comply with requirements for hangers and supports specified in Section 230529 "Hangers and Supports for HVAC Piping and Equipment."

3.2 ALIGNMENT

A. [Engage a factory-authorized service representative to perform] [Perform] alignment service.

Retain this article only for separately coupled, end-suction centrifugal pumps.

B. Comply with requirements in Hydronics Institute standards for alignment of pump and motor shaft. Add shims to the motor feet and bolt motor to base frame. Do not use grout between motor feet and base frame.

C. Comply with pump and coupling manufacturers' written instructions.

D. After alignment is correct, tighten foundation bolts evenly but not too firmly. Completely fill baseplate with nonshrink, nonmetallic grout while metal blocks and shims or wedges are in place. After grout has cured, fully tighten foundation bolts.

3.3 CONNECTIONS

Coordinate piping installations and specialty arrangements with Drawings and with requirements specified in piping systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Comply with requirements for piping specified in Section 232213 "Steam and Condensate Heating Piping" and Section 232216 "Steam and Condensate Piping Specialties."

B. Drawings indicate general arrangement of piping, fittings, and specialties.

C. Where installing piping adjacent to pump, allow space for service and maintenance.

D. Connect piping to pumps. Install valves that are same size as piping connected to pumps.

E. Install suction and discharge pipe sizes equal to or greater than diameter of pump nozzles.

F. Install [check, shutoff, and throttling valves] [check valve and throttling valve with memory stop] [triple-duty valve] on discharge side of pumps.

G. Install [Y-type strainer] [suction diffuser] and shutoff valve on suction side of pumps.

H. Install flexible connectors on suction and discharge sides of base-mounted pumps between pump casing and valves.

I. Install pressure gages on pump suction and discharge or at integral pressure-gage tapping, or install single gage with multiple-input selector valve.

Retain first two paragraphs below for automatic condensate pump units.

J. Install check valve and gate or ball valve on each condensate pump unit discharge.

K. Ground equipment according to Section 260526 "Grounding and Bonding for Electrical Systems."

L. Connect wiring according to Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

END OF SECTION 232123

	HYDRONIC PUMPS
	232123 - 1



