Copyright 2012 AIA
MasterSpec Professional
03/12

Copyright 2012 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 232213 - STEAM AND CONDENSATE HEATING PIPING
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section includes pipe and fittings for LP steam less than 15 psig (104 kPa) and condensate piping.

B. Related Requirements:

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

1. Section 232216 "Steam and Condensate Piping Specialties" for strainers, flash tanks, special-duty valves, steam traps, thermostatic air vents and vacuum breakers, and steam and condensate meters.

1.2 ACTION SUBMITTALS

Retain "Delegated-Design Submittal" Paragraph below if design services have been delegated to Contractor.

A. Delegated-Design Submittal:

1. Design calculations and detailed fabrication and assembly of pipe anchors and alignment guides, hangers and supports for multiple pipes, expansion joints and loops, and attachments of the same to the building structure.

2. Locations of pipe anchors and alignment guides and expansion joints and loops.

3. Locations of and details for penetrations, including sleeves and sleeve seals for exterior walls, floors, basement, and foundation walls.

4. Locations of and details for penetration and firestopping for fire- and smoke-rated wall and floor and ceiling assemblies.

1.3 INFORMATIONAL SUBMITTALS

Retain "Field quality-control reports" Paragraph below if Contractor is responsible for field quality-control testing and inspecting.

A. Field quality-control reports.

1.4 QUALITY ASSURANCE

Retain applicable options in "ASME Compliance" Paragraph below. Retain all three options if steam system includes high and low pressure.

A. ASME Compliance: Comply with [ASME B31.1, "Power Piping,"] [and] [ASME B31.9, "Building Services Piping,"] for materials, products, and installation.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

2.1 PERFORMANCE REQUIREMENTS

Performance requirements in this article are for the piping system. Individual components may have higher pressure or temperature ratings.

A. Components and installation shall be capable of withstanding the following minimum working pressures and temperatures unless otherwise indicated:

Insert minimum working pressure for system in "LP Steam Piping" Subparagraph below.

1. LP Steam Piping: <Insert psig (kPa)>.

Insert or retain minimum working pressure and temperature for systems in "Condensate Piping" and "Makeup-Water Piping" subparagraphs below.

2. Condensate Piping: <Insert psig (kPa)> at [250 deg F (121 deg C)] <Insert temperature>.

3. Makeup-Water Piping: [80 psig (552 kPa)] <Insert value> at [150 deg F (66 deg C)] <Insert temperature>.

4. Blowdown-Drain Piping: Equal to pressure of the piping system to which it is attached.

5. Air-Vent and Vacuum-Breaker Piping: Equal to pressure of the piping system to which it is attached.

6. Safety-Valve-Inlet and -Outlet Piping: Equal to pressure of the piping system to which it is attached.

See "Writing Guide" Article in the Evaluations for discussion of this Section's organization and of the most efficient way to revise this Section.

2.2 STEEL PIPE AND FITTINGS

A. Steel Pipe: ASTM A 53/A 53M, black steel, plain ends, welded and seamless, Grade B, and Schedule as indicated in piping applications articles.

Coordinate flange class in four paragraphs below with products in other parts of this Section and in related Sections to match face size and bolt patterns.

B. Cast-Iron Threaded Fittings: ASME B16.4; Classes 125, 150, and 300 as indicated in piping applications articles.

C. Malleable-Iron Threaded Fittings: ASME B16.3; Classes 150 and 300 as indicated in piping applications articles.

D. Malleable-Iron Unions: ASME B16.39; Classes 150, 250, and 300 as indicated in piping applications articles.

E. Cast-Iron Threaded Flanges and Flanged Fittings: ASME B16.1, Classes 125 and 250 as indicated in piping applications articles; raised ground face, and bolt holes spot faced.

2.3 JOINING MATERIALS

A. Pipe-Flange Gasket Materials: Suitable for chemical and thermal conditions of piping system contents.

1. ASME B16.21, nonmetallic, flat, asbestos free, 1/8-inch (3.2-mm) maximum thickness unless otherwise indicated.

a. Full-Face Type: For flat-face, Class 125, cast-iron and cast-bronze flanges.

b. Narrow-Face Type: For raised-face, Class 250, cast-iron and steel flanges.

B. Flange Bolts and Nuts: ASME B18.2.1, carbon steel, unless otherwise indicated.

PART 3 -  EXECUTION

3.1 LP STEAM PIPING APPLICATIONS

Retain at least one pipe material in paragraphs below for each service required for Project. See "Writing Guide" Article in the Evaluations.

A. LP Steam Piping: [Schedule 40] [Schedule 80], Type S, Grade B, steel pipe; Class 125 cast-iron fittings; and threaded joints.

B. Condensate Piping above Grade: Schedule 80, Type S, Grade B, steel pipe; Class 125 cast-iron fittings; and threaded joints.

C. Condensate Piping below Grade: Schedule 80, Type S, Grade B, steel pipe; Class 125 cast-iron fittings; and threaded joints.

3.2 ANCILLARY PIPING APPLICATIONS

A. Blowdown-Drain Piping: Same materials and joining methods as for piping specified for the service in which blowdown drain is installed.

B. Vacuum-Breaker Piping: Outlet, same as service where installed.

C. Safety-Valve-Inlet and -Outlet Piping: Same materials and joining methods as for piping specified for the service in which safety valve is installed.

3.3 PIPING INSTALLATION

Indicate piping locations and arrangements on Drawings if such were used to size pipe and calculate friction loss, expansion, pump sizing, and other design considerations.

A. Drawing plans, schematics, and diagrams indicate general location and arrangement of piping systems. Install piping as indicated unless deviations to layout are approved on Coordination Drawings.

B. Install piping in concealed locations unless otherwise indicated and except in equipment rooms and service areas.

C. Install piping indicated to be exposed and piping in equipment rooms and service areas at right angles or parallel to building walls. Diagonal runs are prohibited unless otherwise indicated.

D. Install piping above accessible ceilings to allow sufficient space for ceiling panel removal.

E. Install piping to permit valve servicing.

F. Install piping free of sags and bends.

G. Install fittings for changes in direction and branch connections.

H. Install piping to allow application of insulation.

I. Select system components with pressure rating equal to or greater than system operating pressure.

J. Install groups of pipes parallel to each other, spaced to permit applying insulation and servicing of valves.

K. Install drains, consisting of a tee fitting, NPS 3/4 (DN 20) full port-ball valve, and short NPS 3/4 (DN 20) threaded nipple with cap, at low points in piping system mains and elsewhere as required for system drainage.

L. Install steam supply piping at a minimum uniform grade of 0.2 percent downward in direction of steam flow.

M. Install condensate return piping at a minimum uniform grade of 0.4 percent downward in direction of condensate flow.

N. Reduce pipe sizes using eccentric reducer fitting installed with level side down.

O. Install branch connections to mains using[ mechanically formed] tee fittings in main pipe, with the branch connected to top of main pipe.

P. Install valves according to Section 230523 "General-Duty Valves for HVAC Piping."

Q. Install unions in piping, [NPS 2 (DN 50)] <Insert pipe size> and smaller, adjacent to valves, at final connections of equipment, and elsewhere as indicated.

R. Install flanges in piping, [NPS 2-1/2 (DN 65)] <Insert pipe size> and larger, at final connections of equipment and elsewhere as indicated.

S. Install shutoff valve immediately upstream of each dielectric fitting.

T. Install strainers on supply side of control valves, pressure-reducing valves, traps, and elsewhere as indicated. Install NPS 3/4 (DN 20) nipple and full port ball valve in blowdown connection of strainers NPS 2 (DN 50) and larger. Match size of strainer blowoff connection for strainers smaller than NPS 2 (DN 50).

U. Comply with requirements in Section 230516 "Expansion Fittings and Loops for HVAC Piping" for installation of expansion loops, expansion joints, anchors, and pipe alignment guides.

V. Comply with requirements in Section 230553 "Identification for HVAC Piping and Equipment" for identifying piping.

W. Install drip legs at low points and natural drainage points such as ends of mains, bottoms of risers, and ahead of pressure regulators, and control valves.

1. On straight runs with no natural drainage points, install drip legs at intervals not exceeding [300 feet (90 m)] <Insert distance>.

2. Size drip legs same size as main. In steam mains NPS 6 (DN 150) and larger, drip leg size can be reduced, but to no less than NPS 4 (DN 100).

X. Install sleeves for piping penetrations of walls, ceilings, and floors. Comply with requirements for sleeves specified in Section 230517 "Sleeves and Sleeve Seals for HVAC Piping."

Retain first paragraph below for piping that penetrates an exterior concrete wall or concrete slab.

Y. Install sleeve seals for piping penetrations of concrete walls and slabs. Comply with requirements for sleeve seals specified in Section 230517 "Sleeves and Sleeve Seals for HVAC Piping."

Z. Install escutcheons for piping penetrations of walls, ceilings, and floors. Comply with requirements for escutcheons specified in Section 230518 "Escutcheons for HVAC Piping."

3.4 STEAM AND CONDENSATE PIPING SPECIALTIES INSTALLATION

A. Comply with requirements in Section 232216 "Steam and Condensate Piping Specialties" for installation requirements for strainers, flash tanks, special-duty valves, steam traps, thermostatic air vents and vacuum breakers, and steam and condensate meters.

3.5 HANGERS AND SUPPORTS

Piping support must account for expansion and contraction, vibration, dead load of piping and its contents, and seismic-bracing requirements.

A. Comply with requirements in Section 230529 "Hangers and Supports for HVAC Piping and Equipment" for installation of hangers and supports. Comply with requirements below for maximum spacing.

Retain first paragraph below for projects in areas that require seismic restraints.

B. Comply with requirements in Section 230548 "Vibration and Seismic Controls for HVAC" for seismic restraints.

C. Install the following pipe attachments:

1. Adjustable steel clevis hangers for individual horizontal piping less than 20 feet (6 m) long.

2. Adjustable roller hangers and spring hangers for individual horizontal piping 20 feet (6 m) or longer.

3. Pipe Roller: MSS SP-58, Type 44 for multiple horizontal piping 20 feet (6 m) or longer, supported on a trapeze.

4. Spring hangers to support vertical runs.

Verify actual supported loads for hanger sizes and spacing. Consult structural engineer. Maximum spacing in first two paragraphs below is from MSS SP-69, "Pipe Hangers and Supports - Selection and Application," and from the International Mechanical Code. Maximum spacing for steel pipe required by the International Mechanical Code is 12 feet (3.7 m). If hanger spacing is determined by local codes that differ from MSS SP-69 and the International Mechanical Code, delete first two paragraphs below. Contractor is then obligated to comply with the maximum spacing required by authorities having jurisdiction.

D. Install hangers for steel steam supply piping with the following maximum spacing:

1. NPS 3/4 (DN 20): Maximum span, 9 feet (2.7 m).

2. NPS 1 (DN 25): Maximum span, 9 feet (2.7 m).

3. NPS 1-1/2 (DN 40): Maximum span, 12 feet (3.7 m).

4. NPS 2 (DN 50): Maximum span, 13 feet (4 m).

5. NPS 2-1/2 (DN 65): Maximum span, 14 feet (4.3 m).

6. NPS 3 (DN 80) and Larger: Maximum span, 15 feet (4.6 m).

E. Install hangers for steel steam condensate piping with the following maximum spacing:

1. NPS 3/4 (DN 20): Maximum span, 7 feet (2.1 m).

2. NPS 1 (DN 25): Maximum span, 7 feet (2.1 m).

3. NPS 1-1/2 (DN 40): Maximum span, 9 feet (2.7 m).

4. NPS 2 (DN 50): Maximum span, 10 feet (3 m).

5. NPS 2-1/2 (DN 65): Maximum span, 11 feet (3.4 m).

6. NPS 3 (DN 80) and Larger: Maximum span, 12 feet (3.7 m.)
F. Support vertical runs at roof, at each floor, and at 10-foot (3-m) intervals between floors.

3.6 PIPE JOINT CONSTRUCTION

A. Ream ends of pipes and remove burrs. Bevel plain ends of steel pipe.

B. Remove scale, slag, dirt, and debris from inside and outside of pipe and fittings before assembly.

C. Threaded Joints: Thread pipe with tapered pipe threads according to ASME B1.20.1. Cut threads full and clean using sharp dies. Ream threaded pipe ends to remove burrs and restore full ID. Join pipe fittings and valves as follows:

1. Apply appropriate tape or thread compound to external pipe threads unless dry seal threading is specified.

2. Damaged Threads: Do not use pipe or pipe fittings with threads that are corroded or damaged. Do not use pipe sections that have cracked or open welds.

D. Flanged Joints: Select appropriate gasket material, size, type, and thickness for service application. Install gasket concentrically positioned. Use suitable lubricants on bolt threads.

3.7 TERMINAL EQUIPMENT CONNECTIONS

A. Size for supply and return piping connections shall be the same as or larger than equipment connections.

Specify access doors and panels for walls and ceilings in Section 083113 "Access Doors and Frames." Show locations of access doors and panels on Drawings, and coordinate with architectural reflected ceiling and wall elevation Drawings.

B. Install traps and control valves in accessible locations close to connected equipment.

C. Install bypass piping with globe valve around control valve. If parallel control valves are installed, only one bypass is required.

D. Install vacuum breakers downstream from control valve, close to coil inlet connection.

E. Install a drip leg at coil outlet.

3.8 FIELD QUALITY CONTROL

A. Prepare steam and condensate piping according to [ASME B31.1, "Power Piping,"] [and] [ASME B31.9, "Building Services Piping,"] and as follows:

1. Leave joints, including welds, uninsulated and exposed for examination during test.

2. Provide temporary restraints for expansion joints that cannot sustain reactions due to test pressure. If temporary restraints are impractical, isolate expansion joints from testing.

3. Flush system with clean water. Clean strainers.

4. Isolate equipment from piping. If a valve is used to isolate equipment, its closure shall be capable of sealing against test pressure without damage to valve. Install blinds in flanged joints to isolate equipment.

Retain "Testing Agency," "Manufacturer's Field Service," and "Perform the following tests and inspections" paragraphs below to identify who shall perform tests and inspections. If retaining second option in "Testing Agency" Paragraph or if retaining "Manufacturer's Field Service" or "Perform the following tests and inspections" Paragraph, retain "Field quality-control reports" Paragraph in "Informational Submittals" Article.

B. Testing Agency: [Owner will engage] [Engage] a qualified testing agency to perform tests and inspections.

Retain "Manufacturer's Field Service" Paragraph below to require a factory-authorized service representative to perform tests and inspections.

C. Manufacturer's Field Service: Engage a factory-authorized service representative to test and inspect components, assemblies, and equipment installations, including connections.

Retain "Perform the following tests and inspections" Paragraph below to require Contractor to perform tests and inspections.

D. Perform the following tests and inspections[ with the assistance of a factory-authorized service representative]:

Procedures in subparagraphs below are paraphrased from ASME B31.9.

1. Use ambient temperature water as a testing medium unless there is risk of damage due to freezing. Another liquid that is safe for workers and compatible with piping may be used.

2. Subject piping system to hydrostatic test pressure that is not less than 1.5 times the working pressure. Test pressure shall not exceed maximum pressure for any vessel, pump, valve, or other component in system under test. Verify that stress due to pressure at bottom of vertical runs does not exceed 90 percent of specified minimum yield strength.

3. After hydrostatic test pressure has been applied for at least 10 minutes, examine piping, joints, and connections for leakage. Eliminate leaks by tightening, repairing, or replacing components, and repeat hydrostatic test until there are no leaks.

E. Prepare test and inspection reports.

END OF SECTION 232213

	STEAM AND CONDENSATE HEATING PIPING
	232213 - 1



