Copyright 2012 AIA
MasterSpec Professional
03/12

Copyright 2012 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 232500 - HVAC WATER TREATMENT
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section includes the following HVAC water-treatment systems:

1. Manual and automatic chemical-feed equipment and controls.

2. Ozone-generator biocide equipment and controls.

3. Stainless-steel pipes and fittings.

4. UV-irradiation unit, biocide equipment, and controls.

5. Chemical treatment test equipment.

6. Chemicals.

7. HVAC makeup-water softeners.

8. RO equipment for HVAC makeup water.

9. Water filtration equipment.

1.2 ACTION SUBMITTALS

A. Product Data: Include rated capacities, operating characteristics, and furnished specialties and accessories for each type of product.

1.3 INFORMATIONAL SUBMITTALS

A. Field quality-control reports.

1.4 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

2.1 MANUFACTURERS

Retain this article to require a single-source responsibility for all water-treatment equipment and materials. See "Writing Guide" Article in the Evaluations.

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Ampion Corp.

2. Anderson Chemical Company.

3. Aqua-Chem, Inc; Cleaver-Brooks Div.

4. Barclay Water Management, Inc.

5. Boland.

6. Cascade Water Services, Inc.

7. Earthwise Environmental Inc.

8. General Electric Company; GE Water & Process Technologies.

9. H-O-H Water Technology, Inc.

10. Metro Group, Inc. (The); Metropolitan Refining Div.

11. Nalco; an Ecolab company.

12. Watcon, Inc.

13. Water Services Inc.

14. <Insert manufacturer's name>.

2.2 PERFORMANCE REQUIREMENTS

A. Closed hydronic systems shall have the following water qualities:

1. pH: Maintain a value within [9.0 to 10.5] <Insert range>.

2. "P" Alkalinity: Maintain a value within [100 to 500] <Insert range> ppm.

3. Boron: Maintain a value within [100 to 200] <Insert range> ppm.

Retain "Chemical Oxygen Demand" Subparagraph below for systems that do not contain glycol.

4. Chemical Oxygen Demand: Maintain a maximum value of [100] <Insert number> ppm.

5. Soluble Copper: Maintain a maximum value of [0.20] <Insert number> ppm.

6. TSS: Maintain a maximum value of [10] <Insert number> ppm.

7. Ammonia: Maintain a maximum value of [20] <Insert number> ppm.

8. Free Caustic Alkalinity: Maintain a maximum value of [20] <Insert number> ppm.

9. Microbiological Limits:

a. Total Aerobic Plate Count: Maintain a maximum value of [1000] <Insert number> organisms/mL.

b. Total Anaerobic Plate Count: Maintain a maximum value of [100] <Insert number> organisms/mL.

c. Nitrate Reducers: Maintain a maximum value of [100] <Insert number> organisms/mL.

d. Sulfate Reducers: Maintain a maximum value of [zero] <Insert number> organisms/mL.

e. Iron Bacteria: Maintain a maximum value of [zero] <Insert number> organisms/mL.

10. <Insert other requirements if necessary>.

B. Open hydronic systems, including [condenser] [fluid-cooler spray] water, shall have the following water qualities:

1. pH: Maintain a value within [8.0 to 9.1] <Insert range>.

2. "P" Alkalinity: Maintain a maximum value of [100] <Insert number> ppm.

3. Chemical Oxygen Demand: Maintain a maximum value of [100] <Insert number> ppm.

4. Soluble Copper: Maintain a maximum value of [0.20] <Insert number> ppm.

5. TSS: Maintain a maximum value of [10] <Insert number> ppm.

6. Ammonia: Maintain a maximum value of [20] <Insert number> ppm.

7. Free "OH" Alkalinity: Maintain a maximum value of [zero] <Insert number> ppm.

8. Microbiological Limits:

a. Total Aerobic Plate Count: Maintain a maximum value of [10,000] <Insert number> organisms/mL.

b. Total Anaerobic Plate Count: Maintain a maximum value of [1000] <Insert number> organisms/mL.

c. Nitrate Reducers: Maintain a maximum value of [100] <Insert number> organisms/mL.

d. Sulfate Reducers: Maintain a maximum value of [zero] <Insert number> organisms/mL.

e. Iron Bacteria: Maintain a maximum value of [zero] <Insert number> organisms/mL.

9. Polymer Testable: Maintain a minimum value within [10 to 40] <Insert range>.

10. <Insert other requirements if necessary>.

Retain "Passivation for Galvanized Steel" Paragraph below for cooling towers, evaporative coolers, or similar equipment with galvanized-steel components, to avoid white rust. Water quality values below are taken from the 2007 ASHRAE HANDBOOK - "HVAC Applications," Ch. 48, "Water Treatment." Revise these values as recommended by galvanized equipment manufacturers.

C. Passivation for Galvanized Steel: For the first 60 days of operation.

1. pH: Maintain a value within [7 to 8] <Insert range>.

2. Calcium Carbonate Hardness: Maintain a value within [100 to 300] <Insert range> ppm.

3. Calcium Carbonate Alkalinity: Maintain a value within [100 to 300] <Insert range> ppm.

2.3 MANUAL CHEMICAL-FEED EQUIPMENT

Retain this article for closed piping systems such as chilled-water, hot-water, and dual-temperature piping.

A. Bypass Feeders: Steel, with corrosion-resistant exterior coating, minimum 3-1/2-inch (89-mm) fill opening in the top, and NPS 3/4 (DN 20) bottom inlet and top side outlet. Quarter turn or threaded fill cap with gasket seal and diaphragm to lock the top on the feeder when exposed to system pressure in the vessel.

1. Capacity: [2 gal. (7.6 L)] [5 gal. (19 L)] <Insert value>.

2. Minimum Working Pressure: [125 psig (860 kPa)] [175 psig (1210 kPa)] <Insert value>.

2.4 AUTOMATIC CHEMICAL-FEED EQUIPMENT

Retain "Water Meter" Paragraph below. If retaining more than one meter description, indicate on Drawings where meters are to be installed. Open systems and large closed systems, more than 400 gpm (25 L/s), should be equipped with a meter.

A. Water Meter:

1. AWWA C700, oscillating-piston, magnetic-drive, totalization meter.

2. Body: Bronze.

3. Minimum Working-Pressure Rating: 150 psig (1035 kPa).

4. Maximum Pressure Loss at Design Flow: 3 psig (20 kPa).

5. Registration: Gallons (Liters) or cubic feet (cubic meters).

6. End Connections: Threaded.

7. Controls: Flow-control switch with normally open contacts; rated for maximum 10 A, 250-V ac, and that will close at adjustable increments of total flow.

Retain "Inhibitor Injection Timers" Paragraph below for open systems.

B. Inhibitor Injection Timers:

1. Microprocessor-based controller with digital display in NEMA 250, Type 12 enclosure with gasketed and lockable door.[ Interface for start/stop and status indication at central workstation as described in Section 230900 "Instrumentation and Control for HVAC."]

2. Programmable timers with infinite adjustment over full range, and mounted in cabinet with hand-off-auto switches and status lights.

3. Test switch.

4. Hand-off-auto switch for chemical pump.

5. Illuminated legend to indicate feed when pump is activated.

6. Programmable lockout timer with indicator light. Lockout timer to deactivate the pump and activate alarm circuits.

7. Digital display makeup totalizer to measure amount of makeup and bleed-off water from two water meter inputs.

Retain "pH Controller" Paragraph below for open systems that require acid injection for pH control.

C. pH Controller:

1. Microprocessor-based controller, 1 percent accuracy in a range from zero to 14 units. Incorporate solid-state integrated circuits and digital display in NEMA 250, Type 12 enclosure with gasketed and lockable door.[ Interface for start/stop and status indication at central workstation as described in Section 230900 "Instrumentation and Control for HVAC."]

2. Digital display and touch pad for input.

3. Sensor probe adaptable to sample stream manifold.

4. High, low, and normal pH indication.

5. High or low-pH-alarm-light trip points, field adjustable; with silence switch.

6. Hand-off-auto switch for acid pump.

7. Internal adjustable hysteresis or deadband.

Retain "TSS Controller" Paragraph below for open systems, including steam boilers, cooling towers, and fluid coolers.

D. TSS Controller:

1. Microprocessor-based controller, 1 percent accuracy in a range from zero to 5000 micromhos. Incorporate solid-state integrated circuits and digital display in NEMA 250, Type 12 enclosure with gasketed and lockable door.[ Interface for start/stop and status indication at central workstation as described in Section 230900 "Instrumentation and Control for HVAC."]

2. Digital display and touch pad for input.

3. Sensor probe adaptable to sample stream manifold.

4. High, low, and normal conductance indication.

5. High- or low-conductance-alarm-light trip points, field adjustable; with silence switch.

6. Hand-off-auto switch for solenoid bleed-off valve.

7. Bleed-off valve activated indication.

8. Internal adjustable hysteresis or deadband.

9. Bleed Valves:

a. Cooling Systems: Forged-brass body, globe pattern, general-purpose solenoid with continuous-duty coil, or motorized valve.

b. Steam Boilers: Motorized ball valve, steel body, and TFE seats and seals.

Retain "Biocide Feeder Timer" Paragraph below for open hydronic systems, including cooling towers and fluid coolers.

E. Biocide Feeder Timer:

1. Microprocessor-based controller with digital display in NEMA 250, Type 12 enclosure with gasketed and lockable door.[ Interface for start/stop and status indication at central workstation as described in Section 230900 "Instrumentation and Control for HVAC."]

2. 24-hour timer with 14-day skip feature to permit activation any hour of day.

3. Precision, solid-state, bleed-off lockout timer and clock-controlled biocide pump timer. Prebleed and bleed lockout timers.

4. Solid-state alternator to enable use of two formulations.

5. 24-hour display of time of day.

6. 14-day display of day of week.

7. Battery backup so clock is not disturbed by power outages.

8. Hand-off-auto switches for biocide pumps.

9. Biocide A and Biocide B pump running indication.

F. Chemical Solution Tanks:

1. Chemical-resistant reservoirs fabricated from high-density opaque polyethylene with minimum 110 percent containment vessel.

2. Molded cover with recess for mounting pump.

3. Capacity: [30 gal. (114 L)] [50 gal. (189 L)] [120 gal. (454 L)] <Insert value>.

G. Chemical Solution Injection Pumps:

1. Self-priming, positive displacement; rated for intended chemical with minimum 25 percent safety factor for design pressure and temperature.

2. Adjustable flow rate.

3. Metal and thermoplastic construction.

4. Built-in relief valve.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Section 230513 "Common Motor Requirements for HVAC Equipment." If different characteristics are required, add subparagraphs below to suit Project.

5. Fully enclosed, continuous-duty, single-phase motor. Comply with requirements in Section 230513 "Common Motor Requirements for HVAC Equipment."

a. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

H. Chemical Solution Tubing: Polyethylene tubing with compression fittings and joints except ASTM A 269, Type 304, stainless steel for steam boiler injection assemblies.

I. Injection Assembly:

1. Quill: Minimum NPS 1/2 (DN 15) with insertion length sufficient to discharge into at least 25 percent of pipe diameter.

2. Ball Valve: [Three] [Two]-piece stainless steel, as described in "Stainless-Steel Pipes and Fittings" Article; selected to fit quill.

3. Packing Gland: Mechanical seal on quill of sufficient length to allow quill removal during system operation.

4. Assembly Pressure/Temperature Rating: Minimum 600 psig (4137 kPa) at 200 deg F (93 deg C).

2.5 CHEMICALS

Revise this article to suit local conditions and recommendations of chemical treatment manufacturer.

A. Chemicals shall be as recommended by water-treatment system manufacturer that are compatible with piping system components and connected equipment and that can attain water quality specified in "Performance Requirements" Article.

Retain "Water Softener Chemicals" Paragraph below for water softeners.

B. Water Softener Chemicals:

1. Mineral: High-capacity, sulfonated-polystyrene ion-exchange resin that is stable over entire pH range with good resistance to bead fracture from attrition or shock. Resin exchange capacity minimum 30,000 grains/cu. ft. (69 kg/cu. m) of calcium carbonate of resin when regenerated with 15 lb (6.8 kg) of salt.

2. Salt for Brine Tanks: High-purity sodium chloride, free of dirt and foreign material. Rock and granulated forms are unacceptable.

PART 3 -  EXECUTION

3.1 WATER ANALYSIS

Delete this article if water analysis has been or will be performed by Owner.

A. Perform an analysis of supply water to determine quality of water available at Project site.

3.2 INSTALLATION

Coordinate this article with Drawings.

A. Install chemical application equipment on concrete bases level and plumb. Maintain manufacturer's recommended clearances. Arrange units so controls and devices that require servicing are accessible. Anchor chemical tanks and floor-mounting accessories to substrate.

Retain first paragraph below for Project in a seismic area. Add special requirements for seismic restraints here or indicate on Drawings.

B. Install seismic restraints for equipment and floor-mounting accessories and anchor to building structure. See Section 230548 "Vibration and Seismic Controls for HVAC" for seismic restraints.

C. Install interconnecting control wiring for chemical treatment controls and sensors.

D. Mount sensors and injectors in piping circuits.

E. Bypass Feeders: Install in closed hydronic systems, including and equipped with the following:

1. Install bypass feeder in a bypass circuit around circulating pumps unless otherwise indicated on Drawings.

Retain first subparagraph below for closed systems larger than 400 gpm (24 L/s).

2. Install water meter in makeup-water supply.

3. Install test-coupon assembly in bypass circuit around circulating pumps unless otherwise indicated on Drawings.

4. Install a gate or full-port ball isolation valves on inlet, outlet, and drain below feeder inlet.

5. Install a swing check on inlet after the isolation valve.

F. Install automatic chemical-feed equipment for condenser water and include the following:

1. Install makeup-water softener.

2. Install water meter in makeup-water supply.

3. Install inhibitor injection pumps and solution tanks with injection timer sensing contacts in water meter.

a. Pumps shall operate for timed interval on contact closure at water meter in makeup-water supply connection.

4. Install TSS controller with sensor and bleed valves.

a. Bleed valves shall cycle to maintain maximum TSS concentration.

5. Install pH sensor and controller with injection pumps and solution tanks.

a. Injector pumps shall operate to maintain required pH.

6. Install biocide feeder alternating timer with two sets of injection pumps and solution tanks.

a. Injection pumps shall operate to feed biocide on an alternating basis.

Coordinate piping installations and specialty arrangements with Drawings and with requirements specified in piping systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

G. Piping installation requirements are specified in other Sections. Drawings indicate general arrangement of piping, fittings, and specialties.

H. Where installing piping adjacent to equipment, allow space for service and maintenance.

I. Make piping connections between HVAC water-treatment equipment and dissimilar-metal piping with dielectric fittings. Dielectric fittings are specified in Section 232113 "Hydronic Piping."

J. Install shutoff valves on HVAC water-treatment equipment inlet and outlet. Metal general-duty valves are specified in Section 230523 "General-Duty Valves for HVAC Piping."

K. See Section 221119 "Domestic Water Piping Specialties" for backflow preventers required in makeup-water connections to potable-water systems.

L. Confirm applicable electrical requirements in electrical Sections for connecting electrical equipment.

M. Ground equipment according to Section 260526 "Grounding and Bonding for Electrical Systems."

N. Connect wiring according to Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

3.3 FIELD QUALITY CONTROL

A. Perform the following tests and inspections[ with the assistance of a factory-authorized service representative]:

1. Inspect field-assembled components and equipment installation, including piping and electrical connections.

2. Inspect piping and equipment to determine that systems and equipment have been cleaned, flushed, and filled with water, and are fully operational before introducing chemicals for water-treatment system.

3. Place HVAC water-treatment system into operation and calibrate controls during the preliminary phase of HVAC system's startup procedures.

4. Do not enclose, cover, or put piping into operation until it is tested and satisfactory test results are achieved.

5. Test for leaks and defects. If testing is performed in segments, submit separate report for each test, complete with diagram of portion of piping tested.

6. Leave uncovered and unconcealed new, altered, extended, and replaced water piping until it has been tested and approved. Expose work that has been covered or concealed before it has been tested and approved.

7. Cap and subject piping to static water pressure of 50 psig (345 kPa) above operating pressure, without exceeding pressure rating of piping system materials. Isolate test source and allow test pressure to stand for four hours. Leaks and loss in test pressure constitute defects.

8. Repair leaks and defects with new materials and retest piping until no leaks exist.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

B. Equipment will be considered defective if it does not pass tests and inspections.

C. Prepare test and inspection reports.

3.4 DEMONSTRATION

A. Train Owner's maintenance personnel to adjust, operate, and maintain HVAC water-treatment systems and equipment.

END OF SECTION 232500

	HVAC WATER TREATMENT
	232500 - 1



