Copyright 2011 AIA
MasterSpec Professional
09/11

Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 233113 - METAL DUCTS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Rectangular ducts and fittings.

2. Round ducts and fittings.

3. Sheet metal materials.

4. Sealants and gaskets.

5. Hangers and supports.

6. Seismic-restraint devices.

B. Related Sections:

Retain Sections in subparagraphs below that contain requirements Contractor might expect to find in this Section but are specified in other Sections.

1. Section 230593 "Testing, Adjusting, and Balancing for HVAC" for testing, adjusting, and balancing requirements for metal ducts.

2. Section 233116 "Nonmetal Ducts" for fibrous-glass ducts, thermoset fiber-reinforced plastic ducts, thermoplastic ducts, PVC ducts, and concrete ducts.

3. Section 233119 "HVAC Casings" for factory- and field-fabricated casings for mechanical equipment.

4. Section 233300 "Air Duct Accessories" for dampers, sound-control devices, duct-mounting access doors and panels, turning vanes, and flexible ducts.

1.2 PERFORMANCE REQUIREMENTS

Retain first paragraph below if Contractor is required to assume responsibility for duct construction design.

A. Delegated Duct Design: Duct construction, including sheet metal thicknesses, seam and joint construction, reinforcements, and hangers and supports, shall comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible" and performance requirements and design criteria indicated in "Duct Schedule" Article.

Retain seismic options and design criteria in first paragraph below that are approved by authorities having jurisdiction.

B. Structural Performance: Duct hangers and supports[ and seismic restraints] shall withstand the effects of gravity[ and seismic] loads and stresses within limits and under conditions described in SMACNA's "HVAC Duct Construction Standards - Metal and Flexible" [and] [ASCE/SEI 7.] [SMACNA's "Seismic Restraint Manual: Guidelines for Mechanical Systems."] <Insert document.>

Retain one of three subparagraphs below if retaining "SMACNA's 'Seismic Restraint Manual: Guidelines for Mechanical Systems'" option in paragraph above. If using other seismic design criteria, delete three subparagraphs below.

1. Seismic Hazard Level A: Seismic force to weight ratio, 0.48.

2. Seismic Hazard Level B: Seismic force to weight ratio, 0.30.

3. Seismic Hazard Level C: Seismic force to weight ratio, 0.15.

Retain paragraph below to comply with LEED Prerequisite IEQ 1.

C. Airstream Surfaces: Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1.

1.3 ACTION SUBMITTALS

A. Product Data: For each type of product indicated.

B. LEED Submittals:

1. Product Data for Prerequisite IEQ 1: Documentation indicating that duct systems comply with ASHRAE 62.1, Section 5 - "Systems and Equipment."

2. Product Data for Prerequisite EA 2: Documentation indicating that duct systems comply with ASHRAE/IESNA 90.1, Section 6.4.4 - "HVAC System Construction and Insulation."

Retain first subparagraph below if retaining "Duct Cleaning" Article.

3. Duct-Cleaning Test Report for Prerequisite IEQ 1: Documentation of work performed for compliance with ASHRAE 62.1, Section 7.2.4 - "Ventilation System Start-up."

"Product Data for Credit IEQ 4.1" Subparagraph below applies to LEED-NC, LEED-CI, and LEED-CS; coordinate with requirements for adhesives and sealants.

4. Product Data for Credit IEQ 4.1: For adhesives and sealants, documentation including printed statement of VOC content.

"Laboratory Test Reports for Credit IEQ 4" Subparagraph below applies to LEED for Schools.

5. Laboratory Test Reports for Credit IEQ 4: For adhesives and sealants, documentation indicating that products comply with the testing and product requirements of the California Department of Health Services' "Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers."

C. Shop Drawings:

1. Fabrication, assembly, and installation, including plans, elevations, sections, components, and attachments to other work.

2. Factory- and shop-fabricated ducts and fittings.

3. Duct layout indicating sizes, configuration, and static-pressure classes.

4. Elevation of top of ducts.

5. Dimensions of main duct runs from building grid lines.

6. Fittings.

7. Reinforcement and spacing.

8. Seam and joint construction.

9. Penetrations through fire-rated and other partitions.

10. Equipment installation based on equipment being used on Project.

11. Locations for duct accessories, including dampers, turning vanes, and access doors and panels.

12. Hangers and supports, including methods for duct and building attachment[, seismic restraints,] and vibration isolation.

13. <Insert lists of areas or systems requiring Shop Drawings.>

Paragraph below is defined in Section 013300 "Submittal Procedures" as a "Delegated-Design Submittal." Retain with "Performance Requirements" Article if design responsibilities have been delegated to Contractor.

D. Delegated-Design Submittal:

1. Sheet metal thicknesses.

2. Joint and seam construction and sealing.

3. Reinforcement details and spacing.

4. Materials, fabrication, assembly, and spacing of hangers and supports.

Retain subparagraph below if Work of this Section is required to withstand specific design loads and design responsibilities have been delegated to Contractor as another way to verify compliance with performance requirements. Professional engineer qualifications are specified in Section 014000 "Quality Requirements."

5. Design Calculations: Calculations[, including analysis data signed and sealed by the qualified professional engineer responsible for their preparation] for selecting hangers and supports[ and seismic restraints].

1.4 INFORMATIONAL SUBMITTALS

Retain first paragraph below if Drawings do not include detailed plans or if Project involves unusual coordination requirements.

A. Coordination Drawings: Plans, drawn to scale, on which the following items are shown and coordinated with each other, using input from installers of the items involved:

1. Duct installation in congested spaces, indicating coordination with general construction, building components, and other building services. Indicate proposed changes to duct layout.

2. Suspended ceiling components.

3. Structural members to which duct will be attached.

4. Size and location of initial access modules for acoustical tile.

5. Penetrations of smoke barriers and fire-rated construction.

6. Items penetrating finished ceiling including the following:

a. Lighting fixtures.

b. Air outlets and inlets.

c. Speakers.

d. Sprinklers.

e. Access panels.

f. Perimeter moldings.

g. <Insert item>.

Retain paragraph below if retaining procedures for welder certification in "Quality Assurance" Article.

B. Welding certificates.

1.5 QUALITY ASSURANCE

Retain one of first two paragraphs below if welding is required. If retaining, also retain "Welding certificates" Paragraph in "Informational Submittals" Article. Retain first paragraph if only one AWS standard is applicable. Retain second paragraph if more than one AWS standard is referenced.

A. Welding Qualifications: Qualify procedures and personnel according to [AWS D1.1/D1.1M, "Structural Welding Code - Steel," for hangers and supports.] [AWS D1.2/D1.2M, "Structural Welding Code - Aluminum," for aluminum supports.] [AWS D9.1M/D9.1, "Sheet Metal Welding Code," for duct joint and seam welding.]

B. Welding Qualifications: Qualify procedures and personnel according to the following:

Retain applicable subparagraphs below.

1. AWS D1.1/D1.1M, "Structural Welding Code - Steel," for hangers and supports.

2. AWS D1.2/D1.2M, "Structural Welding Code - Aluminum," for aluminum supports.

3. AWS D9.1M/D9.1, "Sheet Metal Welding Code," for duct joint and seam welding.

Retain two paragraphs below if applying for LEED certification or if requiring compliance with ASHRAE or ASHRAE/IESNA.

LEED Prerequisite IEQ 1 requires compliance with requirements in ASHRAE 62.1.

C. ASHRAE Compliance: Applicable requirements in ASHRAE 62.1, Section 5 - "Systems and Equipment" and Section 7 - "Construction and System Start-up."

LEED Prerequisite EA 2 requires compliance with requirements in ASHRAE/IESNA 90.1.

D. ASHRAE/IESNA Compliance: Applicable requirements in ASHRAE/IESNA 90.1, Section 6.4.4 - "HVAC System Construction and Insulation."

PART 2 -  PRODUCTS

2.1 RECTANGULAR DUCTS AND FITTINGS

See "Static-Pressure Classes" and "Leakage and Seal Classes" articles in the Evaluations for discussion on fabrication.

A. General Fabrication Requirements: Comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible" based on indicated static-pressure class unless otherwise indicated.

B. Transverse Joints: Select joint types and fabricate according to SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Figure 2-1, "Rectangular Duct/Transverse Joints," for static-pressure class, applicable sealing requirements, materials involved, duct-support intervals, and other provisions in SMACNA's "HVAC Duct Construction Standards - Metal and Flexible."

C. Longitudinal Seams: Select seam types and fabricate according to SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Figure 2-2, "Rectangular Duct/Longitudinal Seams," for static-pressure class, applicable sealing requirements, materials involved, duct-support intervals, and other provisions in SMACNA's "HVAC Duct Construction Standards - Metal and Flexible."

D. Elbows, Transitions, Offsets, Branch Connections, and Other Duct Construction: Select types and fabricate according to SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Chapter 4, "Fittings and Other Construction," for static-pressure class, applicable sealing requirements, materials involved, duct-support intervals, and other provisions in SMACNA's "HVAC Duct Construction Standards - Metal and Flexible."

2.2 ROUND DUCTS AND FITTINGS

See "Static-Pressure Classes" and "Leakage and Seal Classes" articles in the Evaluations for discussion on fabrication.

A. General Fabrication Requirements: Comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Chapter 3, "Round, Oval, and Flexible Duct," based on indicated static-pressure class unless otherwise indicated.

Retain subparagraph below to require factory-fabricated, round ducts and fittings; delete to allow shop-fabricated ducts and fittings.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain subparagraph and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Lindab Inc.

b. McGill AirFlow LLC.

c. SEMCO Incorporated.

d. Sheet Metal Connectors, Inc.

e. Spiral Manufacturing Co., Inc.

f. <Insert manufacturer's name>.

B. Transverse Joints: Select joint types and fabricate according to SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Figure 3-1, "Round Duct Transverse Joints," for static-pressure class, applicable sealing requirements, materials involved, duct-support intervals, and other provisions in SMACNA's "HVAC Duct Construction Standards - Metal and Flexible."

Option in subparagraph below is SMACNA's requirement. Insert smaller dimension for more stringent requirement.

1. Transverse Joints in Ducts Larger Than [60 Inches (1524 mm)] <Insert dimension> in Diameter: Flanged.

C. Longitudinal Seams: Select seam types and fabricate according to SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Figure 3-2, "Round Duct Longitudinal Seams," for static-pressure class, applicable sealing requirements, materials involved, duct-support intervals, and other provisions in SMACNA's "HVAC Duct Construction Standards - Metal and Flexible."

1. Fabricate round ducts larger Than 90 inches (2286 mm) in diameter with butt-welded longitudinal seams.

D. Tees and Laterals: Select types and fabricate according to SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Figure 3-5, "90 Degree Tees and Laterals," and Figure 3-6, "Conical Tees," for static-pressure class, applicable sealing requirements, materials involved, duct-support intervals, and other provisions in SMACNA's "HVAC Duct Construction Standards - Metal and Flexible."

2.3 SHEET METAL MATERIALS

A. General Material Requirements: Comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible" for acceptable materials, material thicknesses, and duct construction methods unless otherwise indicated. Sheet metal materials shall be free of pitting, seam marks, roller marks, stains, discolorations, and other imperfections.

See "Sheet Metal Materials" Article in the Evaluations for discussion on applicable materials and coatings in first four paragraphs below.

B. Galvanized Sheet Steel: Comply with ASTM A 653/A 653M.

1. Galvanized Coating Designation: [G60 (Z180)] [G90 (Z275)].

2. Finishes for Surfaces Exposed to View: Mill phosphatized.

C. Carbon-Steel Sheets: Comply with ASTM A 1008/A 1008M, with oiled, matte finish for exposed ducts.

D. Stainless-Steel Sheets: Comply with ASTM A 480/A 480M, Type 304 or 316, as indicated in the "Duct Schedule" Article; cold rolled, annealed, sheet. Exposed surface finish shall be No. 2B, No. 2D, No. 3, or No. 4 as indicated in the "Duct Schedule" Article.

E. Aluminum Sheets: Comply with ASTM B 209 (ASTM B 209M) Alloy 3003, H14 temper; with mill finish for concealed ducts, and standard, one-side bright finish for duct surfaces exposed to view.

F. Reinforcement Shapes and Plates: ASTM A 36/A 36M, steel plates, shapes, and bars; black and galvanized.

1. Where black- and galvanized-steel shapes and plates are used to reinforce aluminum ducts, isolate the different metals with butyl rubber, neoprene, or EPDM gasket materials.

G. Tie Rods: Galvanized steel, 1/4-inch (6-mm) minimum diameter for lengths 36 inches (900 mm) or less; 3/8-inch (10-mm) minimum diameter for lengths longer than 36 inches (900 mm).

2.4 SEALANT AND GASKETS

A. General Sealant and Gasket Requirements: Surface-burning characteristics for sealants and gaskets shall be a maximum flame-spread index of 25 and a maximum smoke-developed index of 50 when tested according to UL 723; certified by an NRTL.

See SMACNA's "HVAC Duct Construction Standards - Metal and Flexible" for discussion on seam and joint sealing methods and their applications. Retain one or both of first two paragraphs below, and identify which sealing system applies to which duct system in the "Duct Schedule" Article.

B. Two-Part Tape Sealing System:

1. Tape: Woven cotton fiber impregnated with mineral gypsum and modified acrylic/silicone activator to react exothermically with tape to form hard, durable, airtight seal.

2. Tape Width: [3 inches (76 mm)] [4 inches (102 mm)] [6 inches (152 mm)].

3. Sealant: Modified styrene acrylic.

4. Water resistant.

5. Mold and mildew resistant.

6. Maximum Static-Pressure Class: 10-inch wg (2500 Pa), positive and negative.

7. Service: Indoor and outdoor.

8. Service Temperature: Minus 40 to plus 200 deg F (Minus 40 to plus 93 deg C).

9. Substrate: Compatible with galvanized sheet steel (both PVC coated and bare), stainless steel, or aluminum.

One or both subparagraphs below may be required to comply with Project requirements or authorities having jurisdiction. Retain first subparagraph below if required for LEED-NC, LEED-CI, or LEED-CS Credit IEQ 4.1.

10. For indoor applications, sealant shall have a VOC content of 250 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

Retain subparagraph below if required for LEED for Schools Credit IEQ 4.

11. Sealant shall comply with the testing and product requirements of the California Department of Health Services' "Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers."

C. Water-Based Joint and Seam Sealant:

1. Application Method: Brush on.

2. Solids Content: Minimum 65 percent.

3. Shore A Hardness: Minimum 20.

4. Water resistant.

5. Mold and mildew resistant.

6. VOC: Maximum 75 g/L (less water).

7. Maximum Static-Pressure Class: 10-inch wg (2500 Pa), positive and negative.

8. Service: Indoor or outdoor.

9. Substrate: Compatible with galvanized sheet steel (both PVC coated and bare), stainless steel, or aluminum sheets.

D. Flanged Joint Sealant: Comply with ASTM C 920.

1. General: Single-component, acid-curing, silicone, elastomeric.

2. Type: S.

3. Grade: NS.

4. Class: 25.

5. Use: O.

One or both subparagraphs below may be required to comply with Project requirements or authorities having jurisdiction. Retain first subparagraph below if required for LEED-NC, LEED-CI, or LEED-CS Credit IEQ 4.1.

6. For indoor applications, sealant shall have a VOC content of 250 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

Retain subparagraph below if required for LEED for Schools Credit IEQ 4.

7. Sealant shall comply with the testing and product requirements of the California Department of Health Services' "Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers."

E. Flange Gaskets: Butyl rubber, neoprene, or EPDM polymer with polyisobutylene plasticizer.

O-ring seals are generally available for duct fittings 3 to 24 inches (76 to 610 mm) in diameter.

F. Round Duct Joint O-Ring Seals:

1. Seal shall provide maximum leakage class of3 cfm/100 sq. ft. at 1-inch wg (0.14 L/s per sq. m) and shall be rated for10-inch wg (2500-Pa) static-pressure class, positive or negative.

Retain one or both subparagraphs below. These are proprietary seals provided on factory-fabricated, round duct fitting joints and constructed with specific dimensions to ensure a proper seal.

2. EPDM O-ring to seal in concave bead in coupling or fitting spigot.

3. Double-lipped, EPDM O-ring seal, mechanically fastened to factory-fabricated couplings and fitting spigots.

2.5 HANGERS AND SUPPORTS

Indicate the extent of corrosive environment on Drawings.

A. Hanger Rods for Noncorrosive Environments: Cadmium-plated steel rods and nuts.

B. Hanger Rods for Corrosive Environments: Electrogalvanized, all-thread rods or galvanized rods with threads painted with zinc-chromate primer after installation.

C. Strap and Rod Sizes: Comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Table 5-1 (Table 5-1M), "Rectangular Duct Hangers Minimum Size," and Table 5-2, "Minimum Hanger Sizes for Round Duct."

D. Steel Cables for Galvanized-Steel Ducts: Galvanized steel complying with ASTM A 603.

E. Steel Cables for Stainless-Steel Ducts: Stainless steel complying with ASTM A 492.

F. Steel Cable End Connections: Cadmium-plated steel assemblies with brackets, swivel, and bolts designed for duct hanger service; with an automatic-locking and clamping device.

G. Duct Attachments: Sheet metal screws, blind rivets, or self-tapping metal screws; compatible with duct materials.

H. Trapeze and Riser Supports:

1. Supports for Galvanized-Steel Ducts: Galvanized-steel shapes and plates.

2. Supports for Stainless-Steel Ducts: Stainless-steel shapes and plates.

3. Supports for Aluminum Ducts: Aluminum or galvanized steel coated with zinc chromate.

2.6 SEISMIC-RESTRAINT DEVICES

Coordinate specifications for seismic-restraint components in this article with structural engineer and with Drawings. See the "Seismic Considerations" Article in the Evaluations for discussion on seismic restraints.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain first paragraph and list of manufacturers below. See Section 016000 "Product Requirements."

A. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

1. Cooper B-Line, Inc.; a division of Cooper Industries.

2. Ductmate Industries, Inc.

3. Hilti Corp.

4. Kinetics Noise Control.

5. Loos & Co.; Cableware Division.

6. Mason Industries.

7. TOLCO; a brand of NIBCO INC.

8. Unistrut Corporation; Tyco International, Ltd.

9. <Insert manufacturer's name>.

See the Evaluations in Section 230548 "Vibration and Seismic Controls for HVAC" for discussion on seismic-restraint capacities and rating services.

B. General Requirements for Restraint Components: Rated strengths, features, and applications shall be as defined in reports by [an evaluation service member of the ICC Evaluation Service] [the Office of Statewide Health Planning and Development for the State of California] [an agency acceptable to authorities having jurisdiction].

1. Structural Safety Factor: Allowable strength in tension, shear, and pullout force of components shall be at least [four] <Insert number> times the maximum seismic forces to which they will be subjected.

C. Channel Support System: Shop- or field-fabricated support assembly made of slotted steel channels rated in tension, compression, and torsion forces and with accessories for attachment to braced component at one end and to building structure at the other end. Include matching components and corrosion-resistant coating.

D. Restraint Cables: [ASTM A 603, galvanized] [ASTM A 492, stainless]-steel cables with end connections made of cadmium-plated steel assemblies with brackets, swivel, and bolts designed for restraining cable service; and with an automatic-locking and clamping device or double-cable clips.

Retain first paragraph below for strengthening resistance of hanger rods against seismic forces that may cause rods to buckle. Use with either channel- or cable-type bracing assemblies. Detail fabrication and indicate locations on Drawings.

E. Hanger Rod Stiffener: [Steel tube or steel slotted-support-system sleeve with internally bolted connections] [Reinforcing steel angle clamped] to hanger rod.

F. Mechanical Anchor Bolts: Drilled-in and stud-wedge or female-wedge type. Select anchor bolts with strength required for anchor and as tested according to ASTM E 488.

PART 3 -  EXECUTION

3.1 DUCT INSTALLATION

Coordinate duct layout and duct accessory arrangement with Drawings.

A. Drawing plans, schematics, and diagrams indicate general location and arrangement of duct system. Indicated duct locations, configurations, and arrangements were used to size ducts and calculate friction loss for air-handling equipment sizing and for other design considerations. Install duct systems as indicated unless deviations to layout are approved on Shop Drawings and Coordination Drawings.

B. Install ducts according to SMACNA's "HVAC Duct Construction Standards - Metal and Flexible" unless otherwise indicated.

C. Install round ducts in maximum practical lengths.

D. Install ducts with fewest possible joints.

E. Install factory- or shop-fabricated fittings for changes in direction, size, and shape and for branch connections.

F. Unless otherwise indicated, install ducts vertically and horizontally, and parallel and perpendicular to building lines.

G. Install ducts close to walls, overhead construction, columns, and other structural and permanent enclosure elements of building.

H. Install ducts with a clearance of 1 inch (25 mm), plus allowance for insulation thickness.

I. Route ducts to avoid passing through transformer vaults and electrical equipment rooms and enclosures.

J. Where ducts pass through non-fire-rated interior partitions and exterior walls and are exposed to view, cover the opening between the partition and duct or duct insulation with sheet metal flanges of same metal thickness as the duct. Overlap openings on four sides by at least 1-1/2 inches (38 mm).

K. Where ducts pass through fire-rated interior partitions and exterior walls, install fire dampers. Comply with requirements in Section 233300 "Air Duct Accessories" for fire and smoke dampers.

L. Protect duct interiors from moisture, construction debris and dust, and other foreign materials.[ Comply with SMACNA's "IAQ Guidelines for Occupied Buildings Under Construction," Appendix G, "Duct Cleanliness for New Construction Guidelines."]

3.2 INSTALLATION OF EXPOSED DUCTWORK

A. Protect ducts exposed in finished spaces from being dented, scratched, or damaged.

B. Trim duct sealants flush with metal. Create a smooth and uniform exposed bead. Do not use two-part tape sealing system.

C. Grind welds to provide smooth surface free of burrs, sharp edges, and weld splatter. When welding stainless steel with a No. 3 or 4 finish, grind the welds flush, polish the exposed welds, and treat the welds to remove discoloration caused by welding.

D. Maintain consistency, symmetry, and uniformity in the arrangement and fabrication of fittings, hangers and supports, duct accessories, and air outlets.

E. Repair or replace damaged sections and finished work that does not comply with these requirements.

3.3 ADDITIONAL INSTALLATION REQUIREMENTS FOR COMMERCIAL KITCHEN HOOD EXHAUST DUCT

Delete this article if exhaust ducts for commercial kitchen hoods are specified in Section 235100 "Breechings, Chimneys, and Stacks."

A. Install commercial kitchen hood exhaust ducts without dips and traps that may hold grease, and sloped a minimum of 2 percent to drain grease back to the hood.

B. Install fire-rated access panel assemblies at each change in direction and at maximum intervals of [20 feet (6 m)] [12 feet (3.7 m)] <Insert dimension> in horizontal ducts, and at every floor for vertical ducts, or as indicated on Drawings. Locate access panel on top or sides of duct a minimum of 1-1/2 inches (38 mm) from bottom of duct.

C. Do not penetrate fire-rated assemblies except as allowed by applicable building codes and authorities having jurisdiction.

3.4 DUCT SEALING

Retain one of two paragraphs below. Retain first paragraph if retaining subparagraphs for seal class and leakage class in "Duct Schedule" Article; otherwise, delete first and retain second paragraph.

A. Seal ducts for duct static-pressure, seal classes, and leakage classes specified in "Duct Schedule" Article according to SMACNA's "HVAC Duct Construction Standards - Metal and Flexible."

B. Seal ducts to the following seal classes according to SMACNA's "HVAC Duct Construction Standards - Metal and Flexible":

1. Comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible."

2. Outdoor, Supply-Air Ducts: Seal Class A.

3. Outdoor, Exhaust Ducts: Seal Class C.

4. Outdoor, Return-Air Ducts: Seal Class C.

5. Unconditioned Space, Supply-Air Ducts in Pressure Classes 2-Inch wg (500 Pa) and Lower: Seal Class B.

6. Unconditioned Space, Supply-Air Ducts in Pressure Classes Higher Than 2-Inch wg (500 Pa): Seal Class A.

7. Unconditioned Space, Exhaust Ducts: Seal Class C.

8. Unconditioned Space, Return-Air Ducts: Seal Class B.

9. Conditioned Space, Supply-Air Ducts in Pressure Classes 2-Inch wg (500 Pa) and Lower: Seal Class C.

10. Conditioned Space, Supply-Air Ducts in Pressure Classes Higher Than 2-Inch wg (500 Pa): Seal Class B.

11. Conditioned Space, Exhaust Ducts: Seal Class B.

12. Conditioned Space, Return-Air Ducts: Seal Class C.

3.5 HANGER AND SUPPORT INSTALLATION

A. Comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Chapter 5, "Hangers and Supports."

Verify attachment selection and spacing in first two paragraphs below with structural engineer.

B. Building Attachments: Concrete inserts, powder-actuated fasteners, or structural-steel fasteners appropriate for construction materials to which hangers are being attached.

1. Where practical, install concrete inserts before placing concrete.

2. Install powder-actuated concrete fasteners after concrete is placed and completely cured.

3. Use powder-actuated concrete fasteners for standard-weight aggregate concretes or for slabs more than 4 inches (100 mm) thick.

4. Do not use powder-actuated concrete fasteners for lightweight-aggregate concretes or for slabs less than 4 inches (100 mm) thick.

Retain subparagraph below for Projects that require seismic restraints.

5. Do not use powder-actuated concrete fasteners for seismic restraints.

C. Hanger Spacing: Comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Table 5-1 (Table 5-1M), "Rectangular Duct Hangers Minimum Size," and Table 5-2, "Minimum Hanger Sizes for Round Duct," for maximum hanger spacing; install hangers and supports within 24 inches (610 mm) of each elbow and within 48 inches (1200 mm) of each branch intersection.

D. Hangers Exposed to View: Threaded rod and angle or channel supports.

E. Support vertical ducts with steel angles or channel secured to the sides of the duct with welds, bolts, sheet metal screws, or blind rivets; support at each floor and at a maximum intervals of 16 feet (5 m).

F. Install upper attachments to structures. Select and size upper attachments with pull-out, tension, and shear capacities appropriate for supported loads and building materials where used.

3.6 SEISMIC-RESTRAINT-DEVICE INSTALLATION

A. Install ducts with hangers and braces designed to support the duct and to restrain against seismic forces required by applicable building codes. Comply with [SMACNA's "Seismic Restraint Manual: Guidelines for Mechanical Systems."] [ASCE/SEI 7.]

Options for 40 and 80 feet (12 and 24 m) in first subparagraph below are recommended by SMACNA's "Seismic Restraint Manual: Guidelines for Mechanical Systems." Revise these dimensions based on the configuration of duct and the seismic hazard.

1. Space lateral supports a maximum of [40 feet (12 m)] <Insert dimension> o.c., and longitudinal supports a maximum of [80 feet (24 m)] <Insert dimension> o.c.

2. Brace a change of direction longer than 12 feet (3.7 m).

B. Select seismic-restraint devices with capacities adequate to carry present and future static and seismic loads.

C. Install cables so they do not bend across edges of adjacent equipment or building structure.

D. Install cable restraints on ducts that are suspended with vibration isolators.

E. Install seismic-restraint devices using methods approved by [an evaluation service member of the ICC Evaluation Service] [the Office of Statewide Health Planning and Development for the State of California] [an agency acceptable to authorities having jurisdiction].

F. Attachment to Structure: If specific attachment is not indicated, anchor bracing and restraints to structure, to flanges of beams, to upper truss chords of bar joists, or to concrete members.

G. Drilling for and Setting Anchors:

1. Identify position of reinforcing steel and other embedded items prior to drilling holes for anchors. Do not damage existing reinforcement or embedded items during drilling. Notify the Architect if reinforcing steel or other embedded items are encountered during drilling. Locate and avoid prestressed tendons, electrical and telecommunications conduit, and gas lines.

2. Do not drill holes in concrete or masonry until concrete, mortar, or grout has achieved full design strength.

3. Wedge Anchors: Protect threads from damage during anchor installation. Heavy-duty sleeve anchors shall be installed with sleeve fully engaged in the structural element to which anchor is to be fastened.

4. Set anchors to manufacturer's recommended torque, using a torque wrench.

5. Install zinc-coated steel anchors for interior applications and stainless-steel anchors for applications exposed to weather.

3.7 CONNECTIONS

Coordinate duct installations and specialty arrangements with Drawings.

A. Make connections to equipment with flexible connectors complying with Section 233300 "Air Duct Accessories."

B. Comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible" for branch, outlet and inlet, and terminal unit connections.

3.8 DUCT CLEANING

Retain this article for applications where construction dust and debris in duct system must be removed before air-system operation, or if applying for LEED certification.

LEED Prerequisite IEQ 1 requires compliance with ASHRAE 62.1, in which Section 7.2.4 - "Ventilation System Start-up" requires that distribution systems be clean of dirt and debris.

A. Clean [new] [and] [existing] duct system(s) before testing, adjusting, and balancing.

B. Use service openings for entry and inspection.

1. Create new openings and install access panels appropriate for duct static-pressure class if required for cleaning access. Provide insulated panels for insulated or lined duct. Patch insulation and liner as recommended by duct liner manufacturer. Comply with Section 233300 "Air Duct Accessories" for access panels and doors.

2. Disconnect and reconnect flexible ducts as needed for cleaning and inspection.

3. Remove and reinstall ceiling to gain access during the cleaning process.

C. Particulate Collection and Odor Control:

1. When venting vacuuming system inside the building, use HEPA filtration with 99.97 percent collection efficiency for 0.3-micron-size (or larger) particles.

2. When venting vacuuming system to outdoors, use filter to collect debris removed from HVAC system, and locate exhaust downwind and away from air intakes and other points of entry into building.

D. Clean the following components by removing surface contaminants and deposits:

1. Air outlets and inlets (registers, grilles, and diffusers).

2. Supply, return, and exhaust fans including fan housings, plenums (except ceiling supply and return plenums), scrolls, blades or vanes, shafts, baffles, dampers, and drive assemblies.

3. Air-handling unit internal surfaces and components including mixing box, coil section, air wash systems, spray eliminators, condensate drain pans, humidifiers and dehumidifiers, filters and filter sections, and condensate collectors and drains.

4. Coils and related components.

5. Return-air ducts, dampers, actuators, and turning vanes except in ceiling plenums and mechanical equipment rooms.

6. Supply-air ducts, dampers, actuators, and turning vanes.

7. Dedicated exhaust and ventilation components and makeup air systems.

E. Mechanical Cleaning Methodology:

1. Clean metal duct systems using mechanical cleaning methods that extract contaminants from within duct systems and remove contaminants from building.

2. Use vacuum-collection devices that are operated continuously during cleaning. Connect vacuum device to downstream end of duct sections so areas being cleaned are under negative pressure.

3. Use mechanical agitation to dislodge debris adhered to interior duct surfaces without damaging integrity of metal ducts, duct liner, or duct accessories.

4. Clean fibrous-glass duct liner with HEPA vacuuming equipment; do not permit duct liner to get wet. Replace fibrous-glass duct liner that is damaged, deteriorated, or delaminated or that has friable material, mold, or fungus growth.

5. Clean coils and coil drain pans according to NADCA 1992. Keep drain pan operational. Rinse coils with clean water to remove latent residues and cleaning materials; comb and straighten fins.

6. Provide drainage and cleanup for wash-down procedures.

7. Antimicrobial Agents and Coatings: Apply EPA-registered antimicrobial agents if fungus is present. Apply antimicrobial agents according to manufacturer's written instructions after removal of surface deposits and debris.

3.9 START UP

LEED Prerequisite IEQ 1 requires compliance with ASHRAE 62.1; see Section 7 - "Construction and System Start-up."

A. Air Balance: Comply with requirements in Section 230593 "Testing, Adjusting, and Balancing for HVAC."

3.10 DUCT SCHEDULE

A. Fabricate ducts with galvanized sheet steel except as otherwise indicated and as follows:

1. Underground Ducts: Concrete-encased, [galvanized sheet steel] [PVC-coated, galvanized sheet steel with thicker coating on duct exterior] [stainless steel].

2. <Insert requirements>.

Retain applicable subparagraphs in this Article to set criteria for pressure class, duct seal-class level, and duct-leakage class; or delete applicable subparagraphs and indicate pressure class, duct seal-class level, and duct-leakage class on Drawings. If retaining duct seal and leakage requirements in this article, retain first paragraph in "Duct Sealing" Article. Both seal class and leakage class are included in this article and either one can be deleted, or both can remain if they are consistent.

Paragraphs below are examples of broad system classifications. Revise to suit Project or indicate requirements on Drawings if a more refined classification is required.

See ASHRAE duct leakage recommendations in 2005 ASHRAE HANDBOOK - "Fundamentals," Chapter 35, "Duct Design," Table 7, "Recommended Ductwork Leakage Class by Duct Type."

LEED Prerequisite EA 2 requires compliance with ASHRAE/IESNA 90.1, in which Section 6.4.4.2.1 - "Duct Sealing" requires a minimum seal-class level (A, B, or C) for various duct locations and pressures and specifies seal-class levels for joints and seams in ducts located outdoors, in unconditioned spaces, and in conditioned spaces. Retain second paragraph in "Duct Sealing" Article if applying for LEED certification and requirements are not defined in this article or on Drawings.

B. Supply Ducts:

1. Ducts Connected to Fan Coil Units, Furnaces, Heat Pumps, and Terminal Units <Insert equipment>:

a. Pressure Class: Positive [1-inch wg (250 Pa)] [2-inch wg (500 Pa)] <Insert value>.

b. Minimum SMACNA Seal Class: [A] [B] [C].

c. SMACNA Leakage Class for Rectangular: [12] [24] <Insert value>.

d. SMACNA Leakage Class for Round and Flat Oval: [12] [24] <Insert value>.

2. Ducts Connected to Constant-Volume Air-Handling Units <Insert equipment>:

a. Pressure Class: Positive [2-inch wg (500 Pa)] [3-inch wg (750 Pa)] <Insert value>.

b. Minimum SMACNA Seal Class: [A] [B].

c. SMACNA Leakage Class for Rectangular: [6] [12] [24] <Insert value>.

d. SMACNA Leakage Class for Round and Flat Oval: [6] [12] [24] <Insert value>.

3. Ducts Connected to Variable-Air-Volume Air-Handling Units <Insert equipment>:

a. Pressure Class: Positive [3-inch wg (750 Pa)] [4-inch wg (1000 Pa)] <Insert value>.

b. Minimum SMACNA Seal Class: [A] [B].

c. SMACNA Leakage Class for Rectangular: [3] [6] <Insert value>.

d. SMACNA Leakage Class for Round and Flat Oval: [3] [6] <Insert value>.

4. Ducts Connected to Equipment Not Listed Above:

a. Pressure Class: Positive [2-inch wg (500 Pa)] [3-inch wg (750 Pa)] [4-inch wg (1000 Pa)] <Insert value>.

b. Minimum SMACNA Seal Class: [A] [B].

c. SMACNA Leakage Class for Rectangular: [3] [6] [12] <Insert value>.

d. SMACNA Leakage Class for Round and Flat Oval: [3] [6] [12] <Insert value>.

C. Return Ducts:

1. Ducts Connected to Fan Coil Units, Furnaces, Heat Pumps, and Terminal Units <Insert equipment>:

a. Pressure Class: Positive or negative [1-inch wg (250 Pa)] [2-inch wg (500 Pa)] <Insert value>.

b. Minimum SMACNA Seal Class: [A] [B] [C].

c. SMACNA Leakage Class for Rectangular: [12] [24] <Insert value>.

d. SMACNA Leakage Class for Round and Flat Oval: [12] [24] <Insert value>.

2. Ducts Connected to Air-Handling Units <Insert equipment>:

a. Pressure Class: Positive or negative [2-inch wg (500 Pa)] [3-inch wg (750 Pa)] <Insert value>.

b. Minimum SMACNA Seal Class: [A] [B].

c. SMACNA Leakage Class for Rectangular: [6] [12] [24] <Insert value>.

d. SMACNA Leakage Class for Round and Flat Oval: [6] [12] [24] <Insert value>.

3. Ducts Connected to Equipment Not Listed Above:

a. Pressure Class: Positive or negative [2-inch wg (500 Pa)] [3-inch wg (750 Pa)] [4-inch wg (1000 Pa)] <Insert value>.

b. Minimum SMACNA Seal Class: [A] [B].

c. SMACNA Leakage Class for Rectangular: [3] [6] [12] <Insert value>.

d. SMACNA Leakage Class for Round and Flat Oval: [3] [6] [12] <Insert value>.

D. Exhaust Ducts:

1. Ducts Connected to Fans Exhausting (ASHRAE 62.1, Class 1 and 2) Air:

a. Pressure Class: Negative [1-inch wg (250 Pa)] [2-inch wg (500 Pa)] [3-inch wg (750 Pa)] <Insert value>.

b. Minimum SMACNA Seal Class: [A] [B] [C] if negative pressure, and A if positive pressure.

c. SMACNA Leakage Class for Rectangular: [12] [24] <Insert value>.

d. SMACNA Leakage Class for Round and Flat Oval: [6] [12] [24] <Insert value>.

2. Ducts Connected to Air-Handling Units <Insert equipment>:

a. Pressure Class: Positive or negative [2-inch wg (500 Pa)] [3-inch wg (750 Pa)] <Insert value>.

b. Minimum SMACNA Seal Class: [A] [B] if negative pressure, and A if positive pressure.

c. SMACNA Leakage Class for Rectangular: [6] [12] [24] <Insert value>.

d. SMACNA Leakage Class for Round and Flat Oval: [3] [6] [12] [24] <Insert value>.

Retain first subparagraph below unless fire-rated, factory-fabricated grease ducts for Type I commercial kitchen hoods are specified in Section 235100 "Breechings, Chimneys, and Stacks." Factory-fabricated and -insulated grease ducts can be installed with reduced clearance to combustible construction.

3. Ducts Connected to Commercial Kitchen Hoods: Comply with NFPA 96.

a. Exposed to View: Type 304, stainless-steel sheet, [No. 4] [No. 3] <Insert finish> finish.

b. Concealed: [Type 304, stainless-steel sheet, No. 2D finish] [Carbon-steel sheet].

c. Welded seams and joints.

d. Pressure Class: Positive or negative [2-inch wg (500 Pa)] [3-inch wg (750 Pa)] [4-inch wg (1000 Pa)] <Insert value>.

e. Minimum SMACNA Seal Class: Welded seams, joints, and penetrations.

f. SMACNA Leakage Class: 3.

4. Ducts Connected to Dishwasher Hoods:

a. Type 304, stainless-steel sheet.

b. Exposed to View: [No. 4] [No. 3] <Insert finish> finish.

c. Concealed: [No. 2D] <Insert finish> finish.

d. Welded seams and flanged joints with watertight EPDM gaskets.

e. Pressure Class: Positive or negative [2-inch wg (500 Pa)] [3-inch wg (750 Pa)] <Insert value>.

f. Minimum SMACNA Seal Class: Welded seams, joints, and penetrations.

g. SMACNA Leakage Class: 3.

5. Ducts Connected to Fans Exhausting Laboratory and Process (ASHRAE 62.1, Class 3 and 4) Air:

Retain one of first two subparagraphs below.

a. [Type 316] [Type 304], stainless-steel sheet.

1) Exposed to View: [No. 4] [No. 3] <Insert finish> finish.

2) Concealed: [No. 2B] [No. 2D] <Insert finish> finish.

b. PVC-coated, galvanized sheet steel with thicker coating on duct interior.

c. Pressure Class: Positive or negative [3-inch wg (750 Pa)] [4-inch wg (1000 Pa)] [6-inch wg (1500 Pa)] <Insert value>.

d. Minimum SMACNA Seal Class: [A] [Welded seams, joints, and penetrations].

e. SMACNA Leakage Class: 3.

6. Ducts Connected to Equipment Not Listed Above:

a. Pressure Class: Positive or negative [2-inch wg (500 Pa)] [3-inch wg (750 Pa)] [4-inch wg (1000 Pa)] <Insert value>.

b. Minimum SMACNA Seal Class: [A] [B] if negative pressure, and A if positive pressure.

c. SMACNA Leakage Class for Rectangular: [6] [12] [24] <Insert value>.

d. SMACNA Leakage Class for Round and Flat Oval: [3] [6] [12] [24] <Insert value>.

E. Outdoor-Air (Not Filtered, Heated, or Cooled) Ducts:

1. Ducts Connected to Fan Coil Units, Furnaces, Heat Pumps, and Terminal Units <Insert equipment>:

a. Pressure Class: Positive or negative [1-inch wg (250 Pa)] [2-inch wg (500 Pa)] <Insert value>.

b. Minimum SMACNA Seal Class: [A] [B] [C].

c. SMACNA Leakage Class for Rectangular: [12] [24] <Insert value>.

d. SMACNA Leakage Class for Round and Flat Oval: [6] [12] [24] <Insert value>.

2. Ducts Connected to Air-Handling Units <Insert equipment>:

a. Pressure Class: Positive or negative [2-inch wg (500 Pa)] [3-inch wg (750 Pa)] <Insert value>.

b. Minimum SMACNA Seal Class: [A] [B].

c. SMACNA Leakage Class for Rectangular: [6] [12] [24] <Insert value>.

d. SMACNA Leakage Class for Round and Flat Oval: [3] [6] [12] [24] <Insert value>.

3. Ducts Connected to Equipment Not Listed Above:

a. Pressure Class: Positive or negative [2-inch wg (500 Pa)] [3-inch wg (750 Pa)] [4-inch wg (1000 Pa)] <Insert value>.

b. Minimum SMACNA Seal Class: [A] [B].

c. SMACNA Leakage Class for Rectangular: [3] [6] [12] <Insert value>.

d. SMACNA Leakage Class for Round and Flat Oval: [3] [6] [12] <Insert value>.

F. Intermediate Reinforcement:

1. Galvanized-Steel Ducts: [Galvanized steel] [Carbon steel coated with zinc-chromate primer] [Galvanized steel or carbon steel coated with zinc-chromate primer].

2. PVC-Coated Ducts:

a. Exposed to Airstream: Match duct material.

b. Not Exposed to Airstream: [Galvanized] [Match duct material].

3. Stainless-Steel Ducts:

a. Exposed to Airstream: Match duct material.

b. Not Exposed to Airstream: [Galvanized] [Match duct material].

4. Aluminum Ducts: [Aluminum][or galvanized sheet steel coated with zinc chromate].

G. Elbow Configuration:

Retain one of first two subparagraphs below. Retain first subparagraph to set different requirements for various velocities. Retain second subparagraph to set the same requirements for all velocities.

1. Rectangular Duct: Comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Figure 4-2, "Rectangular Elbows."

a. Velocity 1000 fpm (5 m/s) or Lower:

1) Radius Type RE 1 with minimum 0.5 radius-to-diameter ratio.

2) Mitered Type RE 4 without vanes.

b. Velocity 1000 to 1500 fpm (5 to 7.6 m/s):

1) Radius Type RE 1 with minimum 1.0 radius-to-diameter ratio.

2) Radius Type RE 3 with minimum 0.5 radius-to-diameter ratio and two vanes.

3) Mitered Type RE 2 with vanes complying with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Figure 4-3, "Vanes and Vane Runners," and Figure 4-4, "Vane Support in Elbows."

c. Velocity 1500 fpm (7.6 m/s) or Higher:

1) Radius Type RE 1 with minimum 1.5 radius-to-diameter ratio.

2) Radius Type RE 3 with minimum 1.0 radius-to-diameter ratio and two vanes.

3) Mitered Type RE 2 with vanes complying with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Figure 4-3, "Vanes and Vane Runners," and Figure 4-4, "Vane Support in Elbows."

2. Rectangular Duct: Comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Figure 4-2, "Rectangular Elbows."

a. Radius Type RE 1 with minimum 1.5 radius-to-diameter ratio.

b. Radius Type RE 3 with minimum 1.0 radius-to-diameter ratio and two vanes.

c. Mitered Type RE 2 with vanes complying with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Figure 4-3, "Vanes and Vane Runners," and Figure 4-4, "Vane Support in Elbows."

3. Round Duct: Comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Figure 3-4, "Round Duct Elbows."

a. Minimum Radius-to-Diameter Ratio and Elbow Segments: Comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Table 3-1, "Mitered Elbows." Elbows with less than 90-degree change of direction have proportionately fewer segments.

Retain first three subparagraphs below, or delete and retain fourth subparagraph.

1) Velocity 1000 fpm (5 m/s) or Lower: 0.5 radius-to-diameter ratio and three segments for 90-degree elbow.

2) Velocity 1000 to 1500 fpm (5 to 7.6 m/s): 1.0 radius-to-diameter ratio and four segments for 90-degree elbow.

3) Velocity 1500 fpm (7.6 m/s) or Higher: 1.5 radius-to-diameter ratio and five segments for 90-degree elbow.

4) Radius-to Diameter Ratio: 1.5.

b. Round Elbows, [12 Inches (305 mm)] <Insert dimension> and Smaller in Diameter: Stamped or pleated.

c. Round Elbows, [14 Inches (356 mm)] <Insert dimension> and Larger in Diameter: [Standing seam] [Welded].

Delete paragraph below if branch fittings are detailed on Drawings.

H. Branch Configuration:

1. Rectangular Duct: Comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Figure 4-6, "Branch Connection."

a. Rectangular Main to Rectangular Branch: 45-degree entry.

b. Rectangular Main to Round Branch: Spin in.

2. Round: Comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Figure 3-5, "90 Degree Tees and Laterals," and Figure 3-6, "Conical Tees." Saddle taps are permitted in existing duct.

a. Velocity 1000 fpm (5 m/s) or Lower: 90-degree tap.

b. Velocity 1000 to 1500 fpm (5 to 7.6 m/s): Conical tap.

c. Velocity 1500 fpm (7.6 m/s) or Higher: 45-degree lateral.

END OF SECTION 233113

	METAL DUCTS
	233113 - 1



