Copyright 2011 AIA
MasterSpec Professional
09/11

Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 233119 - HVAC CASINGS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Factory-fabricated, field-assembled, [single] [double] [single- and double]-wall casings for HVAC equipment.

1.2 PERFORMANCE REQUIREMENTS

A. Structural Performance:

1. Casings shall be fabricated to withstand 133 percent of the indicated static pressure without structural failure. Wall and roof deflection at the indicated static pressure shall not exceed 1/8 inch per foot (0.97 mm per meter) of width.

a. Fabricate outdoor casings to withstand wind load of 15 lbf/sq. ft. (720 N/sq. m) and snow load of 30 lbf/sq. ft. (1440 N/sq. m).

Retain paragraph below for projects requiring seismic design. Model building codes and ASCE/SEI 7 establish criteria for buildings subject to earthquake motions. Verify requirements of authorities having jurisdiction.

B. Seismic Performance: HVAC casings shall withstand the effects of earthquake motions determined according to SMACNA's "HVAC Duct Construction Standards - Metal and Flexible" [and] [ASCE/SEI 7] <Insert requirement>.

Retain subparagraph below to define the term "withstand" as it applies to this Project. Definition varies with type of building and occupancy and is critical to valid certification. Option is used for essential facilities where equipment must operate immediately after an earthquake.

1. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified[ and the unit will be fully operational after the seismic event]."

1.3 ACTION SUBMITTALS

A. Product Data: For each type of product indicated.

B. LEED Submittals:

1. Product Data for Prerequisite IEQ 1: Documentation indicating that HVAC casings comply with ASHRAE 62.1, Section 5 - "Systems and Equipment."

2. Product Data for Prerequisite EA 2: Documentation indicating that HVAC casings comply with ASHRAE/IESNA 90.1, Section 6.4.4 - "HVAC System Construction and Insulation."

3. Leakage Test Report for Prerequisite EA 2: Documentation of work performed for compliance with ASHRAE/IESNA 90.1, Section 6.4.4.2.2 - "Duct Leakage Tests."

4. Duct-Cleaning Test Report for Prerequisite IEQ 1: Documentation of work performed for compliance with ASHRAE 62.1, Section 7.2.4 - "Ventilation System Start-up."

"Product Data for Credit IEQ 4.1" Subparagraph below applies to LEED-NC, LEED-CI, and LEED-CS; coordinate with requirements for adhesives and sealants.

5. Product Data for Credit IEQ 4.1: For adhesives and sealants, documentation including a printed statement of VOC content.

"Laboratory Test Reports for Credit IEQ 4" Subparagraph below applies to LEED for Schools.

6. Laboratory Test Reports for Credit IEQ 4: For adhesives and sealants, documentation indicating that products comply with the testing and product requirements of the California Department of Health Services' "Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers."

C. Shop Drawings: For HVAC casings. Include plans, elevations, sections, components, and attachments to other work.

1.4 INFORMATIONAL SUBMITTALS

A. Field quality-control reports.

1.5 QUALITY ASSURANCE

Retain two paragraphs below if applying for LEED certification or if requiring compliance with ASHRAE or ASHRAE/IESNA.

LEED Prerequisite IEQ 1 requires compliance with requirements in ASHRAE 62.1.

A. ASHRAE Compliance: Applicable requirements in ASHRAE 62.1, Section 5 - "Systems and Equipment" and Section 7 - "Construction and System Start-up."

LEED Prerequisite EA 2 requires compliance with requirements in ASHRAE/IESNA 90.1.

B. ASHRAE/IESNA Compliance: Applicable requirements in ASHRAE/IESNA 90.1, Section 6.4.4 - "HVAC System Construction and Insulation."

PART 2 -  PRODUCTS

2.1 GENERAL CASING FABRICATION REQUIREMENTS

A. General Material Requirements: Comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Chapter 9, "Equipment and Casings," for acceptable materials, material thicknesses, and casing construction methods unless otherwise indicated. Sheet metal materials shall be free of pitting, seam marks, roller marks, stains, discolorations, and other imperfections.

1. Fabricate casings with more than 3-inch wg (750-Pa) negative static pressure according to SMACNA's "Rectangular Industrial Duct Construction Standards."

2. Casings with more than 2-inch wg (500-Pa) positive static pressure may be fabricated according to SMACNA's "Rectangular Industrial Duct Construction Standards."

B. Galvanized Sheet Steel: Comply with ASTM A 653/A 653M.

1. Exterior Surface Galvanized Coating Designation: [G60 (Z180)] [G90 (Z275)].

2. Interior Surface Galvanized Coating Designation:

a. Sections Not Exposed to Moisture: [G60 (Z180)] [G90 (Z275)].

b. Sections Housing and Downstream from Cooling Coil and Humidifiers: [G90 (Z275)].

C. Reinforcement Shapes and Plates: ASTM A 36/A 36M, steel plates, shapes, and bars; black and galvanized.

Retain first paragraph below if seal class or leakage class is not indicated on Drawings.

D. Sealing Requirement: SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Seal Class A. Seal all seams, joints, connections, and abutments to building.

E. Penetrations: Seal all penetrations airtight. Cover with escutcheons and gaskets, or fill with suitable compound so there is no exposed insulation. Comply with requirements for escutcheons specified in Section 230518 "Escutcheons for HVAC Piping." Provide shaft seals where fan shafts penetrate casing.

F. Access Doors: Fabricate access doors according to SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Figure 9-15, "Casing Access Doors - 2-inch wg (500 Pa)," and Figure 9-16, "Casing Access Doors - 3-10-inch wg (750-2500 Pa)"; and according to pressure class of the plenum or casing section in which access doors are to be installed.

1. Size: [20 by 54 inches (500 by 1370 mm)] <Insert size>.

2. Vision Panel: Double-glazed, wire-reinforced safety glass with an airspace between panes and sealed with interior and exterior rubber seals.

3. Hinges: Piano or butt hinges and latches, number and size according to SMACNA's "HVAC Duct Construction Standards - Metal and Flexible."

4. Latches: Minimum of two wedge-lever-type latches, operable from inside and outside.

5. Neoprene gaskets around entire perimeters of door frames.

6. Doors shall open against air pressure.

G. Condensate Drain Pans: Formed sections of G90 (Z275) coated, galvanized sheet steel complying with requirements in ASHRAE 62.1. Pans shall extend a minimum of 12 inches (300 mm) past coil.

1. Double-wall construction shall have space between walls filled with foam insulation and sealed moisture tight.

2. Intermediate drain pan or drain trough shall collect condensate from top coil for units with stacked coils or stacked eliminators.

3. Insulation: Polystyrene or polyurethane.

4. Slopes shall be in a minimum of two planes to collect condensate from cooling coils (including coil piping connections and return bends), eliminators, and humidifiers when units are operating at maximum catalogued face velocity across cooling coil.

Retain option in subparagraph below for units with draw-through fan configurations.

5. Each drain pan connection shall have a trap.[ Drain traps with depth and height differential between inlet and outlet equal or greater to the design static pressure plus 2-inch wg (500 Pa.)] Include slab height in trap calculation.

2.2 MANUFACTURED CASINGS

First paragraph below is an example of one type of factory-fabricated casing.

A. Description: Double-wall, insulated, pressurized equipment casing.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain first paragraph and list of manufacturers below. See Section 016000 "Product Requirements."

B. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

1. Acoustical Surfaces, Inc.

2. AeroSonics, Inc.; a division of TUTCO, Inc.

3. Buffalo Air Handling.

4. CertainTeed Corp.; Insulation Group.

5. CLEANPAK International.

6. D&D Sound Control.

7. IACL.

8. Industrial Noise Control, Inc.

9. McGill AirSilence LLC.

10. SEMCO Incorporated.

11. Vibro-Acoustics.

12. <Insert manufacturer's name>.

C. Double-Wall Panel Fabrication: Solid, galvanized sheet steel exterior wall and [solid] [perforated], galvanized sheet steel interior wall; with space between wall filled with insulation.

2-inch (50-mm)-thick walls are usually standard.

1. Wall Thickness: [2 inches (50 mm)] [4 inches (100 mm)].

2. Fabricate with a minimum number of joints.

3. Weld exterior and interior walls to perimeter; to interior, longitudinal, galvanized-steel channels; and to box-end internal closures. Paint welds.

Retain one of first two subparagraphs below.

4. Sheet metal thickness shall comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible" for static-pressure class indicated for casing.

5. Sheet Metal Thicknesses:

a. Exterior Wall Thickness: [0.040 inch (1.0 mm)] <Insert dimension> minimum.

b. Interior Wall Thickness: [0.034 inch (0.85 mm)] <Insert dimension> minimum.

Retain one of first two subparagraphs below.

6. Double-Wall Casing Inner Panel: Perforated, galvanized sheet steel having 3/32-inch- (2.4-mm-) diameter perforations, with overall open area of [23] <Insert number> percent.

7. Double-Wall Casing Inner Panel: Solid sheet steel.

8. Fill each panel assembly with insulating material that is noncombustible, inert, mildew resistant, and vermin proof and that complies with NFPA 90A.

9. Fabricate panels with continuous [tongue-and-groove] [self-locking] [tongue-and-groove or self-locking] joints effective inside and outside each panel.

D. Trim Items: Fabricate from a minimum of 0.052-inch (1.3-mm) galvanized sheet steel, furnished in standard lengths for field cutting.

2.3 CASING LINER

If the objective of casing liner includes achievement of both thermal performance and sound absorption, then casings may need additional external insulation to achieve thermal portion of the objective. LEED Prerequisite EA 2 requires minimum thermal-resistance values for air distribution systems. See Section 230713 "Duct Insulation" for applicable duct insulation and installation requirements for external casing application.

When specifying liner by referencing ASTM C 1071, specifiers are assured of products meeting stated qualifications for corrosiveness, water-vapor sorption, fungi resistance, temperature resistance, erosion resistance, odor emission, surface-burning characteristics, apparent thermal conductivity, sound absorption coefficients, and bacteria resistance.

A. Fibrous-Glass Liner: Comply with ASTM C 1071, NFPA 90A, or NFPA 90B and with NAIMA AH124, "Fibrous Glass Duct Liner Standard."

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain first subparagraph and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. CertainTeed Corp.; Insulation Group.

b. Johns Manville.

c. Knauf Insulation.

d. Owens Corning.

e. <Insert manufacturer's name>.

2. Water-Based Liner Adhesive: Comply with NFPA 90A or NFPA 90B and with ASTM C 916.

One or both subparagraphs below may be required to comply with Project requirements or authorities having jurisdiction. Retain first subparagraph below if required for LEED-NC, LEED-CI, or LEED-CS Credit IEQ 4.1.

a. For indoor applications, adhesive shall have a VOC content of 80 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

Retain subparagraph below if required for LEED for Schools Credit IEQ 4.

b. Adhesive shall comply with the testing and product requirements of the California Department of Health Services' "Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers."

Flexible-elastomeric casing liner in first paragraph below is not suitable for temperatures higher than 220 deg F (104 deg C).

B. Flexible-Elastomeric Casing Liner: Preformed, cellular, closed-cell, sheet materials complying with ASTM C 534, Type II, Grade 1, and with NFPA 90A or NFPA 90B.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain first subparagraph and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Aeroflex USA Inc.

b. Armacell LLC.

c. Rubatex International, LLC.

d. <Insert manufacturer's name>.

Available thicknesses are 3/8, 1/2, 3/4, and 1 inch (9.5, 13, 19, and 25 mm). Indicate thickness on Drawings.

Surface-burning characteristics in first subparagraph below are available in limited thicknesses. Verify maximum thickness with manufacturers.

2. Surface-Burning Characteristics: Maximum flame-spread index of 25 and maximum smoke-developed index of 50 when tested according to UL 723; certified by an NRTL.

3. Liner Adhesive: As recommended by insulation manufacturer and complying with NFPA 90A or NFPA 90B.

One or both subparagraphs below may be required to comply with Project requirements or authorities having jurisdiction. Retain first subparagraph below if required for LEED-NC, LEED-CI, or LEED-CS Credit IEQ 4.1.

a. For indoor applications, adhesive shall have a VOC content of 80 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

Retain subparagraph below if required for LEED for Schools Credit IEQ 4.

b. Adhesive shall comply with the testing and product requirements of the California Department of Health Services' "Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers."

C. Natural-Fiber Casing Liner: 85 percent cotton, 10 percent borate, and 5 percent polybinding fibers, treated with a microbial growth inhibitor, and complying with NFPA 90A or NFPA 90B.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain first subparagraph and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Bonded Logic, Inc.

b. Reflectix Inc.

c. <Insert manufacturer's name>.

Available thicknesses are 1/2 and 1 inch (13 and 25 mm). Indicate thickness on Drawings.

2. Maximum Thermal Conductivity: [0.24 Btu x in./h x sq. ft. x deg F (0.034 W/m x K)] <Insert conductivity> at 75 deg F (24 deg C) mean temperature when tested according to ASTM C 518.

3. Surface-Burning Characteristics: Maximum flame-spread index of 25 and maximum smoke-developed index of 50 when tested according to UL 723; certified by an NRTL.

4. Liner Adhesive: As recommended by insulation manufacturer and complying with NFPA 90A or NFPA 90B.

One or both subparagraphs below may be required to comply with Project requirements or authorities having jurisdiction. Retain first subparagraph below if required for LEED-NC, LEED-CI, or LEED-CS Credit IEQ 4.1.

a. For indoor applications, adhesive shall have a VOC content of 80 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

Retain subparagraph below if required for LEED for Schools Credit IEQ 4.

b. Adhesive shall comply with the testing and product requirements of the California Department of Health Services' "Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers."

D. Insulation Pins and Washers:

1. Cupped-Head, Capacitor-Discharge-Weld Pins: Copper- or zinc-coated steel pin, fully annealed for capacitor-discharge welding, [0.106-inch- (2.6-mm-)] [0.135-inch- (3.5-mm-)] diameter shank, length to suit depth of insulation indicated with integral 1-1/2-inch (38-mm) galvanized carbon-steel washer.

2. Insulation-Retaining Washers: Self-locking washers formed from 0.016-inch- (0.41-mm-) thick, galvanized steel, with beveled edge sized as required to hold insulation securely in place but not less than 1-1/2 inches (38 mm) in diameter.

E. Shop or Factory Application of Casing Liner: Comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Figure 7-11, "Flexible Duct Liner Installation."

1. Adhere a single layer of indicated thickness of casing liner with at least 90 percent adhesive coverage at liner contact surface area. Attaining indicated thickness with multiple layers of casing liner is prohibited.

2. Apply adhesive to transverse edges of liner facing upstream that do not receive metal nosing.

3. Butt transverse joints without gaps, and coat joint with adhesive.

4. Fold and compress liner in corners of casings or cut and fit to ensure butted-edge overlapping.

Retain first subparagraph below if air velocities are 2500 fpm (12.7 m/s) or higher.

5. Apply adhesive coating on longitudinal seams in casings with air velocity of 2500 fpm (12.7 m/s).

Securing method in first subparagraph below is for casings with air velocities of 2500 fpm (12.7 m/s) and lower. Use caution when designing lined casings with air velocities higher than 2500 fpm (12.7 m/s). See SMACNA for requirements.

6. Secure liner with mechanical fasteners 4 inches (100 mm) from corners and at intervals not exceeding 12 inches (300 mm) transversely; at 3 inches (75 mm) from transverse joints and at intervals not exceeding 18 inches (450 mm) longitudinally.

7. Secure transversely oriented liner edges facing the airstream with metal nosings that have either channel or "Z" profiles or are integrally formed from casing wall. Fabricate edge facings at the following locations:

a. Fan discharges.

b. Intervals of lined casing preceding unlined duct.

c. Upstream edges of transverse joints in casings where air velocities are higher than 2500 fpm (12.7 m/s) or where indicated.

Retain subparagraph below if casings with air velocities higher than 4000 fpm (20.3 m/s) are anticipated; indicate locations of double-wall casings on Drawings.

8. Secure insulation between perforated sheet metal inner wall of same thickness as specified for outer wall. Use mechanical fasteners that maintain inner wall at uniform distance from outer wall without compressing insulation.

2.4 SEALANT MATERIALS

See SMACNA's "HVAC Duct Construction Standards - Metal and Flexible" for a discussion on seam and joint sealing methods and their applications. Retain one or more of first three paragraphs below, and identify which sealing system applies to which HVAC casings on Drawings.

A. General Sealant and Gasket Requirements: Surface-burning characteristics for sealants and gaskets shall be a maximum flame-spread index of 25 and a maximum smoke-developed index of 50 when tested according to UL 723; certified by an NRTL.

B. Water-Based Joint and Seam Sealant:

1. Application Method: Brush on.

2. Solids Content: Minimum 65 percent.

3. Shore A Hardness: Minimum 20.

4. Water resistant.

5. Mold and mildew resistant.

One or more of three subparagraphs below may be required to comply with Project requirements or authorities having jurisdiction. Retain one of first two subparagraphs below. Retain second subparagraph if required for LEED-NC, LEED-CI, or LEED-CS Credit IEQ 4.1.

6. VOC: Maximum 75 g/L (less water).

7. For indoor applications, sealant shall have a VOC content of 250 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

Retain first subparagraph below if required for LEED for Schools Credit IEQ 4.

8. Sealant shall comply with the testing and product requirements of the California Department of Health Services' "Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers."

9. Maximum Static-Pressure Class: 10-inch wg (2500 Pa), positive or negative.

10. Service: Indoor or outdoor.

11. Substrate: Compatible with galvanized sheet steel.

C. Flanged Joint Sealant: Comply with ASTM C 920.

1. General: Single component, acid curing, silicone, elastomeric.

2. Type: S.

3. Grade: NS.

4. Class: 25.

5. Use: O.

One or both subparagraphs below may be required to comply with Project requirements or authorities having jurisdiction. Retain first subparagraph below if required for LEED-NC, LEED-CI, or LEED-CS Credit IEQ 4.1.

6. For indoor applications, sealant shall have a VOC content of 250 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

Retain subparagraph below if required for LEED for Schools Credit IEQ 4.

7. Sealant shall comply with the testing and product requirements of the California Department of Health Services' "Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers."

D. Flange Gaskets: Butyl rubber, neoprene, or EPDM polymer with polyisobutylene plasticizer.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Install casings according to SMACNA's "HVAC Duct Construction Standards - Metal and Flexible."

B. Equipment Mounting:

Retain first subparagraph below to require equipment to be installed on cast-in-place concrete equipment bases.

1. Install HVAC casings on cast-in-place concrete equipment base(s). Comply with requirements for equipment bases and foundations specified in [Section 033000 "Cast-in-Place Concrete."] [Section 033053 "Miscellaneous Cast-in-Place Concrete."]

Retain one of two subparagraphs below. Retain first for projects in seismic areas; retain second for projects not in seismic areas. Indicate vibration isolation and seismic-control device type and minimum deflection in supported equipment schedule on Drawings.

2. Comply with requirements for vibration isolation and seismic control devices specified in Section 230548 "Vibration and Seismic Controls for HVAC."

3. Comply with requirements for vibration isolation devices specified in Section 230548.13 "Vibration Controls for HVAC."

C. Apply sealant to joints, connections, and mountings.

D. Field-cut openings for pipe and conduit penetrations; insulate and seal according to SMACNA's "HVAC Duct Construction Standards - Metal and Flexible."

E. Support casings on floor or foundation system. Secure and seal to base.

F. Support components rigidly with ties, braces, brackets, [seismic restraints, ]and anchors of types that will maintain housing shape and prevent buckling.

G. Align casings accurately at connections, with 1/8-inch (3-mm) misalignment tolerance and with smooth interior surfaces.

3.2 FIELD QUALITY CONTROL

A. Tests and Inspections:

1. Perform field tests and inspections according to SMACNA's "HVAC Air Duct Leakage Test Manual."

2. Test the following systems:

LEED Prerequisite EA 2 requires compliance with ASHRAE/IESNA 90.1, in which Section 6.4.4.2.2 - "Duct Leakage Tests" requires leak testing of at least 25 percent of total installed duct area with a pressure class in excess of 3-inch wg (750 Pa). If applying for LEED certification or complying with ASHRAE/IESNA 90.1, retain first subparagraph below to define minimum requirements. Retain second subparagraph to define more stringent requirements.

a. Systems required by ASHRAE/IESNA 90.1.

b. Supply Air: [100] [50] <Insert value> percent of total installed duct area with a pressure class of [3-inch wg (750 Pa)] [4-inch wg (1000 Pa)] <Insert value> or higher.

c. <Insert requirements of other systems>.

3. Conduct tests at static pressures equal to maximum design pressure of system or section being tested. If pressure classes are not indicated, test entire system at maximum system design pressure. Do not pressurize systems above maximum design operating pressure. Give seven days' advance notice for testing.

4. Determine leakage from entire system or section of system by relating leakage to surface area of test section. Comply with requirements for leakage classification of ducts connected to casings.

5. Disassemble, reassemble, and seal segments of systems to accommodate leakage testing and for compliance with test requirements.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

B. HVAC casings will be considered defective if they do not pass tests and inspections.

C. Prepare test and inspection reports.

3.3 CLEANING

Retain this article to require cleaning of new HVAC casings to remove construction dust or existing HVAC casings indicated to remain to comply with ASHRAE 62.1, in which Section 7.2.4 - "Ventilation System Start-up" requires that distribution systems be clean of dirt and debris. Retain also for LEED Prerequisite IEQ 1.

A. Comply with requirements for cleaning in Section 233113 "Metal Ducts."

END OF SECTION 233119

	HVAC CASINGS
	233119 - 1



