Copyright 2011 AIA
MasterSpec Professional
09/11

Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 233413 - AXIAL HVAC FANS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Tubeaxial fans.

2. Vaneaxial fans.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product.

1. Include rated capacities, furnished specialties, and accessories for each fan.

2. Certified fan performance curves with system operating conditions indicated.

3. Certified fan sound-power ratings.

4. Motor ratings and electrical characteristics, plus motor and electrical accessories.

5. Material thickness and finishes, including color charts.

6. Dampers, including housings, linkages, and operators.

7. Fan speed controllers.

B. Shop Drawings:

1. Include plans, elevations, sections, and attachment details.

2. Include details of equipment assemblies. Indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

3. Include diagrams for power, signal, and control wiring.

4. Design Calculations: Calculate requirements for selecting vibration isolators and seismic restraints and for designing vibration isolation bases.

5. Vibration Isolation Base Details: Detail fabrication, including anchorages and attachments to structure and to supported equipment. Include auxiliary motor slides and rails, and base weights.

1.3 INFORMATIONAL SUBMITTALS

Retain "Coordination Drawings" Paragraph below for situations where limited space necessitates maximum utilization for efficient installation of different components or if coordination is required for installation of products and materials by separate installers. Coordinate paragraph with other Sections specifying products listed below. Preparation of coordination drawings requires the participation of each trade involved in installations within the limited space.

A. Coordination Drawings: Show fan room layout and relationships between components and adjacent structural and mechanical elements. Show support locations, type of support, and weight on each support. Indicate and certify field measurements.

Retain "Field quality-control reports" Paragraph below if Contractor is responsible for field quality-control testing and inspecting.

B. Field quality-control reports.

1.4 CLOSEOUT SUBMITTALS

A. Operation and Maintenance Data: For axial fans to include in emergency, operation, and maintenance manuals.

1.5 MAINTENANCE MATERIAL SUBMITTALS

A. Belts: [One] <Insert number> set(s) for each belt-driven unit.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

2.1 PERFORMANCE REQUIREMENTS

AMCA compliance is an optional requirement and not necessarily available from all manufacturers.

A. AMCA Compliance: Comply with AMCA performance requirements and bear the AMCA-Certified Ratings Seal.

If Project has more than one type or configuration of tubeaxial fan, delete "Capacities and Characteristics" Paragraph below and schedule fans on Drawings.

B. Capacities and Characteristics:

1. Airflow: <Insert cfm (L/s)>.

2. External Static Pressure: <Insert inches wg (Pa)>.

3. Fan Diameter: <Insert inches (mm)>.

4. Brake Horsepower: <Insert value>.

5. Drive Type: [Direct] [Belt].

6. Fan Rpm: <Insert value>.

7. Motor:

Retain "Electrical Characteristics" Subparagraph below if characteristics are not indicated on Drawings.

a. Electrical Characteristics:

1) Motor Size: <Insert horsepower>.

2) Motor Rpm: <Insert value>.

3) Volts: [120] [208] [230] [460] <Insert value>.

4) Phase: [Single] [Poly].

5) Hertz: 60.

6) Full-Load Amperes: <Insert value>.

7) Minimum Circuit Ampacity: <Insert value>.

8) Maximum Overcurrent Protection: <Insert amperage>.

8. Sound Power:

a. 1st Octave: <Insert dB>.

b. 2nd Octave: <Insert dB>.

c. 3rd Octave: <Insert dB>.

d. 4th Octave: <Insert dB>.

e. 5th Octave: <Insert dB>.

f. 6th Octave: <Insert dB>.

g. 7th Octave: <Insert dB>.

h. 8th Octave: <Insert dB>.

9. Vibration Isolators: [Spring] [Restrained spring] <Insert type> isolators having a static deflection of [1 inch (25 mm)] <Insert deflection>.

2.2 TUBEAXIAL FANS

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Review list below if AMCA-certified fans are required; not all manufacturers are AMCA members.

1. Acme Engineering & Mfg. Corp.

2. Aerovent; a Twin City Fan company.

3. Airmaster Fan Company.

4. American Coolair Corporation.

5. American Fan Company; part of Flakt Woods Americas.

6. Breidert Air Products.

7. Carnes Company.

8. Chicago Blower Corporation.

9. Cincinnati Fan.

10. CML Northern Blower Inc.

11. Greenheck Fan Corporation.

12. Hartzell Fan Incorporated.

13. Howden Buffalo Inc.

14. Howden Buffalo Inc.; New Philadelphia Division.

15. Lau Industries.

16. Loren Cook Company.

17. Madison Manufacturing.

18. New York Blower Company (The).

19. PennBarry.

20. Strobic Air Corporation.

21. Trane Inc.; a subsidiary of Ingersoll-Rand company.

22. <Insert manufacturer's name>.

C. Description: Fan wheel and housing, factory-mounted motor with [belt] [or] [direct] drive, an inlet cone section, and accessories.

D. Housings: [Steel] [Galvanized steel] [Aluminum] with flanged inlet and outlet connections.

Retain one of two "Wheel Assemblies" paragraphs below.

E. Wheel Assemblies: Cast or extruded aluminum with airfoil-shaped blades mounted on cast-iron wheel plate keyed to shaft with solid-steel key.

F. Wheel Assemblies: Cast aluminum, machined and fitted to shaft.

Retain "Belt Drives" Paragraph below for belt-driven fans.

G. Belt Drives:

1. Factory mounted, with adjustable alignment and belt tensioning.

2. Service Factor Based on Fan Motor Size: 1.2.

3. Fan Shaft: Turned, ground, and polished steel designed to operate at no more than 70 percent of first critical speed at top of fan's speed range.

4. Fan Pulleys: Cast iron with split, tapered bushing; dynamically balanced at factory.

5. Motor Pulleys: Adjustable pitch for use with motors through 5 hp; fixed pitch for use with larger motors. Select pulley so pitch adjustment is at the middle of adjustment range at fan design conditions.

6. Belts: Oil resistant, nonsparking, and nonstatic; matched sets for multiple belt drives.

Belt guards are standard.

7. Belt Guards: Fabricate of steel for motors mounted on outside of fan cabinet.

8. Motor Mount: Adjustable base.

9. Shaft Bearings: Radial, self-aligning bearings.

H. Accessories:

Retain applicable accessories below. Verify availability with manufacturers.

1. Companion Flanges: Rolled flanges of same material as housing.

2. Inspection Door: Bolted door allowing limited access to internal parts of fan, of same material as housing.

3. Propeller Access Section Door: Short duct section bolted to fan [inlet] [and] [outlet] allowing access to internal parts of fan for inspection and cleaning, of same material as housing.

4. Swingout Construction: Assembly allowing entire fan section to swing out from duct for cleaning and servicing, of same material as housing.

5. Mounting Clips: [Horizontal ceiling] [Vertical mounting] clips welded to fan housing, of same material as housing.

6. Horizontal Support: Pair of supports bolted to fan housing, of same material as housing.

7. Vertical Support: Short duct section with welded brackets bolted to fan housing, of same material as housing.

8. Inlet Screen: Wire-mesh screen on fans not connected to ductwork, of same material as housing.

9. Outlet Screen: Wire-mesh screen on fans not connected to ductwork, of same material as housing.

10. Backdraft Dampers: Butterfly style, for bolting to the discharge of fan or outlet cone, of same material as housing.

11. Shaft Seal: Elastomeric seal and Teflon wear plate, suitable for up to 300 deg F (149 deg C).

12. Motor Cover: Cover with side vents to dissipate motor heat, of same material as housing.

13. Inlet Vanes: Adjustable; with peripheral control linkage operated from outside of airstream, bronze sleeve bearings on each end of vane support, and provision for manual or automatic operation of same material as housing.

14. Inlet Bell: Curved inlet for when fan is not attached to duct, [of same material as housing] [aluminum].

15. Inlet Cone: Round-to-round transition of same material as housing.

16. Outlet Cone: Round-to-round transition, of same material as housing.

17. Stack Cap: Vertical discharge assembly with backdraft dampers, of same material as housing.

18. Direct-Driven Units: Encase motor in housing outside of airstream[, factory wired to disconnect switch located on outside of fan housing]. Extend lubrication lines to outside of casing and terminate with grease fittings.

I. Factory Finishes:

1. Sheet Metal Parts: Prime coat before final assembly.

2. Exterior Surfaces: Baked-enamel finish coat after assembly.

Retain "Coatings" Subparagraph for special protection applications. Review manufacturer's data for specific trade names and literature.

3. Coatings: [Thermoplastic vinyl] [Epoxy] [Zinc] [Synthetic resin] [Phenolic] [Color-match enamel] [Polytetrafluoroethylene] [Vinyl ester] [Hot-dip galvanized] [Powder-baked enamel]; <Insert manufacturer's name and trade name>.

a. Apply to finished housings.

b. Apply to fan wheels.

2.3 VANEAXIAL FANS

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

Review list below if AMCA-certified fans are required; not all manufacturers are AMCA members.

1. Acme Engineering & Mfg. Corp.

2. Aerovent; a Twin City Fan company.

3. Airmaster Fan Company.

4. American Coolair Corporation.

5. American Fan Company; part of Flakt Woods Americas.

6. Breidert Air Products.

7. Carnes Company.

8. Chicago Blower Corporation.

9. Cincinnati Fan.

10. CML Northern Blower Inc.

11. Greenheck Fan Corporation.

12. Hartzell Fan Incorporated.

13. Howden Buffalo Inc.

14. Howden Buffalo Inc.; New Philadelphia Division.

15. Lau Industries.

16. Loren Cook Company.

17. Madison Manufacturing.

18. New York Blower Company (The).

19. PennBarry.

20. Strobic Air Corporation.

21. Trane Inc.; a subsidiary of Ingersoll-Rand company.

22. <Insert manufacturer's name>.

C. Description: Fan wheel and housing, straightening vane section, factory-mounted motor with belt drive or direct drive, an inlet cone section, and accessories.

1. Variable-Pitch Fans: Internally mounted [pneumatic] [electric] [electronic] actuator, externally-mounted positive positioner, and mechanical-blade-pitch indicator.

D. Housings: [Steel] [Galvanized steel] [Aluminum].

1. Inlet and Outlet Connections: Flanges.

2. Guide Vane Section: Integral guide vanes downstream from fan wheel designed to straighten airflow.

Retain one of two "Wheel Assemblies" paragraphs below.

E. Wheel Assemblies: Cast aluminum with airfoil-shaped blades mounted on cast-iron wheel plate keyed to shaft with solid-steel key.

F. Wheel Assemblies: Cast-aluminum hub assembly, machined and fitted with threaded bearing wells to receive blade-bearing assemblies with replaceable, cast-aluminum blades; factory mounted and balanced.

Retain "Belt Drives" Paragraph below for belt-driven fans.

G. Belt Drives: Factory mounted, with final alignment and belt adjustment made after installation.

1. Service Factor Based on Fan Motor Size: 1.2.

2. Fan Shaft: Turned, ground, and polished steel designed to operate at no more than 70 percent of first critical speed at top of fan's speed range.

3. Fan Pulleys: Cast iron with split, tapered bushing; dynamically balanced at factory.

4. Motor Pulleys: Adjustable pitch for use with motors through 5 hp; fixed pitch for use with larger motors. Select pulley so pitch adjustment is at the middle of adjustment range at fan design conditions.

5. Belts: Oil resistant, nonsparking, and nonstatic; matched sets for multiple belt drives.

6. Belt Guards: Fabricate of steel for motors mounted on outside of fan cabinet.

7. Motor Mount: Adjustable base.

8. Shaft Bearings: Radial, self-aligning bearings.

H. Accessories:

Retain applicable accessories below. Verify availability with manufacturers.

1. Companion Flanges: Rolled flanges of same material as housing.

2. Inspection Door: Bolted door allowing limited access to internal parts of fan, of same material as housing.

3. Propeller Access Section Door: Short duct section bolted to fan [inlet] [and] [outlet] allowing access to internal parts of fan for inspection and cleaning, of same material as housing.

4. Swingout Construction: Assembly allowing entire fan section to swing out from duct for cleaning and servicing, of same material as housing.

5. Mounting Clips: [Horizontal ceiling] [Vertical mounting] clips welded to fan housing, of same material as housing.

6. Horizontal Support: Pair of supports bolted to fan housing, of same material as housing.

7. Vertical Support: Short duct section with welded brackets bolted to fan housing, of same material as housing.

8. Inlet Screen: Wire-mesh screen on fans not connected to ductwork, of same material as housing.

9. Outlet Screen: Wire-mesh screen on fans not connected to ductwork, of same material as housing.

10. Backdraft Dampers: Butterfly style, for mounting with flexible connection to the discharge of fan or direct mounted to the discharge diffuser section, of same material as housing.

"Stall Alarm Probe" Subparagraph below may be used to activate an alarm, to activate controls, to adjust blade pitch, or to shut down fan.

11. Stall Alarm Probe: Sensing probe capable of detecting fan operation in stall and signaling control devices.

12. Flow Measurement Port: Pressure measurement taps installed in the inlet of fan to detect and signal airflow readings to temperature-control systems.

13. Shaft Seal: Elastomeric seal and Teflon wear plate, suitable for up to 300 deg F (148 deg C).

14. Motor Cover: Cover with side vents to dissipate motor heat, of same material as housing.

15. Inlet Vanes: Adjustable; with peripheral control linkage operated from outside of airstream, bronze sleeve bearings on each end of vane support, and provision for manual or automatic operation, of same material as housing.

16. Inlet Bell: Curved inlet for when fan is not attached to duct, of same material as housing.

17. Inlet Cone: Round-to-round transition, of same material as housing.

18. Outlet Cone: Round-to-round transition, of same material as housing.

19. Stack Cap: Vertical discharge assembly with backdraft dampers, of same material as housing.

20. Direct-Driven Units: Encase motor in housing outside of airstream[, factory wired to disconnect switch located on outside of fan housing]. Extend lubrication lines to outside of casing and terminate with grease fittings.

I. Factory Finishes:

1. Sheet Metal Parts: Prime coat before final assembly.

2. Exterior Surfaces: Baked-enamel finish coat after assembly.

Retain "Coatings" Subparagraph for special protection applications. Review manufacturer's data for specific trade names and literature.

3. Coatings: [Thermoplastic vinyl] [Epoxy] [Zinc] [Synthetic resin] [Phenolic] [Color-match enamel] [Polytetrafluoroethylene] [Vinyl ester] [Hot-dip galvanized] [Powder-baked enamel]; <Insert manufacturer's name and trade name>.

a. Apply to finished housings.

b. Apply to fan wheels.

2.4 SOURCE QUALITY CONTROL

Sound-power rating information may only be available from manufacturers on request. See discussion on sound and vibration control in the Evaluations.

A. Sound-Power Level Ratings: Comply with AMCA 301, "Methods for Calculating Fan Sound Ratings from Laboratory Test Data." Factory test fans according to AMCA 300, "Reverberant Room Method for Sound Testing of Fans." Label fans with the AMCA-Certified Ratings Seal.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Install axial fans level and plumb.

B. Disassemble and reassemble units, as required for moving to the final location, according to manufacturer's written instructions.

C. Lift and support units with manufacturer's designated lifting or supporting points.

D. Equipment Mounting:

Retain first subparagraph below to require equipment to be installed on cast-in-place concrete equipment bases.

1. Install fans on cast-in-place concrete equipment base(s). Comply with requirements for equipment bases and foundations specified in [Section 033000 "Cast-in-Place Concrete."] [Section 033053 "Miscellaneous Cast-in-Place Concrete."]

Retain one of two subparagraphs below. Retain first for projects in seismic areas; retain second for projects not in seismic areas. Indicate vibration isolation and seismic-control device type and minimum deflection in supported equipment schedule on Drawings.

2. Comply with requirements for vibration isolation and seismic control devices specified in Section 230548 "Vibration and Seismic Controls for HVAC."

3. Comply with requirements for vibration isolation devices specified in Section 230548.13 "Vibration Controls for HVAC."

E. Install units with clearances for service and maintenance.

F. Label fans according to requirements specified in Section 230553 "Identification for HVAC Piping and Equipment."

3.2 CONNECTIONS

Coordinate duct installations and specialty arrangements with schematics on Drawings and with requirements specified in duct systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Drawings indicate general arrangement of ducts and duct accessories. Make final duct connections with flexible connectors. Flexible connectors are specified in Section 233300 "Air Duct Accessories."

B. Ground equipment according to Section 260526 "Grounding and Bonding for Electrical Systems."

C. Connect wiring according to Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

3.3 FIELD QUALITY CONTROL

A. Perform the following tests and inspections[ with the assistance of a factory-authorized service representative]:

1. Verify that shipping, blocking, and bracing are removed.

2. Verify that unit is secure on mountings and supporting devices and that connections to ducts and electrical components are complete. Verify that proper thermal-overload protection is installed in motors, starters, and disconnect switches.

3. Verify that cleaning and adjusting are complete.

4. Disconnect fan drive from motor, verify proper motor rotation direction, and verify fan wheel free rotation and smooth bearing operation. Reconnect fan drive system, align and adjust belts, and install belt guards.

5. Adjust belt tension.

6. Adjust damper linkages for proper damper operation.

7. Verify lubrication for bearings and other moving parts.

8. Verify that manual and automatic volume control and fire and smoke dampers in connected ductwork systems are in fully open position.

9. Disable automatic temperature-control operators, energize motor and confirm proper motor rotation and unit operation, adjust fan to indicated rpm, and measure and record motor voltage and amperage.

10. Shut unit down and reconnect automatic temperature-control operators.

11. Remove and replace malfunctioning units and retest as specified above.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

B. Test and adjust controls and safeties. Controls and equipment will be considered defective if they do not pass tests and inspections.

C. Prepare test and inspection reports.

END OF SECTION 233413

	AXIAL HVAC FANS
	233413 - 1



