Copyright 2011 AIA
MasterSpec Professional
09/11

Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 233600 - AIR TERMINAL UNITS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Fan-powered air terminal units.

2. Shutoff, single-duct air terminal units.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product indicated.

B. LEED Submittals:

1. Product Data for Prerequisite EQ 1: Documentation indicating that units comply with ASHRAE 62.1, Section 5 - "Systems and Equipment."

C. Shop Drawings: For air terminal units. Include plans, elevations, sections, details, and attachments to other work.

Paragraph below is defined in Section 013300 "Submittal Procedures" as a "Delegated-Design Submittal." Retain with "Performance Requirements" Article if design responsibilities have been delegated to Contractor.

D. Delegated-Design Submittal:

1. Materials, fabrication, assembly, and spacing of hangers and supports.

Retain subparagraph below if Work of this Section is required to withstand specific design loads and design responsibilities have been delegated to Contractor as another way to verify compliance with performance requirements. Professional engineer qualifications are specified in Section 014000 "Quality Requirements."

2. Design Calculations: Calculations[, including analysis data signed and sealed by the qualified professional engineer responsible for their preparation] for selecting hangers and supports[ and seismic restraints].

1.3 INFORMATIONAL SUBMITTALS

A. Field quality-control reports.

1.4 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

1.5 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

B. ASHRAE Compliance: Applicable requirements in ASHRAE 62.1, Section 5 - "Systems and Equipment" and Section 7 - "Construction and System Start-Up."

PART 2 -  PRODUCTS

2.1 PERFORMANCE REQUIREMENTS

Retain seismic options and design criteria in paragraph below that are approved by authorities having jurisdiction.

A. Structural Performance: Hangers and supports[ and seismic restraints] shall withstand the effects of gravity[ and seismic] loads and stresses within limits and under conditions described in SMACNA's "HVAC Duct Construction Standards - Metal and Flexible" [and] [ASCE/SEI 7] [SMACNA's "Seismic Restraint Manual: Guidelines for Mechanical Systems"] <Insert document>.

2.2 PARALLEL FAN-POWERED AIR TERMINAL UNITS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."

A. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Anemostat Products; a Mestek Company.

2. Carnes.

3. Environmental Technologies, Inc.

4. Krueger.

5. METALAIRE, Inc.

6. Nailor Industries Inc.

7. Price Industries.

8. Titus.

9. Trane; a business of American Standard Companies.

10. Tuttle & Bailey.

11. <Insert manufacturer's name>.

C. Configuration: Volume-damper assembly and fan in parallel arrangement inside unit casing with control components inside a protective metal shroud.

D. Casing: [0.034-inch (0.85-mm) steel] [0.032-inch (0.8-mm) aluminum], [single] [double] wall.

Retain one of two "Casing Lining" subparagraphs below. Retain first subparagraph for standard linings; retain second for non-fiber liners.

1. Casing Lining: Adhesive attached, [1/2-inch- (13-mm-)] [3/4-inch- (19-mm-)] [1-inch- (25-mm-)] thick, coated, fibrous-glass duct liner complying with ASTM C 1071, and having a maximum flame-spread index of 25 and a maximum smoke-developed index of 50, for both insulation and adhesive, when tested according to ASTM E 84.

Retain one of first two subparagraphs below. Retain second subparagraph for double-wall casings.

a. Cover liner with nonporous foil.

b. Cover liner with nonporous foil and perforated metal.

2. Casing Lining: Adhesive attached, [1/2-inch- (13-mm-)] [3/4-inch- (19-mm-)] [1-inch- (25-mm-)] thick, polyurethane foam insulation complying with UL 181 erosion requirements, and having a maximum flame-spread index of 25 and a maximum smoke-developed index of 50, for both insulation and adhesive, when tested according to ASTM E 84.

3. Air Inlets: Round stub connections or S-slip and drive connections for duct attachment.

4. Air Outlet: S-slip and drive connections.

5. Access: Removable panels for access to parts requiring service, adjustment, or maintenance; with airtight gasket and quarter-turn latches.

6. Fan: Forward-curved centrifugal, located at plenum air inlet.

Retain subparagraph below to comply with LEED Prerequisite EQ 1.

7. Airstream Surfaces: Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1.

E. Volume Damper: Galvanized steel with flow-sensing ring and peripheral gasket and self-lubricating bearings.

Leakage rates in first subparagraph below vary among manufacturers and with pressure rating.

1. Maximum Damper Leakage: ARI 880 rated, [2] [3] percent of nominal airflow at [3-inch wg (750-Pa)] [6-inch wg (1500-Pa)] inlet static pressure.

2. Damper Position: Normally [open] [closed].

F. Velocity Sensors: Multipoint array with velocity sensors in cold- and hot-deck air inlets and air outlets.

Default motor characteristics are specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

G. Motor:

1. Comply with NEMA designation, temperature rating, service factor, enclosure type, and efficiency requirements for motors specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

2. Type: [Permanent-split capacitor with SCR for speed adjustment] [Electronically commutated motor].

3. Fan-Motor Assembly Isolation: Rubber isolators.

Verify availability of enclosure types with manufacturer of specified equipment. Delete "Enclosure" Subparagraph below if information is included in schedule on Drawings.

4. Enclosure: [Open dripproof] [Totally enclosed, fan cooled] [Totally enclosed, air over] [Open, externally ventilated] [Totally enclosed, nonventilated] [Severe duty] [Explosion proof] [Dust-ignition-proof machine].

5. Enclosure Materials: [Cast iron] [Cast aluminum] [Rolled steel].

6. Motor Bearings: <Insert special requirements>.

7. Unusual Service Conditions:

a. Ambient Temperature: <Insert deg F (deg C)>.

b. Altitude: <Insert feet (m)> above sea level.

Retain first subparagraph below if application requires this rating.

c. High humidity.

d. <Insert conditions>.

8. Efficiency: Premium efficient.

9. NEMA Design: <Insert designation>.

10. Service Factor: <Insert value>.

11. Motor Speed: [Single speed] [Multispeed].

a. Speed Control: Infinitely adjustable with electronic controls.

Retain subparagraph below if characteristics are not included on Drawings.

12. Electrical Characteristics:

a. Horsepower: <Insert value>.

b. Volts: [120] [208] [230] [460] <Insert value>.

c. Phase: [Single] [Poly].

d. Hz: 60.

e. Full-Load Amperes: <Insert value>.

f. Minimum Circuit Ampacity: <Insert value>.

g. Maximum Overcurrent Protection: <Insert amperage>.

Verify available filter types with manufacturer. Indicate filter thickness in an Air Terminal Unit Schedule on Drawings.

H. Filters: Minimum arrestance according to ASHRAE 52.1 and a minimum efficiency reporting value (MERV) according to ASHRAE 52.2.

Retain one or more of first three subparagraphs below. Indicate filter type in an Air Terminal Unit Schedule on Drawings if all units are not filtered identically. 2-inch- (50-mm-) thick foam is not available. LEED Prerequisite EQ 1 requires compliance with ASHRAE 62.1, which requires a MERV rating of 6 or higher.

1. Material: Polyurethane foam having 70 percent arrestance and 3 MERV.

2. Material: Glass fiber treated with adhesive; having 80 percent arrestance and 5 MERV.

3. Material: Pleated cotton-polyester media having 90 percent arrestance and 7 MERV.

4. Thickness: [2 inches (50 mm)] [1 inch (25 mm)].

I. Attenuator Section: [0.034-inch (0.85-mm) steel] [0.032-inch (0.8-mm) aluminum] sheet.

Retain one of two "Lining" subparagraphs below. Retain first subparagraph for standard linings; retain second for non-fiber liners.

1. Lining: Adhesive attached, [1/2-inch- (13-mm-)] [3/4-inch- (19-mm-)] [1-inch- (25-mm-)] thick, coated, fibrous-glass duct liner complying with ASTM C 1071, and having a maximum flame-spread index of 25 and a maximum smoke-developed index of 50, for both insulation and adhesive, when tested according to ASTM E 84.

Retain one of first two subparagraphs below. Retain second subparagraph for double-wall casings.

a. Cover liner with nonporous foil.

b. Cover liner with nonporous foil and perforated metal.

2. Lining: Adhesive attached, 3/4-inch- (19-mm-) thick, polyurethane foam insulation complying with UL 181 erosion requirements, and having a maximum flame-spread index of 25 and a maximum smoke-developed index of 50, for both insulation and adhesive, when tested according to ASTM E 84.

Retain subparagraph below to comply with LEED Prerequisite EQ 1.

3. Airstream Surfaces: Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1.

Retain one of first two paragraphs below if heating coil is required.

J. Hydronic Coils: Copper tube, with mechanically bonded aluminum fins spaced no closer than 0.1 inch (2.5 mm), and rated for a minimum working pressure of 200 psig (1380 kPa) and a maximum entering-water temperature of 220 deg F (104 deg C). Include manual air vent and drain valve.

1. Location: Plenum air inlet.

K. Electric-Resistance Heating Coils: Nickel-chromium heating wire, free of expansion noise and hum, mounted in ceramic inserts in a galvanized-steel housing; with primary automatic, and secondary manual, reset thermal cutouts. Terminate elements in stainless-steel, machine-staked terminals secured with stainless-steel hardware.

1. Location: Plenum air inlet.

2. Stage(s): [1] [2] [3].

3. Access door interlocked disconnect switch.

4. Downstream air temperature sensor with local connection to override discharge-air temperature to not exceed a maximum temperature set point (adjustable.)

Retain applicable subparagraphs below.

5. Nickel chrome 80/20 heating elements.

6. Airflow switch for proof of airflow.

7. Fan interlock contacts.

8. Fuses in terminal box for overcurrent protection (for coils more than 48 A).

9. Mercury contactors.

10. Magnetic contactor for each step of control (for three-phase coils).

L. Factory-Mounted and -Wired Controls: Electrical components mounted in control box with removable cover. Incorporate single-point electrical connection to power source.

1. Control Transformer: Factory mounted for control voltage on electric and electronic control units with terminal strip in control box for field wiring of thermostat and power source.

2. Wiring Terminations: Fan and controls to terminal strip. Terminal lugs to match quantities, sizes, and materials of branch-circuit conductors. Enclose terminal lugs in terminal box that is sized according to NFPA 70.

3. Disconnect Switch: Factory-mounted, fuse type.

M. Control Panel Enclosure: NEMA 250, Type 1, with access panel sealed from airflow and mounted on side of unit.

Retain one of two paragraphs below or delete both if controls are specified in Section 230900 "Instrumentation and Control for HVAC."

N. Electric Controls: 24-V damper actuator with wall-mounted electric thermostat and appropriate mounting hardware.

O. Electronic Controls: Bidirectional damper operator and microprocessor-based controller with integral airflow transducer and room sensor. Control devices shall be compatible with temperature controls specified in Section 230900 "Instrumentation and Control for HVAC" and shall have the following features:

Retain applicable subparagraphs below.

1. Occupied and unoccupied operating mode.

2. Remote reset of airflow or temperature set points.

3. Adjusting and monitoring with portable terminal.

4. Communication with temperature-control system specified in Section 230900 "Instrumentation and Control for HVAC."

2.3 SERIES FAN-POWERED AIR TERMINAL UNITS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."

A. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Anemostat Products; a Mestek Company.

2. Carnes.

3. Environmental Technologies, Inc.

4. Krueger.

5. METALAIRE, Inc.

6. Nailor Industries Inc.

7. Price Industries.

8. Titus.

9. Trane; a business of American Standard Companies.

10. Tuttle & Bailey.

11. <Insert manufacturer's name>.

C. Configuration: Volume-damper assembly and fan in series arrangement inside unit casing with control components inside a protective metal shroud [for installation above a ceiling] [and] [within a raised access floor].

D. Casing: [0.034-inch (0.85-mm) steel] [0.032-inch (0.8-mm) aluminum], [single] [double] wall.

Retain one of two "Casing Lining" subparagraphs below. Retain first subparagraph for standard linings; retain second for non-fiber liners.

1. Casing Lining: Adhesive attached, [1/2-inch- (13-mm-)] [3/4-inch- (19-mm-)] [1-inch- (25-mm-)] thick, coated, fibrous-glass duct liner complying with ASTM C 1071, and having a maximum flame-spread index of 25 and a maximum smoke-developed index of 50, for both insulation and adhesive, when tested according to ASTM E 84.

Retain one of first two subparagraphs below. Retain second subparagraph for double-wall casings.

a. Cover liner with nonporous foil.

b. Cover liner with nonporous foil and perforated metal.

2. Casing Lining: Adhesive attached, [1/2-inch- (13-mm-)] [3/4-inch- (19-mm-)] [1-inch- (25-mm-)] thick, polyurethane foam insulation complying with UL 181 erosion requirements, and having a maximum flame-spread index of 25 and a maximum smoke-developed index of 50, for both insulation and adhesive, when tested according to ASTM E 84.

3. Air Inlets: Round stub connections or S-slip and drive connections for duct attachment.

4. Air Outlet: S-slip and drive connections.

5. Access: Removable panels for access to parts requiring service, adjustment, or maintenance; with airtight gasket and quarter-turn latches.

6. Fan: Forward-curved centrifugal.

Retain subparagraph below to comply with LEED Prerequisite EQ 1.

7. Airstream Surfaces: Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1.

E. Volume Damper: Galvanized steel with flow-sensing ring and peripheral gasket and self-lubricating bearings.

Leakage rates in first subparagraph below vary among manufacturers and with pressure rating.

1. Maximum Damper Leakage: ARI 880 rated, [2] [3] percent of nominal airflow at [3-inch wg (750-Pa)] [6-inch wg (1500-Pa)] inlet static pressure.

2. Damper Position: Normally [open] [closed].

F. Velocity Sensors: Multipoint array with velocity sensors in cold- and hot-deck air inlets and air outlets.

Default motor characteristics are specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

G. Motor:

1. Comply with NEMA designation, temperature rating, service factor, enclosure type, and efficiency requirements for motors specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

2. Type: [Permanent-split capacitor with SCR for speed adjustment] [Electronically commutated motor].

3. Fan-Motor Assembly Isolation: Rubber isolators.

Verify availability of enclosure types with manufacturer of specified equipment. Delete "Enclosure" Subparagraph below if information is included in schedule on Drawings.

4. Enclosure: [Open dripproof] [Totally enclosed, fan cooled] [Totally enclosed, air over] [Open, externally ventilated] [Totally enclosed, nonventilated] [Severe duty] [Explosion proof] [Dust-ignition-proof machine].

5. Enclosure Materials: [Cast iron] [Cast aluminum] [Rolled steel].

6. Motor Bearings: <Insert special requirements>.

7. Unusual Service Conditions:

a. Ambient Temperature: <Insert deg F (deg C)>.

b. Altitude: <Insert feet (m)> above sea level.

Retain first subparagraph below if application requires this rating.

c. High humidity.

d. <Insert conditions>.

8. Efficiency: Premium efficient.

9. NEMA Design: <Insert designation>.

10. Service Factor: <Insert value>.

11. Motor Speed: [Single speed] [Multispeed].

a. Speed Control: Infinitely adjustable with electronic controls.

Retain subparagraph below if characteristics are not included on Drawings.

12. Electrical Characteristics:

a. Horsepower: <Insert value>.

b. Volts: [120] [208] [230] [460] <Insert value>.

c. Phase: [Single] [Poly].

d. Hz: 60.

e. Full-Load Amperes: <Insert value>.

f. Minimum Circuit Ampacity: <Insert value>.

g. Maximum Overcurrent Protection: <Insert amperage>.

Verify available filter types with manufacturer. Indicate filter thickness in an Air Terminal Unit Schedule on Drawings.

H. Filters: Minimum arrestance according to ASHRAE 52.1 and a minimum efficiency reporting value (MERV) according to ASHRAE 52.2.

Retain one or more of first three subparagraphs below. Indicate filter type in an Air Terminal Unit Schedule on Drawings. 2-inch- (50-mm-) thick foam is not available.

1. Material: Polyurethane foam having 70 percent arrestance and 3 MERV.

2. Material: Glass fiber treated with adhesive; having 80 percent arrestance and 5 MERV.

3. Material: Pleated cotton-polyester media having 90 percent arrestance and 7 MERV.

4. Thickness: [2 inches (50 mm)] [1 inch (25 mm)].

I. Attenuator Section: [0.034-inch (0.85-mm) steel] [0.032-inch (0.8-mm) aluminum] sheet.

Retain one of two "Lining" subparagraphs below. Retain first subparagraph for standard linings; retain second for non-fiber liners.

1. Lining: Adhesive attached, [1/2-inch- (13-mm-)] [3/4-inch- (19-mm-)] [1-inch- (25-mm-)] thick, coated, fibrous-glass duct liner complying with ASTM C 1071, and having a maximum flame-spread index of 25 and a maximum smoke-developed index of 50, for both insulation and adhesive, when tested according to ASTM E 84.

Retain one of first two subparagraphs below. Retain second subparagraph for double-wall casings.

a. Cover liner with nonporous foil.

b. Cover liner with nonporous foil and perforated metal.

2. Lining: Adhesive attached, 3/4-inch- (19-mm-) thick, polyurethane foam insulation complying with UL 181 erosion requirements, and having a maximum flame-spread index of 25 and a maximum smoke-developed index of 50, for both insulation and adhesive, when tested according to ASTM E 84.

Retain subparagraph below to comply with LEED Prerequisite EQ 1.

3. Airstream Surfaces: Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1.

Retain one of first two paragraphs below if heating coil is required.

J. Hydronic Coils: Copper tube, with mechanically bonded aluminum fins spaced no closer than 0.1 inch (2.5 mm), and rated for a minimum working pressure of 200 psig (1380 kPa) and a maximum entering-water temperature of 220 deg F (104 deg C). Include manual air vent and drain valve.

K. Electric-Resistance Heating Coils: Nickel-chromium heating wire, free of expansion noise and hum, mounted in ceramic inserts in a galvanized-steel housing; with primary automatic, and secondary manual, reset thermal cutouts. Terminate elements in stainless-steel, machine-staked terminals secured with stainless-steel hardware.

1. Stage(s): [1] [2] [3].

2. Access door interlocked disconnect switch.

3. Downstream air temperature sensor with local connection to override discharge-air temperature to not exceed a maximum temperature set point (adjustable.)

Retain applicable subparagraphs below.

4. Nickel chrome 80/20 heating elements.

5. Airflow switch for proof of airflow.

6. Fan interlock contacts.

7. Fuses in terminal box for overcurrent protection (for coils more than 48 A).

8. Mercury contactors.

9. Magnetic contactor for each step of control (for three-phase coils).

L. Factory-Mounted and -Wired Controls: Electrical components mounted in control box with removable cover. Incorporate single-point electrical connection to power source.

1. Control Transformer: Factory mounted for control voltage on electric and electronic control units with terminal strip in control box for field wiring of thermostat and power source.

2. Wiring Terminations: Fan and controls to terminal strip. Terminal lugs to match quantities, sizes, and materials of branch-circuit conductors. Enclose terminal lugs in terminal box that is sized according to NFPA 70.

3. Disconnect Switch: Factory-mounted, fuse type.

M. Control Panel Enclosure: NEMA 250, Type 1, with access panel sealed from airflow and mounted on side of unit.

Retain one of two paragraphs below or delete both if controls are specified in Section 230900 "Instrumentation and Control for HVAC."

N. Electric Controls: 24-V damper actuator with wall-mounted electric thermostat and appropriate mounting hardware.

O. Electronic Controls: Bidirectional damper operator and microprocessor-based controller with integral airflow transducer and room sensor. Control devices shall be compatible with temperature controls specified in Section 230900 "Instrumentation and Control for HVAC" and shall have the following features:

Retain applicable subparagraphs below.

1. Occupied and unoccupied operating mode.

2. Remote reset of airflow or temperature set points.

3. Adjusting and monitoring with portable terminal.

4. Communication with temperature-control system specified in Section 230900 "Instrumentation and Control for HVAC."

2.4 SHUTOFF, SINGLE-DUCT AIR TERMINAL UNITS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."

A. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Anemostat Products; a Mestek Company.

2. Carnes.

3. Environmental Technologies, Inc.

4. Krueger.

5. METALAIRE, Inc.

6. Nailor Industries Inc.

7. Phoenix Controls Corporation.

8. Price Industries.

9. Titus.

10. Trane; a business of American Standard Companies.

11. Trox USA Inc.; a subsidiary of the TROX GROUP.

12. Tuttle & Bailey.

13. Warren Technology.

14. <Insert manufacturer's name>.

C. Configuration: Volume-damper assembly inside unit casing with control components inside a protective metal shroud.

D. Casing: [0.034-inch (0.85-mm) steel] [0.032-inch (0.8-mm) aluminum], [single] [double] wall.

Retain one of two "Casing Lining" subparagraphs below. Retain first subparagraph for standard linings; retain second for non-fiber liners.

1. Casing Lining: Adhesive attached, [1/2-inch- (13-mm-)] [3/4-inch- (19-mm-)] [1-inch- (25-mm-)] thick, coated, fibrous-glass duct liner complying with ASTM C 1071, and having a maximum flame-spread index of 25 and a maximum smoke-developed index of 50, for both insulation and adhesive, when tested according to ASTM E 84.

Retain one of first two subparagraphs below. Retain second subparagraph for double-wall casings.

a. Cover liner with nonporous foil.

b. Cover liner with nonporous foil and perforated metal.

2. Casing Lining: Adhesive attached, [1/2-inch- (13-mm-)] [3/4-inch- (19-mm-)] [1-inch- (25-mm-)] thick, polyurethane foam insulation complying with UL 181 erosion requirements, and having a maximum flame-spread index of 25 and a maximum smoke-developed index of 50, for both insulation and adhesive, when tested according to ASTM E 84.

3. Air Inlet: Round stub connection or S-slip and drive connections for duct attachment.

4. Air Outlet: S-slip and drive connections[, size matching inlet size].

5. Access: Removable panels for access to parts requiring service, adjustment, or maintenance; with airtight gasket.

Retain subparagraph below to comply with LEED Prerequisite EQ 1.

6. Airstream Surfaces: Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1.

Retain first paragraph below for units with system-air-powered volume regulators.

E. Regulator Assembly: System-air-powered bellows section incorporating polypropylene bellows for volume regulation and thermostatic control. Bellows shall operate at temperatures from 0 to 140 deg F (minus 18 to plus 60 deg C), shall be impervious to moisture and fungus, shall be suitable for 10-inch wg (2500-Pa) static pressure, and shall be factory tested for leaks.

F. Volume Damper: Galvanized steel with peripheral gasket and self-lubricating bearings.

Leakage rates in first subparagraph below vary among manufacturers and with pressure rating.

1. Maximum Damper Leakage: ARI 880 rated, [2] [3] percent of nominal airflow at [3-inch wg (750-Pa)] [6-inch wg (1500-Pa)] inlet static pressure.

2. Damper Position: Normally [open] [closed].

G. Attenuator Section: [0.034-inch (0.85-mm) steel] [0.032-inch (0.8-mm) aluminum] sheet.

Retain one of two "Lining" subparagraphs below. Retain first subparagraph for standard linings; retain second for non-fiber liners.

1. Lining: Adhesive attached, [1/2-inch- (13-mm-)] [3/4-inch- (19-mm-)] [1-inch- (25-mm-)] thick, coated, fibrous-glass duct liner complying with ASTM C 1071, and having a maximum flame-spread index of 25 and a maximum smoke-developed index of 50, for both insulation and adhesive, when tested according to ASTM E 84.

Retain one of first two subparagraphs below. Retain second subparagraph for double-wall casings.

a. Cover liner with nonporous foil.

b. Cover liner with nonporous foil and perforated metal.

2. Lining: Adhesive attached, 3/4-inch- (19-mm-) thick, polyurethane foam insulation complying with UL 181 erosion requirements, and having a maximum flame-spread index of 25 and a maximum smoke-developed index of 50, for both insulation and adhesive, when tested according to ASTM E 84.

Retain subparagraph below to comply with LEED Prerequisite EQ 1.

3. Airstream Surfaces: Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1.

Retain first paragraph below for multioutlet attenuator system or indicate number of outlets and outlet sizes on Drawings or in a schedule.

H. Multioutlet Attenuator Section: With [two] [three] [four] <Insert number> [6-inch- (150-mm-)] [8-inch- (200-mm-)] [10-inch- (250-mm-)] diameter collars, each with locking butterfly balancing damper.

Retain one of first two paragraphs below if heating coil is required.

I. Hydronic Coils: Copper tube, with mechanically bonded aluminum fins spaced no closer than 0.1 inch (2.5 mm), and rated for a minimum working pressure of 200 psig (1380 kPa) and a maximum entering-water temperature of 220 deg F (104 deg C). Include manual air vent and drain valve.

J. Electric-Resistance Heating Coils: Nickel-chromium heating wire, free of expansion noise and hum, mounted in ceramic inserts in a galvanized-steel housing; with primary automatic, and secondary manual, reset thermal cutouts. Terminate elements in stainless-steel, machine-staked terminals secured with stainless-steel hardware.

1. Access door interlocked disconnect switch.

2. Downstream air temperature sensor with local connection to override discharge-air temperature to not exceed a maximum temperature set point (adjustable.)

Retain applicable subparagraphs below.

3. Nickel chrome 80/20 heating elements.

4. Airflow switch for proof of airflow.

5. Fan interlock contacts.

6. Fuses in terminal box for overcurrent protection (for coils more than 48 A).

7. Mercury contactors.

8. Magnetic contactor for each step of control (for three-phase coils).

Retain one of four paragraphs below or delete all four if controls are specified in Section 230900 "Instrumentation and Control for HVAC."

K. Electric Controls: Damper actuator and thermostat.

1. Damper Actuator: 24 V, powered closed, [spring return open] [powered open].

2. Thermostat: Wall-mounted electronic type with clock display, temperature display in Fahrenheit and Celsius, and space temperature set point.

L. Electronic Controls: Bidirectional damper operator and microprocessor-based thermostat with integral airflow transducer and room sensor. Control devices shall be compatible with temperature controls specified in Section 230900 "Instrumentation and Control for HVAC" and shall have the following features:

1. Damper Actuator: 24 V, powered closed, [spring return open] [powered open].

2. Velocity Controller: Factory calibrated and field adjustable to minimum and maximum air volumes; shall maintain constant airflow dictated by thermostat within 5 percent of set point while compensating for inlet static-pressure variations up to 4-inch wg (1000 Pa); and shall have a multipoint velocity sensor at air inlet.

3. Thermostat: Wall-mounted electronic type with temperature set-point display in Fahrenheit and Celsius.

Retain first paragraph below if control components are specified with the control system; retain second if control components are packaged with the equipment.

M. Direct Digital Controls: Single-package unitary controller and actuator specified in Section 230900 "Instrumentation and Control for HVAC."

N. Direct Digital Controls: Bidirectional damper operators and microprocessor-based controller and room sensor. Control devices shall be compatible with temperature controls specified in Section 230900 "Instrumentation and Control for HVAC" and shall have the following features:

1. Damper Actuator: 24 V, powered closed, [spring return open] [powered open].

2. Terminal Unit Controller: Pressure-independent, variable-air-volume controller with electronic airflow transducer with multipoint velocity sensor at air inlet, factory calibrated to minimum and maximum air volumes, and having the following features:

Retain applicable subparagraphs below.

a. Occupied and unoccupied operating mode.

b. Remote reset of airflow or temperature set points.

c. Adjusting and monitoring with portable terminal.

d. Communication with temperature-control system specified in Section 230900 "Instrumentation and Control for HVAC."

3. Room Sensor: Wall mounted, with temperature set-point adjustment and access for connection of portable operator terminal.

2.5 HANGERS AND SUPPORTS

Indicate the extent of corrosive environment on Drawings.

A. Hanger Rods for Noncorrosive Environments: Cadmium-plated steel rods and nuts.

B. Hanger Rods for Corrosive Environments: Electrogalvanized, all-thread rods or galvanized rods with threads painted with zinc-chromate primer after installation.

C. Steel Cables: [Galvanized steel complying with ASTM A 603] [Stainless steel complying with ASTM A 492].

D. Steel Cable End Connections: Cadmium-plated steel assemblies with brackets, swivel, and bolts designed for duct hanger service; with an automatic-locking and clamping device.

E. Air Terminal Unit Attachments: Sheet metal screws, blind rivets, or self-tapping metal screws; compatible with duct materials.

F. Trapeze and Riser Supports: Steel shapes and plates for units with steel casings; aluminum for units with aluminum casings.

2.6 SEISMIC-RESTRAINT DEVICES

Coordinate specifications for seismic-restraint components in this article with structural engineer and with Drawings. See the Evaluations in Section 230548 "Vibration and Seismic Controls for HVAC" for discussion on seismic-restraint capacities and rating services.

A. General Requirements for Restraint Components: Rated strengths, features, and applications shall be as defined in reports by [an evaluation service member of the ICC Evaluation Service] [the Office of Statewide Health Planning and Development for the State of California] [an agency acceptable to authorities having jurisdiction].

1. Structural Safety Factor: Allowable strength in tension, shear, and pullout force of components shall be at least [four] <Insert number> times the maximum seismic forces to which they will be subjected.

B. Channel Support System: Shop- or field-fabricated support assembly made of slotted steel channels rated in tension, compression, and torsion forces and with accessories for attachment to braced component at one end and to building structure at the other end. Include matching components and corrosion-resistant coating.

C. Restraint Cables: [ASTM A 603, galvanized] [ASTM A 492, stainless]-steel cables with end connections made of cadmium-plated steel assemblies with brackets, swivel, and bolts designed for restraining cable service; with an automatic-locking and clamping device or double-cable clips.

Retain first paragraph below for strengthening resistance of hanger rods against seismic forces that may cause rods to buckle. Use with either channel- or cable-type bracing assemblies. Detail fabrication and indicate locations on Drawings.

D. Hanger Rod Stiffener: [Steel tube or steel slotted-support-system sleeve with internally bolted connections] [Reinforcing steel angle clamped] to hanger rod.

E. Mechanical Anchor Bolts: Drilled-in and stud-wedge or female-wedge type. Select anchor bolts with strength required for anchor and as tested according to ASTM E 488.

2.7 SOURCE QUALITY CONTROL

Retain paragraph below for factory-assembled units. Factory tests are an added cost option and may not be available from some manufacturers. Verify requirement with Owner.

A. Factory Tests: Test assembled air terminal units according to ARI 880.

1. Label each air terminal unit with plan number, nominal airflow, maximum and minimum factory-set airflows, [coil type,] and ARI certification seal.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Install air terminal units according to NFPA 90A, "Standard for the Installation of Air Conditioning and Ventilating Systems."

B. Install air terminal units level and plumb. Maintain sufficient clearance for normal service and maintenance.

Delete paragraph below if thermostats are specified in Section 230900 "Instrumentation and Control for HVAC."

C. Install wall-mounted thermostats.

3.2 HANGER AND SUPPORT INSTALLATION

A. Comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Chapter 5, "Hangers and Supports."

Verify attachment selection and spacing in first two paragraphs below with structural engineer.

B. Building Attachments: Concrete inserts, powder-actuated fasteners, or structural-steel fasteners appropriate for construction materials to which hangers are being attached.

1. Where practical, install concrete inserts before placing concrete.

2. Install powder-actuated concrete fasteners after concrete is placed and completely cured.

3. Use powder-actuated concrete fasteners for standard-weight aggregate concretes and for slabs more than 4 inches (100 mm) thick.

4. Do not use powder-actuated concrete fasteners for lightweight-aggregate concretes and for slabs less than 4 inches (100 mm) thick.

Retain subparagraph below for Projects that require seismic restraints.

5. Do not use powder-actuated concrete fasteners for seismic restraints.

C. Hangers Exposed to View: Threaded rod and angle or channel supports.

D. Install upper attachments to structures. Select and size upper attachments with pull-out, tension, and shear capacities appropriate for supported loads and building materials where used.

3.3 SEISMIC-RESTRAINT-DEVICE INSTALLATION

A. Install hangers and braces designed to support the air terminal units and to restrain against seismic forces required by applicable building codes. Comply with [SMACNA's "Seismic Restraint Manual: Guidelines for Mechanical Systems."] [ASCE/SEI 7.]

B. Select seismic-restraint devices with capacities adequate to carry present and future static and seismic loads.

C. Install cables so they do not bend across edges of adjacent equipment or building structure.

D. Install cable restraints on air terminal units that are suspended with vibration isolators.

E. Install seismic-restraint devices using methods approved by [an evaluation service member of the ICC Evaluation Service] [the Office of Statewide Health Planning and Development for the State of California] [an agency acceptable to authorities having jurisdiction].

F. Attachment to Structure: If specific attachment is not indicated, anchor bracing and restraints to structure, to flanges of beams, to upper truss chords of bar joists, or to concrete members.

G. Drilling for and Setting Anchors:

1. Identify position of reinforcing steel and other embedded items before drilling holes for anchors. Do not damage existing reinforcement or embedded items during drilling. Notify the Architect if reinforcing steel or other embedded items are encountered during drilling. Locate and avoid prestressed tendons, electrical and telecommunications conduit, and gas lines.

2. Do not drill holes in concrete or masonry until concrete, mortar, or grout has achieved full design strength.

3. Wedge Anchors: Protect threads from damage during anchor installation. Install heavy-duty sleeve anchors with sleeve fully engaged in the structural element to which anchor is to be fastened.

4. Set anchors to manufacturer's recommended torque, using a torque wrench.

5. Install zinc-coated steel anchors for interior applications and stainless-steel anchors for applications exposed to weather.

3.4 CONNECTIONS

A. Install piping adjacent to air terminal unit to allow service and maintenance.

B. Hot-Water Piping: In addition to requirements in Section 232113 "Hydronic Piping" and Section 232116 "Hydronic Piping Specialties,"Section 15179 "Hydronic Piping Specialties," connect heating coils to supply with shutoff valve, strainer, control valve, and union or flange; and to return with balancing valve and union or flange.

C. Connect ducts to air terminal units according to [Section 233113 "Metal Ducts."] [Section 233116 "Nonmetal Ducts."]

Coordinate duct installations and specialty arrangements with Drawings.

D. Make connections to air terminal units with flexible connectors complying with requirements in Section 233300 "Air Duct Accessories."

3.5 IDENTIFICATION

A. Label each air terminal unit with plan number, nominal airflow, and maximum and minimum factory-set airflows. Comply with requirements in Section 230553 "Identification for HVAC Piping and Equipment" for equipment labels and warning signs and labels.

3.6 FIELD QUALITY CONTROL

A. Perform tests and inspections.

Retain subparagraph below to require a factory-authorized service representative to assist Contractor with inspections, tests, and adjustments.

1. Manufacturer's Field Service: Engage a factory-authorized service representative to inspect components, assemblies, and equipment installations, including connections, and to assist in testing.

Retain first paragraph below to describe tests and inspections to be performed.

B. Tests and Inspections:

1. After installing air terminal units and after electrical circuitry has been energized, test for compliance with requirements.

Retain first subparagraph below for air terminal units with hot-water coils.

2. Leak Test: After installation, fill water coils and test for leaks. Repair leaks and retest until no leaks exist.

3. Operational Test: After electrical circuitry has been energized, start units to confirm proper motor rotation and unit operation.

4. Test and adjust controls and safeties. Replace damaged and malfunctioning controls and equipment.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

C. Air terminal unit will be considered defective if it does not pass tests and inspections.

D. Prepare test and inspection reports.

3.7 STARTUP SERVICE

A. [Engage a factory-authorized service representative to perform] [Perform] startup service.

1. Complete installation and startup checks according to manufacturer's written instructions.

2. Verify that inlet duct connections are as recommended by air terminal unit manufacturer to achieve proper performance.

3. Verify that controls and control enclosure are accessible.

4. Verify that control connections are complete.

5. Verify that nameplate and identification tag are visible.

6. Verify that controls respond to inputs as specified.

7. <Insert startup steps if any>.

3.8 DEMONSTRATION

A. [Engage a factory-authorized service representative to train] [Train] Owner's maintenance personnel to adjust, operate, and maintain air terminal units.

END OF SECTION 233600

	AIR TERMINAL UNITS
	233600 - 1



