Copyright 2011 AIA
MasterSpec Professional
09/11

Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 237433 - DEDICATED OUTDOOR-AIR UNITS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section includes factory-packaged units capable of supplying up to 100 percent outdoor air and providing cooling [only] [and heating].

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product.

B. LEED Submittals:

1. Product Data for Prerequisite EA 2: Documentation indicating that units comply with applicable requirements in ASHRAE/IESNA 90.1.

2. Product Data for Prerequisite EA 3: Documentation indicating that refrigerants comply.

Coordinate "Product Data for Credit EA 4" Subparagraph below with requirements for refrigerants.

3. Product Data for Credit EA 4: Documentation indicating that equipment and refrigerants comply.

4. Product Data for Prerequisite IEQ 1: Documentation indicating that units comply with ASHRAE 62.1, Section 5 - "Systems and Equipment."

Coordinate "Product Data for Credit IEQ 1" Subparagraph below with requirements for controls.

5. Product Data for Credit IEQ 1: Documentation indicating that units are equipped with a direct outdoor airflow-measuring device capable of measuring the minimum outdoor airflow with accuracy within 15 percent of the design minimum airflow rate, as defined by ASHRAE 62.1.

"Product Data for Credit IEQ 4.1" Subparagraph below applies to LEED-NC, LEED-CI, and LEED-CS; coordinate with requirements for solvent cements and adhesive primers.

6. Product Data for Credit IEQ 4.1: For solvent cements and adhesive primers, documentation including printed statement of VOC content.

"Laboratory Test Reports for Credit IEQ 4" Subparagraph below applies to LEED for Schools.

7. Laboratory Test Reports for Credit IEQ 4: For solvent cements and adhesive primers, documentation indicating that products comply with the testing and product requirements of the California Department of Health Services' "Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers."

Coordinate "Product Data for Credit IEQ 5" Subparagraph below with requirements for filters.

8. Product Data for Credit IEQ 5: Documentation indicating that units include MERV 13 filters rated according to ASHRAE 52.2.

C. Shop Drawings: Include plans, elevations, sections, and attachment details.

Retain "Delegated-Design Submittal" Paragraph below if design services have been delegated to Contractor.

D. Delegated-Design Submittal: For design of [vibration isolation] [seismic restraints] [and] [wind restraints], including analysis data signed and sealed by the qualified professional engineer responsible for their preparation.

1.3 INFORMATIONAL SUBMITTALS

Retain "Coordination Drawings" Paragraph below for situations where limited space necessitates maximum utilization for efficient installation of different components or if coordination is required for installation of products and materials by separate installers.

A. Coordination Drawings: Roof-curb mounting details, drawn to scale, and coordinated with each other, using input from installers of the items involved:

Retain "Seismic Qualification Certificates" Paragraph below if required by seismic criteria applicable to Project. Coordinate with Section 230548 "Vibration and Seismic Controls for HVAC." See ASCE/SEI 7 for certification requirements for equipment and components.

B. Seismic Qualification Certificates: For dedicated outdoor-air units, accessories, and components, from manufacturer.

C. Startup service reports.

D. Sample warranty.

1.4 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

1.5 WARRANTY

A. Special Warranty: Manufacturer agrees to replace components of units that fail in materials or workmanship within specified warranty period.

Verify available warranties and warranty periods for units and components.

Retain "Warranty Period for Compressors" Subparagraph below for units with a refrigeration system.

1. Warranty Period for Compressors: [Five] <Insert number> years from date of Substantial Completion.

Retain "Warranty Period for Heat Exchangers" Subparagraph below for units with fuel-fired furnaces.

2. Warranty Period for Heat Exchangers: [Five] [10] <Insert number> years from date of Substantial Completion.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

2.1 MANUFACTURERS

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. AAON.

2. Addison.

3. Desert Aire.

4. Engineered Air.

5. LCSystems.

6. Munters Corporation, Dehumidification Division; Des Champs Products.

7. Thomas & Betts Corporation; Reznor HVAC Division.

8. <Insert manufacturer's name>.

2.2 PERFORMANCE REQUIREMENTS

LEED Prerequisite IEQ 1 requires compliance with requirements in ASHRAE 62.1, including requirements for controls, surfaces in contact with the airstream, particulate and gaseous filtration, humidification and dehumidification, drain pan construction and connection, finned-tube coil selection and cleaning, and equipment access. Verify, with manufacturers, the availability of units with components and features that comply with these requirements.

A. General Fabrication Requirements: Comply with requirements in ASHRAE 62.1, Section 5 - "Systems and Equipment," and Section 7 - "Construction and System Start-up."

Retain "Delegated Design" Paragraph below if Contractor is required to assume responsibility for design.

B. Delegated Design: Engage a qualified professional engineer, as defined in Section 014000 "Quality Requirements," to design [vibration isolation] [seismic restraints] [and] [wind restraints].

Retain "Seismic Performance" Paragraph below with "Seismic Qualification Certificates" Paragraph in "Informational Submittals" Article for projects requiring seismic design. Delete paragraph if performance requirements are indicated on Drawings. Model building codes and ASCE/SEI 7 establish criteria for buildings subject to earthquake motions. Coordinate requirements with structural engineer.

C. Seismic Performance: Units shall withstand the effects of earthquake motions determined according to [ASCE/SEI 7] <Insert requirement>.

Retain subparagraph below to define the term "withstand" as it applies to this Project. Definition varies with type of building and occupancy and is critical to valid certification. Option is used for essential facilities where equipment must operate immediately after an earthquake.

1. The term "withstand" means "the unit will remain in place without separation of any parts when subjected to the seismic forces specified[ and the unit will be fully operational after the seismic event]."

Retain "Wind-Restraint Performance" Paragraph below with "Delegated-Design Submittal" Paragraph in "Action Submittals" Article for projects requiring wind-restraint design. Model building codes and ASCE/SEI 7 establish criteria for wind loads. Verify requirements of authorities having jurisdiction.

D. Wind-Restraint Performance:

Obtain values for items in subparagraphs below from Project structural engineer or from ASCE/SEI 7.

1. Basic Wind Speed: <Insert value>.

2. Building Classification Category: [I] [II] [III] [IV].

3. Minimum 10 lb/sq. ft (48.8 kg/sq. m) multiplied by the maximum area of unit projected on a vertical plane that is normal to the wind direction and 45 degrees either side of normal.

Retain one or more of "Cabinet Thermal Performance," "Cabinet Surface Condensation," "Maximum Cabinet Leakage," and "Cabinet Deflection Performance" paragraphs below to require explicit cabinet performance requirements. Consult manufacturers to verify ability to comply with specified requirements.

E. Cabinet Thermal Performance:

Retain one of two "Maximum Overall U-Value" paragraphs below.

1. Maximum Overall U-Value: Comply with requirements in ASHRAE/IESNA 90.1.

2. Maximum Overall U-Value: [0.10 Btu/h x sq. ft. x deg F (0.57 W/sq. m x deg K)] <Insert value>.

3. Include effects of metal-to-metal contact and thermal bridges in the calculations.

F. Cabinet Surface Condensation:

1. Cabinet shall have additional insulation and vapor seals if required to prevent condensation on the interior and exterior of the cabinet.

2. Portions of cabinet located downstream from the cooling coil shall have a thermal break at each thermal bridge between the exterior and interior casing to prevent condensation from occurring on the interior and exterior surfaces. The thermal break shall not compromise the structural integrity of the cabinet.

G. Maximum Cabinet Leakage: [0.5] [1] [2] <Insert number> percent of the total supply-air flow at a pressure rating equal to the fan shut-off pressure.

H. Cabinet Deflection Performance:

1. Walls and roof deflection shall be within [1/200] [1/240] <Insert value> of the span at the design working pressure equal to the fan shut-off pressure. Deflection limits shall be measured at any point on the surface.

2. Floor deflections shall be within [1/240] [1/300] [1/360] <Insert value> of the span considering the worst-case condition caused by the following:

a. Service personnel.

b. Internal components.

c. Design working pressure defined for the walls and roof.

I. Electrical components, devices, and accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

If Project has more than one type or configuration of dedicated outdoor-air units, delete "Capacities and Characteristics" Paragraph below and schedule units on Drawings.

J. Capacities and Characteristics:

1. Supply Airflow: <Insert cfm (L/s)>.

2. External Static Pressure: <Insert inches wg (Pa)>.

3. Supply Fan:

a. Size: <Insert wheel size>.

b. Speed: <Insert rpm>.

c. Brake Horsepower: <Insert value>.

4. Supply Fan Motor:

a. Size: <Insert horsepower>.

b. Speed: <Insert rpm>.

c. Volts: [120] [208] [230] [460] <Insert value>.

d. Phase: [Single] [Three].

e. Hertz: 60.

5. Refrigerant Cooling:

a. Capacity: <Insert tons (kW)>.

LEED Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1.

b. Full-Load Efficiency (EER or COP): <Insert number>.

c. Condenser Ambient-Air Temperature: <Insert deg F (deg C)>.

d. Evaporator Coil:

1) Sensible Heat-Transfer Rate: <Insert Btu/h (kW)>.

2) Total Heat-Transfer Rate: <Insert Btu/h (kW)>.

3) Entering-Air, Dry-Bulb Temperature: <Insert deg F (deg C)>.

4) Entering-Air, Wet-Bulb Temperature: <Insert deg F (deg C)>.

5) Leaving-Air, Dry-Bulb Temperature: <Insert deg F (deg C)>.

6) Leaving-Air, Wet-Bulb Temperature: <Insert deg F (deg C)>.

7) Face Area: <Insert sq. ft. (sq. m)>.

8) Maximum Face Velocity: <Insert fpm (m/s)>.

9) Maximum Air-Side, Static-Pressure Drop: <Insert inches wg (Pa)>.

10) Fin Spacing: <Insert fins per inch (cm)>.

11) Fin Thickness: <Insert inches (mm)>.

12) Number of Rows: <Insert number>.

Retain one of "Electric-Resistance Heating Coils," "Gas-Fired Furnace Heating," or "Hot Water Heating Coils" subparagraphs below.

6. Electric-Resistance Heating Coils:

a. Heat-Transfer Rate: <Insert Btu/h (kW)>.

b. Entering-Air Temperature: <Insert deg F (deg C)>.

c. Leaving-Air Temperature: <Insert deg F (deg C)>.

d. Power Input: <Insert kilowatts>.

e. Volts: [120] [208] [230] [480] <Insert value>.

f. Phase: [Single] [Three].

g. Hertz: 60.

h. Full-Load Amperes: <Insert value>.

i. Maximum Overcurrent Protection: <Insert amperage>.

j. Capacity Control Number of Steps: <Insert number>.

7. Gas-Fired Furnace Heating:

a. Heat-Transfer Rate: <Insert Btu/h (kW)>.

b. Entering-Air Temperature: <Insert deg F (deg C)>.

c. Leaving-Air Temperature: <Insert deg F (deg C)>.

LEED Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1, Table 6.8.1E, "Warm Air Furnaces and Combination Warm Air Furnaces/Air-Conditioning Units, Warm Air Duct Furnaces and Unit Heaters."

d. Efficiency: [80] <Insert number> percent.

e. Fuel: [Natural] [Propane] gas.

Consider actual heating value of fuel source if retaining "Gas Heating Value" Subparagraph below. Contact fuel supplier and unit manufacturers to determine impact. Insert text indicating heating value of fuel if applicable.

f. Gas Heating Value: <Insert Btu/cu. ft. (kJ/L)>.

g. Gas Input: <Insert cfh (mL/s)>.

h. Gas Burner Electrical Characteristics:

1) Power Input: <Insert kilowatts>.

2) Volts: [120] [208] [230] [460] <Insert value>.

3) Phase: [Single] [Three].

4) Hertz: 60.

5) Full-Load Amperes: <Insert value>.

6) Minimum Circuit Ampacity: <Insert value>.

7) Maximum Overcurrent Protection: <Insert amperage>.

8. Hot-Water Heating Coils:

a. Heat-Transfer Rate: <Insert Btu/h (kW)>.

b. Entering-Air Temperature: <Insert deg F (deg C)>.

c. Leaving-Air Temperature: <Insert deg F (deg C)>.

d. Face Area: <Insert sq. ft. (sq. m)>.

e. Maximum Face Velocity: <Insert fpm (m/s)>.

f. Maximum Air-Side, Static-Pressure Drop: <Insert inches wg (Pa)>.

g. Coil Type: [Continuous circuit] [Self-draining] [Cleanable].

h. Piping Connections: [Threaded] [Flanged]; [same end] [opposite ends] of coil.

i. Tube Thickness: <Insert inches (mm)>.

j. Fin Spacing: <Insert fins per inch (cm)>.

k. Fin Thickness: <Insert inches (mm)>.

l. Number of Rows: <Insert number>.

Value option "Coil Working-Pressure Ratings" Subparagraph below is standard for most copper tube coils. Verify manufacturer's ability to achieve specified ratings.

m. Coil Working-Pressure Ratings: [200 psig (1380 kPa), 325 deg F (163 deg C)] <Insert value>.

Retain "Fluid Flow," "Maximum Fluid-Pressure Drop," "Entering-Fluid Temperature," "Leaving-Fluid Temperature," and "Fluid Velocity" subparagraphs below for hot-water heating coils.

n. Fluid Flow: <Insert gpm (L/s)>.

o. Maximum Fluid-Pressure Drop: <Insert feet of head (kPa)>.

p. Entering-Fluid Temperature: <Insert deg F (deg C)>.

q. Leaving-Fluid Temperature: <Insert deg F (deg C)>.

r. Fluid Velocity: <Insert fpm (L/s)>.

9. Overall Unit Electrical Characteristics:

a. Volts: [120] [208] [230] [460] <Insert value>.

b. Phase: [Single] [Three].

c. Hertz: 60.

d. Full-Load Amperes: <Insert value>.

e. Minimum Circuit Ampacity: <Insert value>.

f. Maximum Overcurrent Protection: <Insert amperage>.

2.3 CABINET

A. Construction: [Single] [or] [double] wall.

B. Exterior Casing Material: [Galvanized steel with paint finish] [or] [stainless steel].

Retain "Interior Casing Material" paragraph below for double-wall units.

C. Interior Casing Material: [Galvanized] [or] [stainless] steel.

D. Lifting and Handling Provisions: Factory-installed shipping skids and lifting lugs.

Coordinate "Base Rails" Paragraph below with "Exterior Casing Material" Paragraph above.

E. Base Rails: [Galvanized] [Stainless]-steel rails for mounting on roof curb or pad as indicated.

Retain "Access for Inspection, Cleaning, and Maintenance" Paragraph below if applying for LEED certification or if required by Project requirements or authorities having jurisdiction. LEED Prerequisite IEQ 1 requires compliance with ASHRAE 62.1, which includes requirements for equipment access for inspection, cleaning, and maintenance.

F. Access for Inspection, Cleaning, and Maintenance: Comply with requirements in ASHRAE 62.1.

1. Service Doors: Hinged access doors with gaskets. Material and construction of doors shall match material and construction of cabinet in which doors are installed.

G. Roof: Standing seam or membrane; sloped to drain water.

H. Floor: Reinforced, metal surface; reinforced to limit deflection when walked on by service personnel. Insulation shall be below metal walking surface.

I. Cabinet Insulation:

1. Type: [Fibrous-glass duct lining complying with ASTM C 1071, Type II] [or] [flexible elastomeric insulation complying with ASTM C 534, Type II, sheet materials.]

2. Thickness: [1 inch (25 mm)] [2 inches (50 mm)] <Insert dimension>.

3. Insulation Adhesive: Comply with ASTM C 916, Type I.

4. Mechanical Fasteners: Suitable for adhesive, mechanical, or welding attachment to casing without damaging liner and without causing air leakage when applied as recommended by manufacturer.

J. Condensate Drain Pans:

First option in "Shape" Subparagraph below is minimum slope in ASHRAE 62.1.

1. Shape: Rectangular, with [1] [2] percent slope in at least two planes to direct water toward drain connection.

2. Size: Large enough to collect condensate from cooling coils including coil piping connections, coil headers, and return bends.

Retain option in "Length" Subparagraph below to comply with LEED Prerequisite IEQ 1 or if required by Project requirements or authorities having jurisdiction; otherwise, insert distance.

a. Length: Extend drain pan downstream from leaving face [to comply with ASHRAE 62.1] <Insert distance>.

b. Depth: A minimum of [2 inches (50 mm)] <Insert dimension> deep.

Retain one of two "Configuration" subparagraphs below.

3. Configuration: Single wall.

4. Configuration: Double wall, with space between walls filled with foam insulation and moisture-tight seal.

Retain one of two "Material" subparagraphs below.

5. Material: Galvanized-steel sheet with asphaltic waterproofing compound coating on pan top surface.

6. Material: Stainless-steel sheet.

7. Drain Connection:

a. Located on [one end] [both ends] of pan, at lowest point of pan.

b. Terminated with threaded nipple.

c. Minimum Connection Size: [NPS 1 (DN 25)] [NPS 2 (DN 50)] <Insert size>.

8. Units with stacked coils shall have an intermediate drain pan to collect condensate from top coil.

Retain "Surfaces in Contact with Airstream" Paragraph below to comply with LEED Prerequisite IEQ 1 or if required by Project requirements or authorities having jurisdiction.

K. Surfaces in Contact with Airstream: Comply with requirements in ASHRAE 62.1 for resistance to mold and erosion.

Retain "Roof Curb" paragraph below to require unit manufacturer to furnish roof curb; delete to require unit installation on Contractor-provided equipment supports. Coordinate with "Installation" Article.

L. Roof Curb: Full-perimeter curb of sheet metal, minimum [8 inches (200 mm)] [12 inches (300 mm)] [16 inches (400 mm)] <Insert number> high, with wood nailer, neoprene sealing strip, and welded Z-bar flashing.

1. Comply with requirements in "The NRCA Roofing Manual."

2.4 SUPPLY FAN

Retain either "Forward-Curved Fan Type" or "Plenum Fan Type" Paragraph below, or both. Retain both when Project includes more than one unit and both fan types are employed. Verify availability with manufacturers.

Some manufacturers coat fan assemblies with a proprietary coating system to prevent corrosion.

A. Forward-Curved Fan Type: Centrifugal; statically and dynamically balanced.

1. Fan Wheel Material: [Galvanized] [Painted] [Coated] steel, mounted on solid-steel shaft.

2. Bearings: [Self-aligning, permanently lubricated ball bearings] [Pillow-block bearings rated L50 for 200,000 hours and having external grease fittings].

B. Plenum Fan Type: Single width, non-overloading, with backward-inclined or airfoil blades.

1. Fan Wheel Material: Aluminum; attached directly to motor shaft.

2. Fan Wheel Drive and Arrangement: Direct drive, AMCA Arrangement 4.

3. Fan panel and frame Material: Powder-coated steel, stainless steel, or aluminum.

4. Fan Enclosure: Easily removable enclosure around rotating parts.

5. Fan Balance: Precision balance fan below 0.08 inch/s (2.0 mm/s) at design speed with filter in.

C. Service Factor for Belt Drive Applications: [Multiple ]V-belt drive with matching fan pulley and adjustable motor sheaves and belt assembly with minimum [1.4] [1.5] [2.0] <Insert value> service factor.

D. Motors:

Default motor characteristics are specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

1. Comply with NEMA designation, temperature rating, service factor, and efficiency requirements for motors specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

2. Enclosure: [Open dripproof] [Totally enclosed].

Retain "Enclosure Materials," "Motor Bearings," "Unusual Service Conditions," "Efficiency," "NEMA Design," and "Service Factor" subparagraphs below if options are available from equipment manufacturers and are different from default requirements specified in Section 230513 "Common Motor Requirements for HVAC Equipment." Consider each subparagraph and retain only those that vary from default requirements.

3. Enclosure Materials: [Cast iron] [Cast aluminum] [Rolled steel].

4. Motor Bearings: <Insert requirements>.

5. Unusual Service Conditions:

a. Ambient Temperature: <Insert deg C>.

b. Altitude: <Insert feet (m)> above sea level.

c. High humidity.

d. <Insert conditions>.

6. Efficiency: Premium efficient.

7. NEMA Design: <Insert designation>.

8. Service Factor: [1.0] [1.15] <Insert value>.

Retain first option in "Mounting" Paragraph below for units installed in seismic areas and retain one of last two options.

E. Mounting: Fan wheel, motor, and drives shall be mounted to fan casing with [restrained] [elastomeric] [spring] isolators.

2.5 COOLING COILS

Options in this article are not available from all manufacturers on all models; verify availability with manufacturers.

A. Capacity Ratings: Comply with ASHRAE 33 and ARI 410 [and coil bearing the ARI label].

B. Coil Casing Material: [Manufacturer's standard material] [Aluminum] [Galvanized steel] [Stainless steel] <Insert material>.

C. Tube Material: [Copper] <Insert material>.

D. Tube Header Material: [Manufacturer's standard material] [Copper] [Carbon steel] [Red brass] <Insert material>.

E. Fin Material: [Aluminum] [Copper] <Insert material>.

F. Fin and Tube Joints: Mechanical bond.

G. Leak Test: Coils shall be leak tested with air underwater.

H. Refrigerant Coil Capacity Reduction: Circuit coils for [face] [row] [interleaved] control.

I. Refrigerant Coil Suction and Distributor Header Materials: Seamless copper tube with brazed joints.

Retain "Coating" Paragraph below for projects in corrosive environments.

J. Coating: Phenolic epoxy corrosion-protection coating after assembly.

2.6 REFRIGERATION SYSTEM

A. Comply with requirements in ASHRAE 15, "Safety Standard for Refrigeration Systems."

B. Refrigerant Charge: Factory charged with refrigerant and filled with oil.

Verify availability of crankcase heater in "Compressors" Paragraph below with manufacturers.

C. Compressors: [Scroll] [Reciprocating or scroll] compressors with integral vibration isolators, internal overcurrent and overtemperature protection, internal pressure relief[, and crankcase heater].

LEED-NC, LEED-CS, and LEED for Schools Credit EA 4 award a single point if all HVAC&R equipment uses environmentally friendly refrigerants. R-134a, R-407C, and R-410A are HFC refrigerants and should be evaluated for the credit. Verify available refrigerants with manufacturers.

D. Refrigerant: [R-22] [R-134a] [R-407C] [R-410A] [HFC refrigerant] <Insert other available type>.

1. Classified as Safety Group A1 according to ASHRAE 34.

2. Provide unit with operating charge of refrigerant.

E. Refrigeration System Specialties:

Six subparagraphs below are optional components. Verify availability of specialties with manufacturer.

1. Expansion valve with replaceable thermostatic element.

2. Refrigerant dryer.

3. High-pressure switch.

4. Low-pressure switch.

5. Thermostat for coil freeze-up protection during low ambient temperature operation or loss of air.

6. Brass service valves installed in discharge and liquid lines.

F. Capacity Control:

Retain one or more of four subparagraphs below. Retaining all four subparagraphs is nonrestrictive. Coordinate with manufacturers.

1. Hot-gas bypass refrigerant control for capacity control with continuous dehumidification on a single compressor.

Control method in first subparagraph below is proprietary to LCSystems.

2. Patented, Rawal APR control with zero to 100 percent modulating capacity control using hot-gas bypass. Evaporator coil shall be continuously active for dehumidification.

Control method in first subparagraph below is proprietary to Reznor.

3. Single compressor with evaporator and condenser coil within the refrigerant section to provide initial pre-cooling and to reheat for humidity control.

Control method in subparagraph below is available from Addison and Des Champs.

4. Heat-pipe heat exchanger wrapped around the evaporator coil to pre-cool the air entering the evaporator coil and reheat the air leaving the evaporator coil to control humidity.

G. Refrigerant [condenser] [and] [reheat condenser] coils:

1. Capacity Ratings: Complying with ASHRAE 33 and ARI 410 [and coil bearing the ARI label].

2. Tube Material: Copper.

3. Fin Material: [Aluminum] [Copper].

4. Fin and Tube Joint: Mechanical bond.

5. Leak Test: Coils shall be leak tested with air underwater.

Retain "Coating" Subparagraph below for projects in corrosive environments.

6. Coating: Phenolic epoxy corrosion-protection coating after assembly.

H. Condenser Fan Assembly:

1. Fans: Direct-drive propeller type with statically and dynamically balanced fan blades.

Default motor characteristics are specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

2. Fan Motors:

a. Comply with NEMA designation, temperature rating, service factor, and efficiency requirements for motors specified in Section 230513 "Common Motor Requirements for HVAC Equipment."

b. Motor Enclosure: Totally enclosed non-ventilating (TENV) or totally enclosed air over (TEAO) enclosure.

Retain subparagraphs below if options are available from equipment manufacturers and are different from default requirements specified in Section 230513 "Common Motor Requirements for HVAC Equipment." Consider each subparagraph and retain only those that vary from default requirements.

c. Enclosure Materials: [Cast iron] [Cast aluminum] [Rolled steel].

d. Motor Bearings: [Permanently lubricated bearings] <Insert requirements>.

e. Unusual Service Conditions:

1) Ambient Temperature: <Insert deg C>.

2) Altitude: <Insert feet (m)> above sea level.

3) High humidity.

4) <Insert conditions>.

f. Built-in overcurrent and thermal-overload protection.

g. Efficiency: Premium efficient.

h. NEMA Design: <Insert designation>.

i. Service Factor: <Insert value>.

3. Fan Safety Guards: Steel with corrosion-resistant coating.

I. Safety Controls:

1. Compressor motor and condenser coil fan motor low ambient lockout.

2. Overcurrent protection for compressor motor.

Retain one of first three heating articles below. If Project has more than one unit and each has a different heating method, retain one or more of five alternative heating articles and indicate heating method in schedule on Drawings.

2.7 ELECTRIC-RESISTANCE HEATING COIL

A. UL Compliance: Comply with requirements in UL 1995, "Heating and Cooling Equipment."

Retain one of two "Electric-Resistance Heating Elements" paragraphs below. Verify availability of electric-resistance heating with manufacturers.

B. Electric-Resistance Heating Elements:

1. Coiled Resistance Wire: 80 percent nickel and 20 percent chromium.

2. Tubular-Steel Sheath: Compacted magnesium oxide powder.

3. Fins: Spiral-wound, copper-plated, steel fins continuously brazed to sheath.

4. Heating Capacity: Low density 35 W per sq. in. (54 kW per sq. m), factory wired for single-point wiring connection; with time delay for element staging and overcurrent- and overheat-protection devices.

5. Safety Controls:

a. Blower-motor interlock, air-pressure switch.

b. Quiet mercury contactors.

c. Time delay between steps.

d. Integral, nonfused power disconnect switch.

C. Electric-Resistance Heating Elements:

1. Open-Coil Resistance Wire: 80 percent nickel and 20 percent chromium.

2. Supports and Insulation: Floating ceramic bushings recessed into casing openings; fastened to supporting brackets and mounted in galvanized-steel frame.

3. Heating Capacity: Low density 35 W per sq. in. (54 kW per sq. m), factory wired for single-point wiring connection; with time delay for element staging and overcurrent- and overheat-protection devices.

4. Safety Controls:

a. Blower-motor interlock, air-pressure switch.

b. Quiet mercury contactors.

c. Time delay between steps.

d. Integral, nonfused power disconnect switch.

2.8 INDIRECT-FIRED GAS FURNACE HEATING

A. Furnace Assembly:

1. Factory assembled, piped, and wired.

2. Comply with requirements in NFPA 54, "National Fuel Gas Code," and ANSI Z21.47, "Gas-Fired Central Furnaces."

3. AGA Approval: Designed and certified by and bearing label of AGA.

B. Burners:

1. Heat-Exchanger Material: [Aluminized steel with stainless-steel inserts] [Stainless steel] with a minimum thermal efficiency of 80 percent.

2. Fuel: [Natural] [Propane] gas.

3. Ignition: Electronically controlled electric spark with flame sensor.

Verify availability of high-altitude feature in "High-Altitude (Model) (Kit)" Subparagraph below with manufacturers.

4. High-Altitude [Model] [Kit]: For Project elevations more than 2000 feet (610 m) above sea level.

C. Heat-Exchanger Drain Pan Material: Stainless steel.

Retain one of two "Venting" paragraphs below.

D. Venting: Gravity vented.

E. Venting: Power vent with integral, motorized centrifugal fan interlocked with gas valve.

F. Safety Controls:

1. Gas Control Valve: [Single stage] [Two stage] [Electronic modulating].

2. Gas Train: Single-body, regulated, redundant, 24-V ac gas valve assembly containing pilot solenoid valve, pilot filter, pressure regulator, pilot shutoff, and manual shutoff.

2.9 HOT-WATER HEATING COIL

A. Capacity Ratings: Comply with ASHRAE 33 and ARI 410 [and coil bearing the ARI label].

B. Coil Casing Material: [Manufacturer's standard material] [Aluminum] [Galvanized steel] [Stainless steel] <Insert material>.

C. Tube Material: [Copper] <Insert material>.

D. Tube Header Material: [Manufacturer's standard material] [Copper] [Carbon steel] [Red brass] <Insert material>.

E. Fin Material: [Aluminum] [Copper] <Insert material>.

F. Fin and Tube Joints: Mechanical bond.

G. Leak Test: Coils shall be leak tested with air underwater.

Retain "Coating" Paragraph below for projects in corrosive environments.

H. Coating: Phenolic epoxy corrosion-protection coating after assembly.

2.10 OUTDOOR-AIR INTAKE HOOD

A. Type: Manufacturer's standard hood or louver.

B. Materials: Match cabinet.

C. Bird Screen: Comply with requirements in ASHRAE 62.1.

D. Configuration: Designed to inhibit wind-driven rain and snow from entering unit.

2.11 FILTERS

Retain one or more of "Cleanable Filters," "Disposable Panel Filters," "Extended-Surface, Disposable Panel Filters," and "Extended-Surface, Nonsupported-Media Filters" paragraphs below.

A. Cleanable Filters: 2-inch- (50-mm-) thick, cleanable metal mesh.

LEED Prerequisite IEQ 1 requires compliance with ASHRAE 62.1, which requires a MERV rating of 6 or higher.

LEED Credit IEQ 5 requires minimum MERV-13 filters. Verify availability with unit manufacturers.

B. Disposable Panel Filters:

1. Comply with NFPA 90A.

2. Factory-fabricated, viscous-coated, flat-panel type.

3. Thickness: [1 inch (25 mm)] [2 inches (50 mm)].

4. Initial Resistance: <Insert inches wg (Pa)>.

5. Recommended Final Resistance: <Insert inches wg (Pa)>.

6. Minimum Arrestance: [80] <Insert value>, according to ASHRAE 52.1.

7. Minimum Merv: [6] <Insert value>, according to ASHRAE 52.2.

8. Media: Interlaced glass fibers sprayed with nonflammable adhesive[ and antimicrobial agent].

C. Extended-Surface, Disposable Panel Filters:

1. Comply with NFPA 90A.

2. Factory-fabricated, dry, extended-surface type.

3. Thickness: [1 inch (25 mm)] [2 inches (50 mm)] [4 inches (100 mm)].

4. Initial Resistance: <Insert inches wg (Pa)>.

5. Recommended Final Resistance: <Insert inches wg (Pa)>.

6. Minimum Arrestance: [90] <Insert value>, according to ASHRAE 52.1.

7. Minimum Merv: [7] <Insert value>, according to ASHRAE 52.2.

8. Media: Fibrous material formed into deep-V-shaped pleats[ with antimicrobial agent] and held by self-supporting wire grid.

D. Extended-Surface, Nonsupported-Media Filters:

1. Comply with NFPA 90A.

2. Factory-fabricated, dry, extended-surface, self-supporting type.

3. Initial Resistance: <Insert inches wg (Pa)>.

4. Recommended Final Resistance: <Insert inches wg (Pa)>.

5. Minimum Arrestance: [95] <Insert value>, according to ASHRAE 52.1.

6. Minimum Merv: [13] <Insert value>, according to ASHRAE 52.2.

7. Media: Fibrous material [coated with an antimicrobial agent and ]constructed so individual pleats are maintained in tapered form by flexible internal supports under rated-airflow conditions.

E. Mounting Frames:

1. Panel filters arranged for flat or angular orientation, with access doors on both sides of unit. Filters shall be removable from one side or from access plenum.

2. Extended surface filters arranged for flat orientation, removable from access plenum.

3. Galvanized or stainless steel with gaskets and fasteners, suitable for bolting together into built-up filter banks[ with space for prefilter].

2.12 ELECTRICAL POWER CONNECTIONS

Not all manufacturers provide all features indicated in this article. Verify availability with manufacturers.

A. General Electrical Power Connection Requirements: Factory-installed and -wired switches, motor controllers, transformers, and other necessary electrical devices shall provide a [single-point ]field power connection to unit.

B. Enclosure: NEMA 250, [Type 3R] [Type 4] [Type 4X] <Insert type>, mounted in unit with hinged access door in unit cabinet having a lock and key or padlock and key,

C. Wiring: Numbered and color-coded to match wiring diagram.

D. Wiring Location: Install factory wiring outside an enclosure in a raceway.

E. Power Interface: Field power interface shall be to [wire lugs] [NEMA KS 1, heavy-duty, nonfused disconnect switch].

F. Factory Wiring: Branch power circuit to each motor and to controls with one of the following disconnecting means:

1. NEMA KS 1, heavy-duty, fusible switch with rejection-type fuse clips rated for fuses. Select and size fuses to provide Type 2 protection according to IEC 60947-4-1.

2. NEMA KS 1, heavy-duty, nonfusible switch.

3. UL 489, motor-circuit protector (circuit breaker) with field-adjustable, short-circuit trip coordinated with motor locked-rotor amperes.

G. Factory-Mounted, Overcurrent-Protection Service: For each motor.

Retain "Transformer" Paragraph below if required for controls or unit-mounted convenience power receptacle.

H. Transformer: Factory mounted with primary and secondary fuses and sized with enough capacity to operate electrical load plus spare capacity.

I. Controls: Factory wire unit-mounted controls where indicated.

Retain "Lights" and "Receptacle" paragraphs below if unit-mounted lights and receptacle are required.

J. Lights: Factory wire unit-mounted lights.

K. Receptacle: Factory wire unit-mounted, ground fault interrupt (GFI) duplex receptacle.

L. Control Relays: Auxiliary and adjustable time-delay relays.

2.13 CONTROLS

Retain first paragraph below if cooling, heating, humidity, and pressure controls are not provided with unit. Not all manufacturers provide all features indicated in this article. Verify availability with manufacturers.

A. Control equipment and sequence of operation are specified in Section 230900 "Instrumentation and Control for HVAC."

Retain "Control Valves" Paragraph below if manufacturers do not provide control valves for water coils. Coordinate requirements for control valves with Section 230900 "Instrumentation and Control for HVAC."

B. Control Valves: Comply with requirements in Section 230900 "Instrumentation and Control for HVAC."

C. Control Wiring: Factory wire connection for controls' power supply.

D. Control Devices: Sensors, transmitters, relays, switches, detectors, operators, actuators, and valves shall be manufacturer's standard items to accomplish indicated control functions.

E. [Remote] [Unit]-Mounted Status Panel:

1. Cooling/Off/Heating Controls: Control operational mode.

2. Damper Position: Indicate position of outdoor-air dampers in terms of percentage of outdoor air.

3. Status Lights:

a. Filter dirty.

b. Fan operating.

c. Cooling operating.

d. Heating operating.

e. Smoke alarm.

f. General alarm.

g. <Insert points>.

4. Digital Numeric Display:

a. Outdoor airflow.

b. Supply airflow.

c. Outdoor dry-bulb temperature.

d. Outdoor dew point temperature.

e. Space temperature.

f. Supply temperature.

g. Space relative humidity.

h. Space carbon dioxide level.

i. <Insert points>.

F. Control Dampers:

1. Damper Location: Factory installed inside unit for ease of blade axle and bushing service. Arrange dampers located in a mixing box to achieve convergent airflow to minimize stratification.

2. Damper Leakage: Comply with requirements in AMCA 500-D. Leakage shall not exceed 6.5 cfm per sq. ft. (33 L/s per sq. m) at a static-pressure differential of 4.0 inches water column (1000 Pa) when a torque of 5 inch pounds per sq. ft. (30.1 Newton meters per sq. m) is applied to the damper jackshaft.

3. Damper Rating: Rated for close-off pressure equal to the fan shutoff pressure.

Retain "Damper Label" Subparagraph below for AMCA seals to ensure performance.

4. Damper Label: Bear the AMCA seal for both air leakage and performance.

5. Blade Configuration: Unless otherwise indicated, use parallel blade configuration for two-position control and equipment isolation service and use modulating control when mixing two airstreams. For other applications, use an opposed-blade configuration.

6. Damper Frame Material: [Extruded aluminum] [galvanized steel] [or] [stainless steel].

7. Blade Type: [Single-thickness metal reinforced with multiple V-grooves] [or] [hollow-shaped airfoil].

8. Blade Material: [Extruded aluminum] [galvanized steel] [or] [stainless steel].

9. Maximum Blade Width: 6 inches (150 mm).

10. Maximum Blade Length: 48 inches (1200 mm).

11. Blade Seals: Replaceable, continuous perimeter vinyl seals and jambs with stainless-steel compression-type seals.

12. Bearings: Thrust bearings for vertical blade axles.

13. Airflow Measurement:

a. Monitoring System: Complete and functioning system of airflow monitoring as an integral part of the damper assembly where indicated.

b. Remote Monitoring Signal: 0-10 volt or 4-20 mA scaled signal.

c. Accuracy of flow measurement: Within [5] [10] <Insert value> percent of the actual flow rate between the range of the scheduled minimum and maximum airflow. For units with a large range between minimum and maximum airflow, configure the damper sections and flow measurement assembly as necessary to comply with accuracy.

d. Straightening Device: Integral to the flow measurement assembly if required to achieve the specified accuracy as installed.

e. flow measuring device: Suitable for operation in untreated and unfiltered outdoor air. If necessary, include temperature and altitude compensation and correction to maintain the accuracy.

G. Damper Operators:

1. Factory-installed electric operator for each damper assembly with one operator for each damper assembly mounted to the damper frame.

2. Operator capable of shutoff against fan pressure and able to operate the damper with sufficient reserve power to achieve smooth modulating action and proper speed of response at the velocity and pressure conditions to which the damper is subjected.

3. Maximum Operating Time: Open or close damper 90 degrees in [60] [90] <Insert value> seconds.

4. Adjustable Stops: For both maximum and minimum positions.

5. Position Indicator and Graduated Scale: Factory installed on each actuator with words "OPEN" and "CLOSED," or similar identification, at travel limits.

6. Spring-return operator to fail-safe; either closed or open as required by application.

7. Operator Type: Direct coupled, designed for minimum 60,000 full-stroke cycles at rated torque.

8. Position feedback Signal: For remote monitoring of damper position.

9. Coupling: V-bolt and V-shaped, toothed cradle.

10. Circuitry: Electronic overload or digital rotation-sensing circuitry.

H. Refrigeration System Controls:

1. Unit-mounted enthalpy controller shall lock out refrigerant system when outdoor-air enthalpy is less than [28 Btu/lb (65 kJ/kg)] <Insert value> of dry air or outdoor-air temperature is less than 60 deg F (15 deg C)<Insert value>.

Both subparagraphs below are proprietary to Reznor.

2. Outdoor-air sensor de-energizes dehumidifier operation when outdoor-air temperature is less than 60 deg F (15 deg C)<Insert value>.

3. Relative-humidity sensor energizes dehumidifier operation when relative humidity is more than [50] <Insert value> percent.

I. Furnace Controls:

Retain first subparagraph below for discharge sensing.

1. [Factory-mounted sensor in supply outlet] [Remote sensor for field installation in supply-air duct] with sensor adjustment located in control panel to modulate gas furnace burner to maintain space temperature.

Retain first subparagraph below for remote sensing.

2. Wall-mounted, space-temperature sensor with [temperature adjustment] [unit-mounted temperature adjustment] [adjustment on remote-control panel] to modulate gas furnace burner to maintain space temperature.

3. Remote Setback: Adjustable room thermostat selected by timer, set at [50 deg F (10 deg C)] <Insert temperature>; cycles supply fan and gas furnace burner to maintain space temperature.

Retain "Staged Burner Control" or "Electromechanical or Electronic Burner Control" Subparagraph below for units with gas-fired furnace heating option. Retain first subparagraph for units with indirect-fired furnaces; retain second subparagraph for units with direct-fired furnaces.

4. Staged Burner Control: [Two] [Four] steps of control.

5. Electromechanical or Electronic Burner Control: 20 to 100 percent modulation of the firing rate; 10 to 100 percent with dual-furnace units.

Retain "Electric-Resistance Heat Controls" Paragraph below for units with electric-resistance heating coil option.

J. Electric-Resistance Heat Controls:

Retain first subparagraph below for electric-resistance heat with discharge-air temperature control.

1. [Factory-mounted sensor in unit discharge] [Remote sensor for field installation in supply-air duct] with sensor adjustment located in control panel to control electric coil to maintain temperature.

Retain first subparagraph below for electric-resistance heat with remote temperature control.

2. Wall-mounted, space-temperature sensor with [temperature adjustment] [unit-mounted temperature adjustment] [adjustment on remote-control panel] to control electric coil to maintain temperature.

3. Capacity Controls: [On/off] [Multiple steps] [Modulating SCR] <Insert type>.

Retain first "Hot-Water Coil Controls" Paragraph below for units with hot-water heating coils and for discharge-air temperature control.

K. Hot-Water Coil Controls: [Factory-mounted sensor in unit discharge] [Remote sensor for field installation in supply-air duct] with sensor adjustment located in control panel to modulate factory-[mounted] [furnished] coil control valve to maintain temperature.

Retain "Hot-Water Coil Controls" Paragraph below for hot-water heating coils and for remote temperature control.

L. Hot-Water Coil Controls: Space-temperature sensor with [temperature adjustment] [unit-mounted temperature adjustment] [adjustment on remote-control panel] to modulate factory-[mounted] [furnished] coil control valve to maintain temperature.

Retain "Damper Controls" Paragraph below if unit maintains minimum building pressure by introducing variable quantities of outdoor air.

M. Damper Controls: Space pressure sensor modulates outdoor- and return-air dampers to maintain a positive pressure in space at a minimum of [0.05 inch wg (12.4 Pa)] <Insert value> with respect to outdoor reference.

Revise "Integral Smoke Alarm" Paragraph below according to requirements of authorities having jurisdiction.

N. Integral Smoke Alarm: Smoke detector installed in [supply] [and] [return] air.

O. DDC Temperature Control: Standalone control module for link between unit controls and DDC temperature-control system. Control module shall be compatible with control system specified in Section 230900 "Instrumentation and Control for HVAC." Links shall include the following:

1. Start/stop interface relay, and relay to notify DDC temperature-control system alarm condition.

2. Hardware interface or additional sensors for the following:

a. Room temperature.

b. Discharge-air temperature.

c. Refrigeration system operating.

d. Furnace operating.

LEED-NC and LEED for Schools Credit EA 5, LEED-CI Credit EA 3, and LEED-CS Credit EA 5.1 require continuous metering equipment for monitoring building energy consumption performance over time. Retain five subparagraphs below if required to comply with the requirements for this credit or if required by Project requirements or authorities having jurisdiction. Verify availability of feature with unit manufacturers.

e. Constant and variable motor loads.

f. Variable-frequency-controller operation.

g. Cooling load.

h. Economizer cycles.

i. Air-distribution static pressure and ventilation-air volumes.

Retain "BAS Interface" Paragraph below if unit controls interface with the BAS. Coordinate with Section 230900 "Instrumentation and Control for HVAC."

P. BAS Interface: Factory-installed hardware and software to enable the BAS to monitor, control, and display unit status and alarms.

Retain "Hardwired Points" Subparagraph below if interface with the BAS is through hardwired points and minimal interface is required.

1. Hardwired Points:

a. Monitoring: On-off status, [common trouble alarm] <Insert monitoring point>.

b. Control: On-off operation, [space temperature set-point adjustment] [supply temperature set-point adjustment] [space humidity set-point adjustment] [space pressure set-point adjustment] <Insert control point>.

Delete "Hardwired Points" Subparagraph above and retain subparagraph below if extensive interface with the BAS is required and is beyond what hardwired points can provide. Requirement may exclude some manufacturers.

2. [ASHRAE 135 (BACnet)] [LonTalk] [Modbus] [Industry-accepted, open-protocol] <Insert type of interface> communication interface with the BAS shall enable the BAS operator to remotely control and monitor the unit from an operator workstation. Control features and monitoring points displayed locally at unit control panel shall be available through the BAS.

2.14 ACCESSORIES

A. Service Lights and Switch: Factory installed in [fan section] [fan and coil sections] [each accessible section] <Insert locations> with weatherproof cover. Factory wire lights to a single-point field connection.

B. Duplex Receptacle: Factory mounted in unit supply-fan section [and refrigeration section], with 20 amp 120 V GFI duplex receptacle and weatherproof cover.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Comply with manufacturer's rigging and installation instructions for unloading units and moving to final locations.

Retain "Curb Support" Paragraph below unless unit is installed on field-fabricated roof curbs or pilings specified in Section 077200 "Roof Accessories."

Retain "Curb Support" Paragraph below if roof curbs are furnished by unit manufacturer.

B. Curb Support: Install roof curb on roof structure according to "The NRCA Roofing Manual."

1. Install and secure units on curbs and coordinate roof penetrations and flashing with roof construction.

2. Coordinate size, installation, and structural capacity of roof curbs, equipment supports, and roof penetrations. These items are specified in Section 077200 "Roof Accessories."

3. Coordinate size, location, and installation of unit manufacturer's roof curbs and equipment supports with roof Installer.

Retain "Restrained Curb Support" Paragraph below for projects located in seismic areas.

C. Restrained Curb Support: Install restrained vibration isolation roof-curb rails on roof structure according to "The NRCA Roofing Manual."

D. Equipment Mounting:

Retain first subparagraph below to require equipment to be installed on cast-in-place concrete equipment bases.

1. Install air units on cast-in-place concrete equipment base(s). Comply with requirements for equipment bases and foundations specified in [Section 033000 "Cast-in-Place Concrete."] [Section 033053 "Miscellaneous Cast-in-Place Concrete."]

Retain one of two subparagraphs below. Retain first for projects in seismic areas; retain second for projects not in seismic areas. Indicate vibration isolation and seismic-control device type and minimum deflection in supported equipment schedule on Drawings.

2. Comply with requirements for vibration isolation and seismic control devices specified in Section 230548 "Vibration and Seismic Controls for HVAC."

3. Comply with requirements for vibration isolation devices specified in Section 230548.13 "Vibration Controls for HVAC."

Retain "Suspended Units" Paragraph below for suspended units. Retain options for projects in seismic areas.

E. Suspended Units: Suspend[ and brace] units from structural-steel support frame using threaded steel rods and spring hangers. Comply with requirements for vibration isolation devices specified in [Section 230548 "Vibration and Seismic Controls for HVAC."] [Section 230548.13 "Vibration Controls for HVAC."]

Retain first paragraph below if wall- and duct-mounted sensors are furnished by unit manufacturer for field installation.

F. Install wall- and duct-mounted sensors furnished by manufacturer for field installation. Install control wiring and make final connections to control devices and unit control panel.

Retain paragraph below for added sound and vibration isolation. Coordinate with structural engineer.

G. Install 3000-psi (20.7-MPa), compressive-strength (28-day) concrete base inside roof curb, [4 inches (100 mm)] <Insert dimension> thick. Concrete and reinforcement are specified with concrete.

Retain first paragraph below for units with gas-fired furnaces.

H. Comply with requirements for gas-fired furnace installation in NFPA 54, "National Fuel Gas Code."

I. Install separate devices furnished by manufacturer and not factory installed.

J. Install new filters at completion of equipment installation and before testing, adjusting, and balancing.

K. Install drain pipes from unit drain pans to sanitary drain.

Retain one of two "Drain Piping" subparagraphs below.

1. Drain Piping: Drawn-temper copper water tubing complying with ASTM B 88, Type L (ASTM B 88M, Type B), with soldered joints.

2. Drain Piping: Schedule 40 PVC pipe complying with ASTM D 1785, with solvent-welded fittings.

Retain first two subparagraphs below if required for LEED-NC, LEED-CI, or LEED-CS Credit IEQ 4.1 or if required by Project requirements or authorities having jurisdiction. VOC content limit is that for PVC welding compounds and adhesive primers for plastic.

a. PVC solvent cement shall have a VOC content of 510 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

b. Adhesive primer shall have a VOC content of 550 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

Retain first subparagraph below if required for LEED for Schools or if required by Project requirements or authorities having jurisdiction.

c. Solvent cement and adhesive primer shall comply with the testing and product requirements of the California Department of Health Services' "Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers."

3. Pipe Size: Same size as condensate drain pan connection.

3.2 CONNECTIONS

Coordinate installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Where installing piping adjacent to units, allow space for service and maintenance.

Retain "Gas Piping Connections" Paragraph below for units with a furnace.

B. Gas Piping Connections:

1. Comply with requirements in [Section 231123 "Facility Natural-Gas Piping."] [Section 231126 "Facility Liquefied-Petroleum Gas Piping."]

Retain option in first subparagraph below if pressure regulator is required and not provided by manufacturer.

2. Connect gas piping to furnace, full size of gas train inlet, and connect with union[, pressure regulator,] and shutoff valve with sufficient clearance for burner removal and service.

3. Install AGA-approved flexible connectors.

Retain "Hydronic Piping Connections" Paragraph below for units with hot-water coils.

C. Hydronic Piping Connections:

1. Comply with requirements in Section 232113 "Hydronic Piping" and Section 232116 "Hydronic Piping Specialties."Section 15179 "Hydronic Piping Specialties."

2. Install shutoff valve and union or flange on each supply connection and install balancing valve and union or flange on each return connection.

Coordinate duct installation requirements with schematics on Drawings and with requirements specified for duct systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

D. Duct Connections:

1. Comply with requirements in Section 233113 "Metal Ducts."

2. Drawings indicate the general arrangement of ducts.

3. Connect ducts to units with flexible duct connectors. Comply with requirements for flexible duct connectors in Section 233300 "Air Duct Accessories."

E. Electrical Connections: Comply with requirements for power wiring, switches, and motor controls in electrical Sections.

1. Install electrical devices furnished by unit manufacturer but not factory mounted.

3.3 STARTUP SERVICE

A. [Engage a factory-authorized service representative to perform] [Perform] startup service.

1. Complete installation and startup checks according to manufacturer's written instructions.

Retain first three subparagraphs below for units with a furnace.

2. Inspect units for visible damage to furnace combustion chamber.

3. Perform the following operations for both minimum and maximum firing and adjust burner for peak efficiency:

a. Measure gas pressure at manifold.

b. Measure combustion-air temperature at inlet to combustion chamber.

c. Measure flue-gas temperature at furnace discharge.

d. Perform flue-gas analysis. Measure and record flue-gas carbon dioxide and oxygen concentration.

e. Measure supply-air temperature and volume when burner is at maximum firing rate and when burner is off. Calculate useful heat to supply air.

4. Verify operation of remote panel including pilot-light operation and failure modes. Inspect the following:

a. High-limit heat exchanger.

b. Alarms.

Retain first three subparagraphs below with "Refrigeration System" Article.

5. Inspect units for visible damage to refrigerant compressor, condenser and evaporator coils, and fans.

6. Start refrigeration system when outdoor-air temperature is within normal operating limits and measure and record the following:

a. Cooling coil leaving-air, dry- and wet-bulb temperatures.

b. Cooling coil entering-air, dry- and wet-bulb temperatures.

c. Condenser coil entering-air dry-bulb temperature.

d. Condenser coil leaving-air dry-bulb temperature.

7. Simulate maximum cooling demand and inspect the following:

a. Compressor refrigerant suction and hot-gas pressures.

b. Short-circuiting of air through outside coil or from outside coil to outdoor-air intake.

8. Inspect casing insulation for integrity, moisture content, and adhesion.

9. Verify that clearances have been provided for servicing.

10. Verify that controls are connected and operable.

11. Verify that filters are installed.

12. Clean coils and inspect for construction debris.

Retain first three subparagraphs below for units with furnace.

13. Clean furnace flue and inspect for construction debris.

14. Inspect operation of power vents.

15. Purge gas line.

Retain first subparagraph below for units with restrained vibration isolation roof-curb rails.

16. Inspect and adjust vibration isolators and seismic restraints.

17. Verify bearing lubrication.

18. Clean fans and inspect fan-wheel rotation for movement in correct direction without vibration and binding.

19. Adjust fan belts to proper alignment and tension.

20. Start unit.

21. Inspect and record performance of interlocks and protective devices including response to smoke detectors by fan controls and fire alarm.

22. Operate unit for run-in period.

23. Calibrate controls.

24. Adjust and inspect high-temperature limits.

Retain first subparagraph below for units designed to operate, at least part-time, with less than 100 percent outdoor air.

25. Inspect outdoor-air dampers for proper stroke[ and interlock with return-air dampers].

26. Verify operational sequence of controls.

27. Measure and record the following airflows. Plot fan volumes on fan curve.

a. Supply-air volume.

Retain first subparagraph below for units designed to operate, at least part-time, with less than 100 percent outdoor air.

b. Return-air flow.

c. Outdoor-air flow.

B. After startup, change filters, verify bearing lubrication, and adjust belt tension.

C. Remove and replace components that do not properly operate and repeat startup procedures as specified above.

D. Prepare written report of the results of startup services.

3.4 ADJUSTING

A. Adjust initial temperature and humidity set points.

B. Set field-adjustable switches and circuit-breaker trip ranges as indicated.

C. Occupancy Adjustments: When requested within [12] <Insert number> months from date of Substantial Completion, provide on-site assistance in adjusting system to suit actual occupied conditions. Provide up to [two] <Insert number> visits to Project during other-than-normal occupancy hours for this purpose.

END OF SECTION 237433

	DEDICATED OUTDOOR-AIR UNITS
	237433 - 1



