Copyright 2012 AIA
MasterSpec Professional
03/12

Copyright 2012 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 260536 - CABLE TRAYS FOR ELECTRICAL SYSTEMS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Ladder cable trays.

2. Single-rail cable trays.

3. Trough cable trays.

4. Fiberglass cable trays.

B. Related Requirements:

Retain subparagraph below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

1. Section 270536 "Cable Trays for Communications Systems" for cable trays and accessories serving communications systems.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product.

B. Shop Drawings: For each type of cable tray.

Retain "Delegated-Design Submittal" Paragraph below if design services have been delegated to Contractor.

C. Delegated-Design Submittal: For seismic restraints.

1. Seismic-Restraint Details: Signed and sealed by a qualified professional engineer, licensed in the state where Project is located, who is responsible for their preparation.

2. Design Calculations: Calculate requirements for selecting seismic restraints.

3. Detail fabrication, including anchorages and attachments to structure and to supported cable trays.

1.3 INFORMATIONAL SUBMITTALS

Retain "Seismic Qualification Certificates" Paragraph below if required by seismic criteria applicable to Project. Coordinate with Section 260548.16 "Seismic Controls for Electrical Systems." See ASCE/SEI 7 for certification requirements for equipment and components.

A. Seismic Qualification Certificates: For cable trays, accessories, and components, from manufacturer.

B. Field quality-control reports.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

2.1 PERFORMANCE REQUIREMENTS

Retain "Delegated Design" Paragraph below if Contractor is required to assume responsibility for design.

A. Delegated Design: Engage a qualified professional engineer, as defined in Section 014000 "Quality Requirements," to design cable tray supports and seismic bracing.

Retain "Seismic Performance" Paragraph below with "Seismic Qualification Certificates" Paragraph in "Informational Submittals" Article for projects requiring seismic design. Delete paragraph if performance requirements are indicated on Drawings. Model building codes and ASCE/SEI 7 establish criteria for buildings subject to earthquake motions. Coordinate requirements with structural engineer.

B. Seismic Performance: Cable trays and supports shall withstand the effects of earthquake motions determined according to [ASCE/SEI 7] <Insert requirement>.

For life-safety components required to function after an earthquake (such as fire-sprinkler systems, components that contain hazardous content, and storage racks in structures open to the public), the Component Importance Factor is 1.5. For other components, the Component Importance Factor is 1.0 unless the structure is in Seismic Use Group III and component is necessary for continued operation of facility or failure of component could impair continued operation of facility, in which case the Component Importance Factor is 1.5.

1. Component Importance Factor: [1.5] [1.0].

See ASCE/SEI 7, Coefficients for Architectural Component Table and Seismic Coefficients for Mechanical and Electrical Components Table for requirements to be inserted in subparagraph below.

2. <Insert requirements for Component Amplification Factor and Component Response Modification Factor>.

2.2 GENERAL REQUIREMENTS FOR CABLE TRAYS

If cable trays are identified for use via listing, then follow listing requirements. This may require that all interconnected cable trays be from single manufacturer. Some tray types may not be capable of being interconnected.

A. Cable Trays and Accessories: Identified as defined in NFPA 70 and marked for intended location, application, and grounding.

If using multiple types, sizes, or ratings of cable trays on a project, consider adding a table to Drawings.

B. Sizes and Configurations: See the Cable Tray Schedule on Drawings for specific requirements for types, materials, sizes, and configurations.

See "Load/Span Classification System" Article in the Evaluations.

C. Structural Performance: See articles on individual cable tray types for specific values for uniform load distribution, concentrated load, and load and safety factor parameters.

2.3 LADDER CABLE TRAYS

A. Description:

1. Configuration: Two I-beam side rails with transverse rungs welded to side rails.

2. Rung Spacing: [6 inches (150 mm)] [9 inches (225 mm)] [12 inches (300 mm)] [18 inches (450 mm)] o.c.

3. Radius-Fitting Rung Spacing: 9 inches (225 mm) at center of tray's width.

4. Minimum Cable-Bearing Surface for Rungs: 7/8-inch (22-mm) width with radius edges.

5. No portion of the rungs shall protrude below the bottom plane of side rails.

6. Structural Performance of Each Rung: Capable of supporting a maximum cable load, with a safety factor of 1.5, plus a200-lb (90-kg) concentrated load, when tested according to NEMA VE 1.

7. Minimum Usable Load Depth: [3 inches (75 mm)] [4 inches (100 mm)] [5 inches (125 mm)] [6 inches (150 mm)].

8. Straight Section Lengths: [10 feet (3 m)] [12 feet (3.6 m)] [20 feet (6 m)] [24 feet (7.4 m)] except where shorter lengths are required to facilitate tray assembly.

9. Width: [6 inches (150 mm)] [9 inches (225 mm)] [12 inches (300 mm)] [18 inches (450 mm)] [24 inches (600 mm)] [30 inches (750 mm)] [36 inches (900 mm)] unless otherwise indicated on Drawings.

10. Fitting Minimum Radius: [12 inches (300 mm)] [24 inches (600 mm)] [36 inches (900 mm)] [48 inches (1200 mm)].

The maximum uniform load and the support span are indicated by the cable tray class.

11. Class Designation: Comply with NEMA VE 1, [Class 12B] [Class 12C] [Class 20B] [Class 20C] <Insert designation>.

12. Splicing Assemblies: Bolted type using serrated flange locknuts.

13. Hardware and Fasteners: [ASTM F 593 and ASTM F 594 stainless steel, Type 316] [Steel, zinc plated according to ASTM B 633].

14. Splice Plate Capacity: Splices located within support span shall not diminish rated loading capacity of cable tray.

2.4 SINGLE-RAIL CABLE TRAYS

A. Description:

1. Configuration: Center rail with extruded-aluminum rungs arranged symmetrically about the center rail.

2. Construction: Aluminum rungs mechanically connected to aluminum center rail in at least two places, with ends finished to protect installers and cables.

3. Rung Spacing: [6 inches (150 mm)] [9 inches (225 mm)] [12 inches (300 mm)] o.c.

4. Radius-Fitting Rung Spacing: 9 inches (225 mm) at center of tray's width.

5. Straight Section Lengths: [10 feet (3 m)] [12 feet (3.6 m)] except where shorter lengths are required to facilitate tray assembly.

6. Width: [6 inches (150 mm)] [9 inches (225 mm)] [12 inches (300 mm)] [18 inches (450 mm)] [24 inches (600 mm)] unless otherwise indicated on Drawings.

7. Support Point: Splice fittings shall be hanger support point.

8. Support Spacing: Support each section at midpoint. Support wall-mounted sections a maximum of one-sixth of the section length from each end.

9. Loading Depth: [3 inches (75 mm)] [4 inches (100 mm)] [6 inches (150 mm)].

10. Maximum Loads: [25 lb/ft. (37 kg/m)] [50 lb/ft. (74 kg/m)].

Maintaining cable tray rungs within six degrees of horizontal is for aesthetic reasons. The tray looks uneven when tilted more than this. Support variations are available to allow varying levels of unbalanced loads while not exceeding the maximum tilt.

11. Unbalanced Loads: Maintain cable tray rungs within six degrees of horizontal under all loading conditions.
12. Splicing Assemblies: Bolted type using serrated flange locknuts.

13. Splicing Assembly Capacity: Splices located within support span shall not diminish rated loading capacity of cable tray.

14. Hardware and Fasteners: [ASTM F 593 and ASTM F 594 stainless steel, Type 316] [Steel, zinc plated according to ASTM B 633].

15. Splices and Connectors: Protect cables from edges of center rail and do not intrude into cable fill area.

2.5 TROUGH CABLE TRAYS

A. Description:

1. Configuration: Two longitudinal members (side rails) with a solid sheet over rungs exposed on the interior of the trough, or corrugated sheet with both edges welded to the side rails.

2. Rung Spacing: Rungs or corrugations shall be spaced a maximum of 6 inches (150 mm) o.c. and have a minimum flat bearing surface of 2 inches (50 mm).

3. Radius-Fitting Rung Spacing: 9 inches (225 mm) at center of tray's width.

4. Structural Performance: Capable of supporting a maximum cable load, with a safety factor of 1.5, plus a200-lb (90-kg) concentrated load, when tested according to NEMA VE 1.

5. Minimum Usable Load Depth: [3 inches (75 mm)] [4 inches (100 mm)] [5 inches (125 mm)] [6 inches (150 mm)].

6. Straight Section Lengths: [10 feet (3 m)] [12 feet (3.6 m)] [20 feet (6 m)] [24 feet (7.4 m)] except where shorter lengths are required to facilitate tray assembly.

7. Width: [6 inches (150 mm)] [9 inches (225 mm)] [12 inches (300 mm)] [18 inches (450 mm)] [24 inches (600 mm)] [30 inches (750 mm)] [36 inches (900 mm)] unless otherwise indicated on Drawings.

8. Fitting Minimum Radius: [12 inches (300 mm)] [24 inches (600 mm)] [36 inches (900 mm)] [48 inches (1200 mm)].

The maximum uniform load and the support span are indicated by the cable tray class.

9. Class Designation: Comply with NEMA VE 1, [Class 12B] [Class 12C] [Class 20B] [Class 20C] <Insert designation>.

10. Splicing Assemblies: Bolted type using serrated flange locknuts.

11. Splicing Assembly Capacity: Splices located within support span shall not diminish rated loading capacity of cable tray.

12. Hardware and Fasteners: [ASTM F 593 and ASTM F 594 stainless steel, Type 316] [Steel, zinc plated according to ASTM B 633].

2.6 FIBERGLASS CABLE TRAYS

A. Description:

1. Configuration: Two longitudinal members with rounded edges and smooth surfaces, complying with NEMA FG 1.

2. Materials: Straight section structural elements; side rails, rungs and splice plates shall be pultruded from glass-fiber-reinforced [polyester] [vinyl ester] resin, complying with NEMA FG 1 and UL 568.

3. Fasteners: Fiberglass-encapsulated, ASTM F 593 and ASTM F 594 stainless steel, Type 316. Design fasteners so that no metal is visible when fully assembled and tightened. Fastener encapsulation shall not be damaged when torqued to manufacturer's recommended value.

4. Minimum Usable Load Depth: [1 inch (25 mm)] [2 inches (50 mm)] [3 inches (75 mm)] [5 inches (125 mm)] [7 inches (175 mm)] according to NEMA FG 1.

5. Straight Section Lengths: [10 feet (3 m)] [20 feet (6 m)].

6. Width: [6 inches (150 mm)] [9 inches (225 mm)] [12 inches (300 mm)] [18 inches (450 mm)] [24 inches (600 mm)] [30 inches (750 mm)] [36 inches (900 mm)] unless otherwise indicated on Drawings.

The maximum uniform load and the support span are indicated by the cable tray class.

7. Class Designation: Comply with NEMA VE 1, [Class 12B] [Class 12C] [Class 20B] [Class 20C] <Insert designation>.

See "Load/Span Classification System" Article in the Evaluations for discussion of temperature effects.

8. Temperature Rating: Reduce the load rating of tray exposed to temperatures above 75 deg F (24 deg C)according to Table 4-3, "Working Loads," in NEMA FG 1.

9. Fitting Minimum Radius: [12 inches (300 mm)] [24 inches (600 mm)].

10. Splicing Assemblies: Minimum four nuts and bolts per plate. Splice plates shall be furnished with straight sections and fittings.

11. Splicing Assembly Capacity: Splices located within support span shall not diminish rated loading capacity of cable tray.

2.7 MATERIALS AND FINISHES

Retain one or more of "Steel," "Aluminum," and "Stainless Steel" paragraphs below. If using more than one type of cable tray material for Project, consider using a schedule to detail the specific requirements in each area. See "Cable Tray Materials" Article in the Evaluations.

A. Steel:

ASTM A 1011/A 1011M is for 14 gage and thicker; ASTM A 1008/A 1008M is for 16 gage and thinner. Both have structural-steel (SS) and high-strength, low-alloy-steel (HSLAS) designations.

1. Straight Section and Fitting Side Rails and Rungs: Steel complies with the minimum mechanical properties of [ASTM A 1011/A 1011M, SS, Grade 33] [ASTM A 1008/A 1008M, Grade 33, Type 2].

2. Steel Tray Splice Plates: ASTM A 1011/A 1011M, HSLAS, Grade 50, Class 1.

3. Fasteners: Steel complies with the minimum mechanical properties of ASTM A 510/A 510M, Grade 1008.

Retain one of six "Finish" subparagraphs below or insert a different finish.

4. Finish: Mill galvanized before fabrication.

Retain one option in "Hardware" Subparagraph below.

a. Hardware: [Galvanized, ASTM B 633] [Chromium-zinc plated, ASTM F 1136].

5. Finish: Electrogalvanized before fabrication.

6. Finish: Hot-dip galvanized after fabrication.

Retain one option in "Hardware" Subparagraph below.

a. Hardware: [Chromium-zinc plated, ASTM F 1136] [Stainless steel, Type 316, ASTM F 593 and ASTM F 594].

7. Finish: [Epoxy-resin] [Powder-coat enamel] paint.

Retain one option in "Hardware" Subparagraph below.

a. Hardware: [Chromium-zinc plated. ASTM F 1136] [Stainless steel, Type 316, ASTM F 593 and ASTM F 594].

8. Finish: Factory-standard primer, ready for field painting, with chromium-zinc-plated hardware according to ASTM F 1136.

9. Finish: Black oxide finish for support accessories and miscellaneous hardware according to ASTM D 769.

B. Aluminum:

1. Materials: Alloy 6063-T6 according to ANSI H35.1/H 35.1M for extruded components, and [Alloy 5052-H32] [or] [Alloy 6061-T6] according to ANSI H35.1/H 35.1M for fabricated parts.

2. Hardware: [Chromium-zinc-plated steel, ASTM F 1136] [Stainless steel, Type 316, ASTM F 593 and ASTM F 594].

3. Hardware for Aluminum Cable Tray Used Outdoors: Stainless steel, Type 316, ASTM F 593 and ASTM F 594.

C. Stainless Steel:

1. Materials: Low-carbon, passivated, stainless steel, [Type 304L] [or] [Type 316L], ASTM F 593 and ASTM F 594.

2. Hardware for Stainless-Steel Cable Tray Used Outdoors: Stainless steel, Type 316, ASTM F 593 and ASTM F 594.

2.8 CABLE TRAY ACCESSORIES

A. Fittings: Tees, crosses, risers, elbows, and other fittings as indicated, of same materials and finishes as cable tray.

If more than one cable tray cover type is required, delete "Covers" Paragraph below and indicate type on Drawings or in a schedule. Retain paragraph if cable tray covers are required. See "Cable Tray Covers" Article in the Evaluations.

B. Covers: [Solid] [Louvered] [Ventilated-hat] [2-in-3 pitch] type made of same materials and with same finishes as cable tray.

Indicate required locations for barrier strips on Drawings.

C. Barrier Strips: Same materials and finishes as for cable tray.

D. Cable tray supports and connectors, including bonding jumpers, as recommended by cable tray manufacturer.

2.9 WARNING SIGNS

Insert different lettering size in "Lettering" Paragraph below to suit 25-foot (7.6-m) viewing distance.

A. Lettering: [1-1/2-inch- (40-mm-)] <Insert dimension> high, black letters on yellow background with legend "Warning! Not To Be Used as Walkway, Ladder, or Support for Ladders or Personnel."

B. Comply with requirements for fasteners in Section 260553 "Identification for Electrical Systems."

2.10 SOURCE QUALITY CONTROL

A. Testing: Test and inspect cable trays according to [NEMA FG 1] [NEMA VE 1].

PART 3 -  EXECUTION

3.1 CABLE TRAY INSTALLATION

NEMA FG 1 applies to fiberglass cable trays only. NEMA VE 2 applies to all metallic cable trays.

A. Install cable trays according to [NEMA FG 1] [NEMA VE 2].

B. Install cable trays as a complete system, including fasteners, hold-down clips, support systems, barrier strips, adjustable horizontal and vertical splice plates, elbows, reducers, tees, crosses, cable dropouts, adapters, covers, and bonding.

C. Fasten cable tray supports to building structure[ and install seismic restraints].

Retain first paragraph below if deleting "Delegated Design" Paragraph in "Performance Requirements" Article. Delete below if retaining "Delegated Design" Paragraph.

D. Design fasteners and supports to carry cable tray, the cables, and a concentrated load of 200 lb (90 kg). Comply with requirements in Section 260529 "Hangers and Supports for Electrical Systems."[ Comply with seismic-restraint details according to Section 260548.16 "Seismic Controls for Electrical Systems."]

E. Install center-hung supports for single-rail trays designed for 60 versus 40 percent eccentric loading condition, with a safety factor of 3.

Retain first paragraph below if cable trays connect to equipment.

F. Make connections to equipment with flanged fittings fastened to cable trays and to equipment. Support cable trays independent of fittings. Do not carry weight of cable trays on equipment enclosure.

Retain first paragraph below if expansion fittings are required.

G. Install expansion connectors where cable trays cross building expansion joints and in cable tray runs that exceed dimensions recommended in [NEMA FG 1] [NEMA VE 2]. Space connectors and set gaps according to applicable standard.

H. Seal penetrations through fire and smoke barriers. Comply with requirements in Section 078413 "Penetration Firestopping."

If cable trays are sized for future cables, specify provisions for penetrations with sleeves through fire-rated partitions or use "repairable" firestop-sealing material. Include this Section's specific firestopping requirements in a schedule developed in Section 078413 "Penetration Firestopping."

I. Install capped metal sleeves for future cables through firestop-sealed cable tray penetrations of fire and smoke barriers.

Retain first paragraph below if systems are mixed in a single cable tray.

J. Install barriers to separate cables of different systems, such as power, communications, and data processing; or of different insulation levels, such as 600, 5000, and 15 000 V.

See "Cable Tray Covers" Article in the Evaluations.

K. Install permanent covers, if used, after installing cable. Install cover clamps according to NEMA VE 2.

L. Install warning signs in visible locations on or near cable trays after cable tray installation.

3.2 CABLE TRAY GROUNDING

A. Ground cable trays according to NFPA 70 unless additional grounding is specified. Comply with requirements in Section 260526 "Grounding and Bonding for Electrical Systems."

B. Cable trays with electrical power conductors shall be bonded together with splice plates listed for grounding purposes or with listed bonding jumpers.

Verify that cable tray system is specified for grounding and bonding the largest power conductor in the tray. If system is not specified, retain first paragraph below and revise to suit Project.

C. Cable trays with single-conductor power conductors shall be bonded together with a grounding conductor run in the tray along with the power conductors and bonded to the tray at 72-inch (1800-mm) intervals. The grounding conductor shall be sized according to NFPA 70, Article 250.122, "Size of Equipment Grounding Conductors," and Article 392, "Cable Trays."

D. Bond cable trays to power source for cables contained within with bonding conductors sized according to NFPA 70, Article 250.122, "Size of Equipment Grounding Conductors."

3.3 CABLE INSTALLATION

A. Install cables only when each cable tray run has been completed and inspected.

Fastening cables on horizontal runs is beyond the requirements of NFPA 70 in most cases. See Evaluations.

B. Fasten cables on horizontal runs with cable clamps or cable ties according to NEMA VE 2. Tighten clamps only enough to secure the cable, without indenting the cable jacket.

C. Fasten cables on vertical runs to cable trays every 18 inches (450 mm).

Length of unsupported cable is dependent on the cable diameter. See "Cable Installations" Article in Evaluations.

D. Fasten and support cables that pass from one cable tray to another or drop from cable trays to equipment enclosures. Fasten cables to the cable tray at the point of exit and support cables independent of the enclosure. The cable length between cable trays or between cable tray and enclosure shall be no more than 72 inches (1800 mm).

E. Tie MI cables down every 36 inches (900 mm) where required to provide a 2-hour fire rating and every 72 inches (1800 mm) elsewhere.

F. In existing construction, remove inactive or dead cables from cable trays.

3.4 CONNECTIONS

A. Connect raceways to cable trays according to requirements in NEMA VE 2 and NEMA FG 1.

3.5 FIELD QUALITY CONTROL

Retain "Perform the following tests and inspections" Paragraph below to require Contractor to perform tests and inspections.

A. Perform the following tests and inspections[ with the assistance of a factory-authorized service representative]:

1. After installing cable trays and after electrical circuitry has been energized, survey for compliance with requirements.

2. Visually inspect cable insulation for damage. Correct sharp corners, protuberances in cable trays, vibrations, and thermal expansion and contraction conditions, which may cause or have caused damage.

3. Verify that the number, size, and voltage of cables in cable trays do not exceed that permitted by NFPA 70. Verify that communications or data-processing circuits are separated from power circuits by barriers or are installed in separate cable trays.

4. Verify that there are no intruding items such as pipes, hangers, or other equipment in the cable tray.

5. Remove dust deposits, industrial process materials, trash of any description, and any blockage of tray ventilation.

6. Visually inspect each cable tray joint and each ground connection for mechanical continuity. Check bolted connections between sections for corrosion. Clean and retorque in suspect areas.

7. Check for missing, incorrect, or damaged bolts, bolt heads, or nuts. When found, replace with specified hardware.

8. Perform visual and mechanical checks for adequacy of cable tray grounding; verify that all takeoff raceways are bonded to cable trays. Test entire cable tray system for continuity. Maximum allowable resistance is 1 ohm.

B. Prepare test and inspection reports.

3.6 PROTECTION

A. Protect installed cable trays and cables.

END OF SECTION 260536

	CABLE TRAYS FOR ELECTRICAL SYSTEMS
	260536 - 1



