Copyright 2012 AIA
MasterSpec Professional
03/12

Copyright 2012 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 260943.23 - RELAY-BASED LIGHTING CONTROLS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

If applying for LEED certification, LEED-NC Prerequisite EA 2 requires compliance with ASHRAE/IESNA 90.1. ASHRAE/IESNA 90.1, Section 9, "Lighting," sets minimum interior and exterior lighting power densities and minimum requirements for lighting controls.

Additional lighting controls can be used to meet the requirements of LEED-NC Credit EQ 6.1 if individual lighting controls are provided for a minimum of 90 percent of the building occupants and lighting system controls are provided for all shared multi-occupant spaces to enable adjustment to meet group needs. Indicate locations of lighting controls on Drawings.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section includes lighting control panels using mechanically held relays for switching.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product.

B. Shop Drawings: For each relay panel and related equipment.

1. Include dimensioned plans, elevations, sections, and details. Show tabulations of installed devices, equipment features, and ratings.

2. Detail enclosure types and details for types other than NEMA 250, Type 1.

3. Detail wiring partition configuration, current, and voltage ratings.

4. Short-circuit current rating of relays.

5. Include diagrams for power, signal, and control wiring.

1.3 INFORMATIONAL SUBMITTALS

Retain "Coordination Drawings" Paragraph below if lighting controls are connected to devices or systems specified in other Sections.

A. Coordination Drawings: Submit evidence that lighting controls are compatible with connected monitoring and control devices and systems specified in other Sections.

1. Show interconnecting signal and control wiring, and interface devices that prove compatibility of inputs and outputs.

B. Field quality-control reports.

C. Sample warranty.

1.4 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

1.5 DELIVERY, STORAGE, AND HANDLING

A. Handle and prepare panels for installation according to NECA 407.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

2.1 SYSTEM DESCRIPTION

A. Input signal from field-mounted manual switches, or digital signal sources, shall open or close one or more lighting control relays in the lighting control panels. Any combination of inputs shall be programmable to any number of control relays.

B. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

C. Comply with UL 916.

2.2 PERFORMANCE REQUIREMENTS

Delete "Seismic Performance" Paragraph below if performance requirements are indicated on Drawings. Model building codes and ASCE/SEI 7 establish criteria for buildings subject to earthquake motions. Coordinate requirements with structural engineer.

A. Seismic Performance: Lighting control panels shall withstand the effects of earthquake motions determined according to [ASCE/SEI 7] <Insert requirement>.

Retain first subparagraph below to define the term "withstand" as it applies to this Project. Definition varies with type of building and occupancy and is critical to valid certification. Option is used for essential facilities where equipment must operate immediately after an earthquake.

1. The term "withstand" means "the unit will remain in place without separation of any parts when subjected to the seismic forces specified[ and the unit will be fully operational after the seismic event]."

For life-safety components required to function after an earthquake (such as fire-sprinkler systems, components that contain hazardous content, and storage racks in structures open to the public), the Component Importance Factor is 1.5. For other components, the Component Importance Factor is 1.0 unless the structure is in Seismic Use Group III and component is necessary for continued operation of facility or failure of component could impair continued operation of facility, in which case the Component Importance Factor is 1.5.

2. Component Importance Factor: [1.5] [1.0].

See ASCE/SEI 7, Coefficients for Architectural Component Table and Seismic Coefficients for Mechanical and Electrical Components Table for requirements to be inserted in subparagraph below.

3. <Insert requirements for Component Amplification Factor and Component Response Modification Factor>.

2.3 LIGHTING CONTROL RELAY PANELS

Retain "Products" Paragraph and list of manufacturers and products below to require specific products or a comparable product from other manufacturers.

A. Products: Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

1. Acuity Brands, Inc., Lighting Control & Design, Inc.; GR2400.

2. General Electric Company, GE Consumer & Industrial - Electrical Distribution; LVRC.

3. Leviton Mfg. Company Inc.; Z-Max Plus.

4. Lightolier Controls, a Philips Group brand; Lyteswitch.

5. Siemens Energy & Automation, Inc.; LCP3000EZ.

6. Touch-Plate Technologies; Zone Z.

7. WattStopper, a Legrand Group brand; Lighting Integrator.

8. <Insert manufacturer's name; product name or designation>.

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Acuity Brands, Inc.; Lighting Control & Design, Inc.

2. General Electric Company; GE Consumer & Industrial - Electrical Distribution.

3. Leviton Mfg. Company Inc.

4. Lightolier Controls; a Philips Group brand.

5. Siemens Energy & Automation, Inc.

6. Touch-Plate Technologies.

7. WattStopper; a Legrand Group brand.

8. <Insert manufacturer's name>.

C. Description: Standalone lighting control panel using mechanically latched relays to control lighting and appliances.

D. Lighting Control Panel:

1. A single enclosure with incoming lighting branch circuits, control circuits, switching relays, and on-board timing and control unit.

2. A vertical barrier separating branch circuits from control wiring.

E. Control Unit: Contain the power supply and electronic control for operating and monitoring individual relays.

1. Timing Unit:

a. 365-day calendar, astronomical clock, and automatic adjustments for daylight savings and leap year.

b. Clock configurable for 12-hour (A.M./P.M.) or 24-hour format.

c. [Four] <Insert number> independent schedules, each having [24] <Insert number> time periods.

d. Schedule periods settable to the minute.

e. Day-of-week, day-of-month, day-of-year with one-time or repeating capability.

f. [10] <Insert number> special date periods.

In "Sequencing Control with Override" Subparagraph below, two control units are available from some manufacturers.

2. Sequencing Control with Override:

a. Automatic sequenced on and off switching of selected relays at times set at the timing unit, allowing timed overrides from external switches.

b. Sequencing control shall operate relays one at a time, completing the operation of all connected relays in not more than 10 seconds.

c. Override control shall allow any relay connected to it to be switched on or off by a field-deployed manual switch or by an automatic switch, such as an occupancy sensor.

d. Override control "blink warning" shall warn occupants approximately [five minutes] <Insert time> before actuating the off sequence.

3. Nonvolatile memory shall retain all setup configurations. After a power failure, the controller shall automatically reboot and return to normal system operation, including accurate time of day and date.

Retain one of two "Relays" paragraphs below. Not all listed manufacturers can comply with requirements when retaining second paragraph. Two-pole relays are available from some manufacturers.

F. Relays: Electrically operated, mechanically held single-pole switch, rated at 20 A at 277 V. Short-circuit current rating shall be not less than 5 kA. Control shall be three-wire, 24-V ac.

G. Relays: Electrically operated, mechanically held single-pole switch, rated at 20 A at 120-V tungsten, 30 A at 277-V ballast, 1.5 hp at 120 V, and 3 hp at 277 V. Short-circuit current rating shall be not less than 14 kA. Control shall be three-wire, 24-V ac.

H. Power Supply: NFPA 70, Class 2, sized for connected equipment, plus 20 percent spare capacity. Powered from a dedicated branch circuit of the panelboard that supplies power to the line side of the relays, sized to provide control power for the local panel-mounted relays, bus system, low-voltage inputs, field-installed occupancy sensors, and photo sensors.

Alternatives to "Operator Interface" Paragraph below are available from some manufacturers. Alternatives include hand-held portable PCs, personal digital assistants, and mobile telephones.

I. Operator Interface:

1. Integral alphanumeric keypad and digital display, and intuitive drop-down menus to assist in programming.

2. Log and display relay on-time.

3. Connect relays to one or more time and sequencing schemes.

2.4 MANUAL SWITCHES AND PLATES

Coordinate use of manual switches in this article with required control and override functions, with occupancy sensor applications where used, and with switch and wall-plate finish specified in Section 262726 "Wiring Devices."

A. Push-Button Switches: Modular, momentary contact, three wire, for operating one or more relays and to override automatic controls.

1. Match color and style specified in Section 262726 "Wiring Devices."

Retain both subparagraphs below if required.

2. Integral green [LED] [neon] pilot light to indicate when circuit is on.

3. Internal white [LED] [neon] locator light to illuminate when circuit is off.

B. Wall Plates: Single and multigang plates as specified in Section 262726 "Wiring Devices."

C. Legend: Engraved or permanently silk-screened on wall plate where indicated. Use designations indicated on Drawings.

2.5 FIELD-MOUNTED SIGNAL SOURCES

A. Daylight Harvesting Switching Controls: Comply with Section 260923 "Lighting Control Devices." Control power may be taken from the lighting control panel, and signal shall be compatible with the relays.

B. Indoor Occupancy Sensors[ and Extreme-Temperature Occupancy Sensors]: Comply with Section 260923 "Lighting Control Devices." Control power may be taken from the lighting control panel, and signal shall be compatible with the relays.

2.6 CONDUCTORS AND CABLES

A. Power Wiring to Supply Side of Class 2 Power Source: Not smaller than No. 12 AWG, complying with Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

B. Classes 2 and 3 Control Cables: Multiconductor cable with copper conductors not smaller than [No. 18] [No. 22] [No. 24] AWG, complying with Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

C. Class 1 Control Cables: Multiconductor cable with copper conductors not smaller than [No. 14] [No. 16] [No. 18] AWG, complying with Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

PART 3 -  EXECUTION

3.1 EXAMINATION

A. Receive, inspect, handle, and store panels according to NECA 407.

B. Examine panels before installation. Reject panels that are damaged or rusted or have been subjected to water saturation.

C. Examine elements and surfaces to receive panels for compliance with installation tolerances and other conditions affecting performance of the Work.

D. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 WIRING INSTALLATION

A. Comply with NECA 1.

Retain one of two "Wiring Method" paragraphs below and coordinate with Drawings. Delete both if wiring methods for system are indicated on Drawings.

B. Wiring Method: Install cables in raceways and cable trays except within consoles, cabinets, desks, and counters[ and except in accessible ceiling spaces and in gypsum board partitions where unenclosed wiring method may be used]. Conceal raceway and cables except in unfinished spaces.

Retain first subparagraph below if retaining option in "Wiring Method" Paragraph above.

1. Install plenum cable in environmental air spaces, including plenum ceilings.

2. Comply with requirements for cable trays specified in Section 260536 "Cable Trays for Electrical Systems."

3. Comply with requirements for raceways and boxes specified in Section 260533 "Raceways and Boxes for Electrical Systems."

C. Wiring Method: Conceal conductors and cables in accessible ceilings, walls, and floors where possible.

D. Wiring within Enclosures: Bundle, lace, and train conductors to terminal points with no excess and without exceeding manufacturer's limitations on bending radii. Install lacing bars and distribution spools.

3.3 PANEL INSTALLATION

A. Comply with NECA 1.

B. Install panels and accessories according to NECA 407.

Retain first paragraph below if seismic controls are required for Project. Coordinate with Drawings.

C. Comply with mounting and anchoring requirements specified in Section 260548 "Vibration and Seismic Controls for Electrical Systems."

Ensure that, whatever height is retained for top of trim in first paragraph below, the operating handle of topmost switch or circuit breaker, in on position, is not higher than 79 inches (2000 mm)above finished floor or grade.
D. Mount top of trim [90 inches (2286 mm)] <Insert dimension> above finished floor unless otherwise indicated.

E. Mount panel cabinet plumb and rigid without distortion of box.

F. Install filler plates in unused spaces.

3.4 IDENTIFICATION

A. Identify system components, wiring, cabling, and terminals. Comply with requirements for identification specified in Section 260553 "Identification for Electrical Systems."

B. Identify field-installed conductors, interconnecting wiring, and components; provide warning signs complying with Section 260553 "Identification for Electrical Systems."

C. Create a directory to indicate loads served by each relay; incorporate Owner's final room designations. Obtain approval before installing. Use a PC or typewriter to create directory; handwritten directories are unacceptable.

D. Lighting Control Panel Nameplates: Label each panel with a nameplate complying with requirements for identification specified in Section 260553 "Identification for Electrical Systems."

3.5 FIELD QUALITY CONTROL

Retain "Manufacturer's Field Service" Paragraph below to require a factory-authorized service representative to perform tests and inspections.

A. Manufacturer's Field Service: Engage a factory-authorized service representative to test and inspect components, assemblies, and equipment installations, including connections.

Retain "Perform the following tests and inspections" Paragraph below to require Contractor to perform tests and inspections.

B. Perform the following tests and inspections[ with the assistance of a factory-authorized service representative]:

1. Perform each visual and mechanical inspection and electrical test stated in NETA Acceptance Testing Specification. Certify compliance with test parameters.

2. Correct malfunctioning units on-site, where possible, and retest to demonstrate compliance; otherwise, replace with new units and retest.

C. Acceptance Testing Preparation:

1. Test continuity of each circuit.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

D. Lighting control panel will be considered defective if it does not pass tests and inspections.

Retain paragraph below if tests and inspections are performed by Contractor or manufacturer's field-service representative engaged by Contractor.

E. Prepare test and inspection reports, including a certified report that identifies lighting control panels and describes scanning results. Include notation of deficiencies detected, remedial action taken, and observations made after remedial action.

3.6 STARTUP SERVICE

A. [Engage a factory-authorized service representative to perform] [Perform] startup service.

1. Complete installation and startup checks according to manufacturer's written instructions.

2. Confirm correct communications wiring, initiate communications between panels, and program the lighting control system according to approved configuration schedules, time-of-day schedules, and input override assignments.

3. <Insert startup steps if any>.

3.7 ADJUSTING

A. Occupancy Adjustments: When requested within [12] <Insert number> months from date of Substantial Completion, provide on-site assistance in adjusting system to suit actual occupied conditions. Provide up to [two] <Insert number> visits to Project during other-than-normal occupancy hours for this purpose.

3.8 DEMONSTRATION

A. [Engage a factory-authorized service representative to train] [Train] Owner's maintenance personnel to adjust, operate, and maintain the control unit and operator interface.

END OF SECTION 260943.23

	RELAY-BASED LIGHTING CONTROLS
	260943.23 - 1



