Copyright 2012 AIA
MasterSpec Professional
03/12

Copyright 2012 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 262413 - SWITCHBOARDS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Service and distribution switchboards rated 600 V and less.

2. Transient voltage suppression devices.

3. Disconnecting and overcurrent protective devices.

4. Instrumentation.

5. Control power.

6. Accessory components and features.

7. Identification.

1.2 PERFORMANCE REQUIREMENTS

Retain this article with "Seismic Qualification Certificates" Paragraph in "Informational Submittals" Article for projects requiring seismic design. Model building codes and SEI/ASCE 7 establish criteria for buildings subject to earthquake motions. Verify requirements of authorities having jurisdiction.

A. Seismic Performance: Switchboards shall withstand the effects of earthquake motions determined according to [SEI/ASCE 7] <Insert requirement>.

Retain subparagraph below to define the term "withstand" as it applies to this Project. Definition varies with type of building and occupancy and is critical to valid certification. Option is used for essential facilities where equipment must operate immediately after an earthquake.

1. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified[ and the unit will be fully operational after the seismic event]."

1.3 ACTION SUBMITTALS

A. Product Data: For each type of product indicated.

B. Shop Drawings: For each switchboard and related equipment.

1. Include dimensioned plans, elevations, sections, and details, including required clearances and service space around equipment. Show tabulations of installed devices, equipment features, and ratings.

2. Include time-current coordination curves for each type and rating of overcurrent protective device included in switchboards.

3. Include schematic and wiring diagrams for power, signal, and control wiring.

1.4 INFORMATIONAL SUBMITTALS

A. Seismic Qualification Certificates: Submit certification that switchboards, overcurrent protective devices, accessories, and components will withstand seismic forces defined in Section 260548.16 "Seismic Controls for Electrical Systems."

B. Field quality-control reports.

1.5 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

1.6 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

B. Comply with NEMA PB 2.

C. Comply with NFPA 70.

D. Comply with UL 891.

1.7 WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this article are not less than remedies available to Owner under prevailing local laws.

A. Special Warranty: Manufacturer's standard form in which manufacturer agrees to repair or replace transient voltage suppression devices that fail in materials or workmanship within specified warranty period.

Verify available warranties and warranty periods with manufacturers listed in Part 2 articles.

1. Warranty Period: [Five] <Insert number> years from date of Substantial Completion.

PART 2 -  PRODUCTS

2.1 MANUFACTURED UNITS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."

A. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Eaton Electrical Inc.; Cutler-Hammer Business Unit.

2. General Electric Company; GE Consumer & Industrial - Electrical Distribution.

3. Siemens Energy & Automation, Inc.

4. Square D; a brand of Schneider Electric.

5. <Insert manufacturer's name>.

C. Front-Connected, Front-Accessible Switchboards:

1. Main Devices: [Panel] [Fixed, individually] mounted.

2. Branch Devices: Panel mounted.

3. Sections front and rear aligned.

Retain first two paragraphs below if rating data are not on Drawings.

D. Nominal System Voltage: [480Y/277 V] [208Y/120 V] <Insert system voltage>.

E. Main-Bus Continuous: [4000] [3000] [2500] [2000] [1600] [1200] <Insert ampere rating> A.

Retain first paragraph below for projects in seismic areas. If retaining, also retain "Seismic Qualification Certificates" Paragraph in "Informational Submittals" Article.

F. Seismic Requirements: Fabricate and test switchboards according to IEEE 344 to withstand seismic forces defined in Section 260548.16 "Seismic Controls for Electrical Systems."

Switchboards rely on natural convection for dissipating heat; therefore, NEMA 250, Type 12 enclosures are not usually available.

G. Enclosure: Steel, NEMA 250, [Type 1] [Type 3R] [Type 3R, with interior-lighted walk-in aisle].

1. Enclosure Finish: Factory-applied finish in manufacturer's standard gray finish over a rust-inhibiting primer on treated metal surface.

2. Enclosure: [Flat] [Downward, rearward sloping] roof; bolt-on rear covers for each section, with provisions for padlocking.

Retain first paragraph below for switchboards installed outdoors. Heaters and controls may be required for indoor units in unconditioned spaces.

H. Cubical Space Heaters: Factory-installed electric space heaters of sufficient wattage in each vertical section to maintain enclosure temperature above expected dew point.

I. Space-Heater Control: Thermostats to maintain temperature of each section.

J. Space-Heater Power Source: 120-V external branch circuit.

K. Utility Metering Compartment: Fabricated, barrier compartment and section complying with utility company's requirements. If separate vertical section is required for utility metering, match and align with basic switchboard. Provide service entrance label and necessary applicable service entrance features.

Pull sections in first paragraph below may be required if incoming supply is beneath switchboard.

L. Bus Transition and Incoming Pull Sections: Matched and aligned with basic switchboard.

M. Hinged Front Panels: Allow access to circuit breaker, metering, accessory, and blank compartments.

A pull box across the entire top of switchboard is usually only required for very large quantities of outgoing feeders and across the main incoming section for very large feeders with multiple large conductors per phase and neutral. Indicate the presence and extent of pull boxes on Drawings.

N. Pull Box on Top of Switchboard:

1. Adequate ventilation to maintain temperature in pull box within same limits as switchboard.

2. Removable covers shall form top, front, and sides. Top covers at rear shall be easily removable for drilling and cutting.

3. Bottom shall be insulating, fire-resistive material with separate holes for cable drops into switchboard.

4. Cable supports shall be arranged to facilitate cabling and adequate to support cables indicated, including those for future installation.

O. Phase and Neutral Buses and Connections: Three phase, four wire unless otherwise indicated. Tin-plated, high-strength, electrical-grade aluminum alloy with tin-plated aluminum circuit-breaker line connections.

1. Ground Bus: 1/4-by-2-inch- (6-by-50-mm-) minimum size, hard-drawn copper of 98 percent conductivity, equipped with pressure connectors for feeder and branch-circuit ground conductors.

2. Main Phase Buses and Equipment Ground Buses: Uniform capacity for entire length of switchboard's main and distribution sections. Provide for future extensions from both ends.

3. Neutral Buses: [50] [100] percent of the ampacity of phase buses unless otherwise indicated, equipped with pressure connectors for outgoing circuit neutral cables.

P. Future Devices: Equip compartments with mounting brackets, supports, bus connections, and appurtenances at full rating of circuit-breaker compartment.

2.2 TRANSIENT VOLTAGE SUPPRESSION DEVICES

A. Surge Protection Device Description: IEEE C62.41-compliant, integrally mounted, solid-state, parallel-connected, with sine-wave tracking suppression and filtering modules, UL 1449, second edition, short-circuit current rating matching or exceeding the switchboard short-circuit rating, and with the following features and accessories:

If specifying fuses for connecting TVSS devices to distribution system, verify ability of fuses to withstand surges consistent with ultimate surge current rating of device.

1. Fuses, rated at 200-kA interrupting capacity.

2. LED indicator lights for power and protection status.

3. Audible alarm, with silencing switch, to indicate when protection has failed.

4. Form-C contacts rated at 5 A and 250-V ac, one normally open and one normally closed, for remote monitoring of system operation. Contacts shall reverse position on failure of any surge diversion module or on opening of any current-limiting device.

5. Transient-event counter set to totalize transient surges.

Select first option in first paragraph below for high exposure and cost, second option for medium exposure and cost, and third option for low exposure and cost.

B. Peak Single-Impulse Surge Current Rating: [160 kA per mode/320 kA per phase] [120 kA per mode/240 kA per phase] [80 kA per mode/160 kA per phase].

C. Withstand Capabilities: 5000 IEEE C62.41, Category C3 (10 kA), 8-by-20-mic.sec. surges with less than 5 percent change in clamping voltage.

Adjust clamping voltages in paragraph below to comply with Project conditions and verify compatibility of peak surge current rating and clamping voltage. Reference to UL 1449 is to its second edition.

D. Protection modes and UL 1449 SVR for grounded wye circuits with [480Y/277] [208Y/120]-V, three-phase, four-wire circuits shall be as follows:

1. Line to Neutral: [800 V for 480Y/277] [400 V for 208Y/120].

2. Line to Ground: [800 V for 480Y/277] [400 V for 208Y/120].

3. Neutral to Ground: [800 V for 480Y/277] [400 V for 208Y/120].

2.3 DISCONNECTING AND OVERCURRENT PROTECTIVE DEVICES

Coordinate this article with Drawings. See the "Disconnecting and Overcurrent Protective Devices" Article in the Evaluations for guidance on making selections.

A. Molded-Case Circuit Breaker (MCCB): Comply with UL 489, with [series-connected rating] [interrupting capacity] to meet available fault currents.

1. Thermal-Magnetic Circuit Breakers: Inverse time-current element for low-level overloads, and instantaneous magnetic trip element for short circuits. Adjustable magnetic trip setting for circuit-breaker frame sizes 250 A and larger.

2. Adjustable Instantaneous-Trip Circuit Breakers: Magnetic trip element with front-mounted, field-adjustable trip setting.

3. Electronic trip circuit breakers with rms sensing; field-replaceable rating plug or field-replicable electronic trip; and the following field-adjustable settings:

Retain one or more of first four subparagraphs below; coordinate required adjustable settings with Section 260573 "Overcurrent Protective Device Coordination Study." See "Electronic rms Trip versus MCCBs" Paragraph in "Disconnecting and Overcurrent Protective Devices" Article in the Evaluations for additional features available for standard- and full-function trip units.

a. Instantaneous trip.

b. Long- and short-time pickup levels.

c. Long- and short-time time adjustments.

d. Ground-fault pickup level, time delay, and I2t response.

4. Current-Limiting Circuit Breakers: Frame sizes 400 A and smaller; let-through ratings less than NEMA FU 1, RK-5.

5. Molded-Case Circuit-Breaker (MCCB) Features and Accessories:

Not all accessories and options listed in subparagraphs below are available for every rating and from every listed manufacturer. Verify availability and unique characteristics with manufacturers selected.

a. Standard frame sizes, trip ratings, and number of poles.

See Editing Instruction No. 5 in the Evaluations for guidance on using mechanical vs. compression lugs.

b. Lugs: [Mechanical] [Compression] style, suitable for number, size, trip ratings, and conductor material.

c. Application Listing: Appropriate for application; Type SWD for switching fluorescent lighting loads; Type HID for feeding fluorescent and high-intensity discharge (HID) lighting circuits.

Select first option in first subparagraph below for solid-state trip units; select second option for thermal-magnetic trip units. If selecting second option, also retain "Shunt Trip" Subparagraph below.

d. Ground-Fault Protection: [Integrally mounted] [Remote-mounted] relay and trip unit with adjustable pickup and time-delay settings, push-to-test feature, and ground-fault indicator.

e. Zone-Selective Interlocking: Integral with electronic trip unit; for interlocking ground-fault protection function.

f. Communication Capability: [Circuit-breaker-mounted] [Universal-mounted] [Integral] [Din-rail-mounted] communication module with functions and features compatible with power monitoring and control system specified in Section 260913 "Electrical Power Monitoring and Control."

g. Shunt Trip: 120-V trip coil energized from separate circuit, set to trip at [55] [75] percent of rated voltage.

h. Undervoltage Trip: Set to operate at 35 to 75 percent of rated voltage without intentional time delay.

i. Auxiliary Contacts: [One SPDT switch] [Two SPDT switches] with "a" and "b" contacts; "a" contacts mimic circuit-breaker contacts, "b" contacts operate in reverse of circuit-breaker contacts.

j. Key Interlock Kit: Externally mounted to prohibit circuit-breaker operation; key shall be removable only when circuit breaker is in off position.

B. Insulated-Case Circuit Breaker (ICCB): 100 percent rated, sealed, insulated-case power circuit breaker with interrupting capacity rating to meet available fault current.

1. Fixed circuit-breaker mounting.

2. Two-step, stored-energy closing.

3. [Standard] [Full]-function, microprocessor-based trip units with interchangeable rating plug, trip indicators, and the following field-adjustable settings:

Retain one or more of first four subparagraphs below; coordinate required adjustable settings with Section 260573 "Overcurrent Protective Device Coordination Study." See "Electronic rms Trip versus MCCBs" Paragraph in "Disconnecting and Overcurrent Protective Devices" Article in the Evaluations for additional features available for standard- and full-function trip units.

a. Instantaneous trip.

b. Long- and short-time time adjustments.

c. Ground-fault pickup level, time delay, and I2t response.

d. <Insert settings>.

4. Zone-Selective Interlocking: Integral with electronic trip unit; for interlocking ground-fault protection function.

5. Remote trip indication and control.

6. Communication Capability: Integral communication module with functions and features compatible with power monitoring and control system specified in Section 260913 "Electrical Power Monitoring and Control."

7. Key Interlock Kit: Externally mounted to prohibit circuit-breaker operation; key shall be removable only when circuit breaker is in off position.

Retain voltage in subparagraph below to match control-power supply.

8. Control Voltage: [40-V dc] [125-V dc] [250-V dc] [120-V ac].

Retain one of first two paragraphs below.

C. Bolted-Pressure Contact Switch: Operating mechanism uses rotary-mechanical-bolting action to produce and maintain high clamping pressure on the switch blade after it engages the stationary contacts.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain first subparagraph and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. Boltswitch, Inc.

b. Eaton Electrical Inc.; Cutler-Hammer Business Unit.

c. Pringle Electrical Manufacturing Company, Inc.

d. Siemens Energy & Automation, Inc.

e. Square D; a brand of Schneider Electric.

f. <Insert manufacturer's name>.

2. Operating Mechanism: Manual handle operation to close switch; stores energy in mechanism for opening and closing.

Retain one or both of first two subparagraphs below depending on switch applications in Project. First subparagraph is for switches with ground-fault protection and for remotely tripped switches; second is for manually tripped units. See Editing Instruction No. 4 in the Evaluations. Coordinate with Drawings and include notation that identifies electrically and manually tripped switches.

a. Electrical Trip: Operation of lever or push-button trip switch, or trip signal from ground-fault relay or remote-control device, causes switch to open.

b. Mechanical Trip: Operation of mechanical lever, push button, or other device causes switch to open.

3. Auxiliary Switches: Factory installed, single pole, double throw, with leads connected to terminal block, and including one set more than quantity required for functional performance indicated.

Coordinate first subparagraph below with Drawings; include notation "suitable for use as service equipment" for switches that are the main control and means of disconnection for separately derived systems or for separate structures.

4. Service-Rated Switches: Labeled for use as service equipment.

Coordinate first subparagraph below with Drawings; indicate minimum fault-current rating of each switch.

5. Ground-Fault Relay: Comply with UL 1053; self-powered type with mechanical ground-fault indicator, test function, tripping relay with internal memory, and three-phase current transformer/sensor.

Revise first subparagraph below if relays capable of zone-selective interlocking are required.

a. Configuration: [Integrally mounted] [Remote-mounted] relay and trip unit with adjustable pickup and time-delay settings, push-to-test feature, and ground-fault indicator.

6. Open-Fuse Trip Device: Arranged to trip switch open if a phase fuse opens.

D. High-Pressure, Butt-Type Contact Switch: Operating mechanism uses butt-type contacts and a spring-charged mechanism to produce and maintain high-pressure contact when switch is closed.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain first subparagraph and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

a. General Electric Company; GE Consumer & Industrial - Electrical Distribution.

b. <Insert manufacturer's name>.

2. Operating Mechanism: Manual handle operation to close switch; stores energy in mechanism for opening and closing.

Retain one or both of first two subparagraphs below depending on switch applications in Project. First subparagraph is for switches with ground-fault protection and for remotely tripped switches; second is for manually tripped units. See Editing Instruction No. 4 in the Evaluations. Coordinate with Drawings and include notation that identifies electrically and manually tripped switches.

a. Electrical Trip: Operation of lever or push-button trip switch, or trip signal from ground-fault relay or remote-control device, causes switch to open.

b. Mechanical Trip: Operation of mechanical lever, push button, or other device causes switch to open.

3. Auxiliary Switches: Factory installed, single pole, double throw, with leads connected to terminal block, and including one set more than quantity required for functional performance indicated.

Coordinate first subparagraph below with Drawings; include notation "suitable for use as service equipment" for switches that are the main control and means of disconnection for separately derived systems or for separate structures.

4. Service-Rated Switches: Labeled for use as service equipment.

Coordinate first subparagraph below with Drawings; indicate minimum fault-current rating of each switch.

5. Ground-Fault Relay: Comply with UL 1053; self-powered type with mechanical ground-fault indicator, test function, tripping relay with internal memory, and three-phase current transformer/sensor.

Revise first subparagraph below if relays capable of zone-selective interlocking are required.

a. Configuration: [Integrally mounted] [Remote-mounted] relay and trip unit with adjustable pickup and time-delay settings, push-to-test feature, and ground-fault indicator.

6. Open-Fuse Trip Device: Arranged to trip switch open if a phase fuse opens.

E. Fused Switch: NEMA KS 1, Type HD; clips to accommodate specified fuses; lockable handle.

F. Fuses are specified in Section 262813 "Fuses."

2.4 INSTRUMENTATION

Retain this article for Owner, not utility, metering.

A. Instrument Transformers: IEEE C57.13, NEMA EI 21.1, and the following:

Coordinate first subparagraph below with Drawings and indicate specific accuracy classes and burdens required for each application and the primary-to-secondary ratio.

1. Current Transformers: IEEE C57.13; 5 A, 60 Hz, secondary and secondary shorting device. Burden and accuracy shall be consistent with connected metering and relay devices.

2. Control-Power Transformers: Dry type, mounted in separate compartments for units larger than 3 kVA.

Retain subparagraph below for certain ground-fault protection situations such as double-ended switchboards on four-wire, grounded neutral systems. Coordinate with Drawings.

3. Current Transformers for Neutral and Ground-Fault Current Sensing: Connect secondary wiring to ground overcurrent relays, via shorting terminals, to provide selective tripping of main and tie circuit breaker. Coordinate with feeder circuit-breaker, ground-fault protection.

Retain paragraph below if digital metering is required. It offers substantially more capabilities than analog metering in much smaller packages; however, some facility managers still prefer analog devices with large, easy-to-read dials.

B. Multifunction Digital-Metering Monitor: Microprocessor-based unit suitable for three- or four-wire systems and with the following features:

1. Switch-selectable digital display of the following values with maximum accuracy tolerances as indicated:

a. Phase Currents, Each Phase: Plus or minus 1 percent.

b. Phase-to-Phase Voltages, Three Phase: Plus or minus 1 percent.

c. Phase-to-Neutral Voltages, Three Phase: Plus or minus 1 percent.

d. Megawatts: Plus or minus 2 percent.

e. Megavars: Plus or minus 2 percent.

f. Power Factor: Plus or minus 2 percent.

g. Frequency: Plus or minus 0.5 percent.

h. Accumulated Energy, Megawatt Hours: Plus or minus 2 percent; accumulated values unaffected by power outages up to 72 hours.

Retain first subparagraph below for local recording of demand.

i. Megawatt Demand: Plus or minus 2 percent; demand interval programmable from five to 60 minutes.

2. Mounting: Display and control unit flush or semiflush mounted in instrument compartment door.

2.5 CONTROL POWER

A. Control Circuits: 120-V ac, supplied through secondary disconnecting devices from control-power transformer.

Retain three paragraphs below to require an automatic transfer of power using a main-tie-main or two-main scheme. See "Interlocked Main and Tie Circuit Breakers for Automatic and Manual Transfer of Power" Paragraph in "Disconnecting and Overcurrent Protective Devices" Article in the Evaluations for discussion of other types of available transfer schemes, along with advantages and disadvantages of each type.

B. Electrically Interlocked Main and Tie Circuit Breakers: Two control-power transformers in separate compartments, with interlocking relays, connected to the primary side of each control-power transformer at the line side of the associated main circuit breaker. 120-V secondaries connected through automatic transfer relays to ensure a fail-safe automatic transfer scheme.

C. Control-Power Fuses: Primary and secondary fuses for current-limiting and overload protection of transformer and fuses for protection of control circuits.

D. Control Wiring: Factory installed, with bundling, lacing, and protection included. Provide flexible conductors for No. 8 AWG and smaller, for conductors across hinges, and for conductors for interconnections between shipping units.

2.6 ACCESSORY COMPONENTS AND FEATURES

Retain first paragraph below for circuit breakers with solid-state trip devices.

A. Portable Test Set: For testing functions of solid-state trip devices without removing from switchboard. Include relay and meter test plugs suitable for testing switchboard meters and switchboard class relays.

Retain paragraph below if fuse cabinet is not specified in Section 262813 "Fuses."

B. Spare-Fuse Cabinet: Suitably identified, wall-mounted, lockable, compartmented steel box or cabinet. Arrange for wall mounting.

2.7 IDENTIFICATION

Retain this article for switchboards that incorporate one or more service disconnecting and overcurrent protective devices and that are used as the service entrance, outside feeder, or separately derived source means of disconnect and overcurrent protection.

A. Service Equipment Label: NRTL labeled for use as service equipment for switchboards with one or more service disconnecting and overcurrent protective devices.

PART 3 -  EXECUTION

3.1 INSTALLATION

Referenced NECA and NEMA standards in first paragraph below include similar requirements. See "Testing and Inspecting" Article in the Evaluations.

A. Receive, inspect, handle, store and install switchboards and accessories according to [NECA 400] [NEMA PB 2.1].

B. Equipment Mounting: Install switchboards on concrete base, 4-inch (100-mm) nominal thickness. Comply with requirements for concrete base specified in [Section 033000 "Cast-in-Place Concrete."] [Section 033053 "Miscellaneous Cast-in-Place Concrete."]

1. Install dowel rods to connect concrete base to concrete floor. Unless otherwise indicated, install dowel rods on 18-inch (450-mm) centers around the full perimeter of concrete base.

2. For supported equipment, install epoxy-coated anchor bolts that extend through concrete base and anchor into structural concrete floor.

3. Place and secure anchorage devices. Use setting drawings, templates, diagrams, instructions, and directions furnished with items to be embedded.

4. Install anchor bolts to elevations required for proper attachment to switchboards.

C. Temporary Lifting Provisions: Remove temporary lifting eyes, channels, and brackets and temporary blocking of moving parts from switchboard units and components.

Retain first paragraph below if seismic controls are required for Project. Coordinate with Drawings.

D. Comply with mounting and anchoring requirements specified in Section 260548.16 "Seismic Controls for Electrical Systems."

E. Install filler plates in unused spaces of panel-mounted sections.

F. Install overcurrent protective devices, transient voltage suppression devices, and instrumentation.

Subparagraph below assumes that settings are indicated on Drawings or a coordination report is available for Contractor to use.

1. Set field-adjustable switches and circuit-breaker trip ranges.

Retain first paragraph below if spare-fuse cabinets are specified in "Accessory Components and Features" Article.

G. Install spare-fuse cabinet.

H. Comply with NECA 1.

Coordinate two paragraphs below with Drawings. Show locations and types of grounding connections available and which ones are used for grounding switchboards.

Coordinate bus duct and cable tray installations and specialty arrangements with schematics on Drawings and with requirements specified for bus duct and cable tray systems. Ensure that referenced Sections include required interfacing terminations necessary to attach to switchboards. If Drawings are explicit enough, these requirements may be reduced or omitted.

I. Comply with requirements for terminating feeder bus specified in Section 262500 "Enclosed Bus Assemblies." Drawings indicate general arrangement of bus, fittings, and specialties.

J. Comply with requirements for terminating cable trays specified in Section 260536 "Cable Trays for Electrical Systems." Drawings indicate general arrangement of cable trays, fittings, and specialties.

3.2 IDENTIFICATION

A. Identify field-installed conductors, interconnecting wiring, and components; provide warning signs complying with requirements for identification specified in Section 260553 "Identification for Electrical Systems."

B. Switchboard Nameplates: Label each switchboard compartment with a nameplate complying with requirements for identification specified in Section 260553 "Identification for Electrical Systems."

C. Device Nameplates: Label each disconnecting and overcurrent protective device and each meter and control device mounted in compartment doors with a nameplate complying with requirements for identification specified in Section 260553 "Identification for Electrical Systems."

3.3 FIELD QUALITY CONTROL

A. Acceptance Testing Preparation:

1. Test insulation resistance for each switchboard bus, component, connecting supply, feeder, and control circuit.

2. Test continuity of each circuit.

B. Tests and Inspections:

1. Perform each visual and mechanical inspection and electrical test stated in NETA Acceptance Testing Specification. Certify compliance with test parameters.

2. Correct malfunctioning units on-site, where possible, and retest to demonstrate compliance; otherwise, replace with new units and retest.

3. Test and adjust controls, remote monitoring, and safeties. Replace damaged and malfunctioning controls and equipment.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

C. Switchboard will be considered defective if it does not pass tests and inspections.

D. Prepare test and inspection reports, including a certified report that identifies switchboards included and that describes scanning results. Include notation of deficiencies detected, remedial action taken, and observations after remedial action.

END OF SECTION 262413

	SWITCHBOARDS
	262413 - 1



