Copyright 2012 AIA
MasterSpec Professional
03/12

Copyright 2012 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 262416.16 - ELECTRONICALLY OPERATED CIRCUIT-BREAKER PANELBOARDS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes: Panelboards using electronically controlled, electrically operated circuit breakers.

1.2 DEFINITIONS

Retain terms that remain after this Section has been edited for a project.

A. BAS: Building automation system.

B. Low Voltage: As defined in NFPA 70 for circuits and equipment operating at less than 50 V or for remote-control, signaling power-limited circuits.

C. Monitoring: Acquisition, processing, communication, and display of equipment status data, metered electrical parameter values, power quality evaluation data, event and alarm signals, tabulated reports, and event logs.

D. RS-485: A serial network protocol, similar to RS-232, complying with TIA-485-A.

1.3 ACTION SUBMITTALS

A. Product Data: For each type of product.

B. Shop Drawings: For each electronically operated, circuit-breaker panelboard and related equipment.

1. Include dimensioned plans, elevations, sections, and details. Show tabulations of installed devices, equipment features, and ratings.

2. Detail bus configuration, current, and voltage ratings.

3. Short-circuit current rating of panelboards and overcurrent protective devices.

1.4 INFORMATIONAL SUBMITTALS

Retain "Seismic Qualification Certificates" Paragraph below if required by seismic criteria applicable to Project. Coordinate with Section 260548.16 "Seismic Controls for Electrical Systems." See ASCE/SEI 7 for certification requirements for equipment and components.

A. Seismic Qualification Certificates: For panelboards, accessories, and components, from manufacturer.

B. Field quality-control reports.

C. Sample Warranty: For manufacturer's special warranty.

1.5 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

Retain "Software and Firmware Operational Documentation" Paragraph below for PC- and IP-based control systems.

B. Software and Firmware Operational Documentation:

1. Software operating and upgrade manuals.

2. Program Software Backup: On magnetic media or compact disk, complete with data files.

3. Device address list.

4. Printout of software application and graphic screens.

1.6 QUALITY ASSURANCE

Retain "Testing Agency Qualifications" Paragraph below if Contractor selects testing agency or if Contractor is required to provide services of a qualified testing agency in "Field Quality Control" Article.

A. Testing Agency Qualifications: Member company of NETA or an NRTL.

1. Testing Agency's Field Supervisor: Certified by NETA to supervise on-site testing.

1.7 WARRANTY

A. Special Warranty: Manufacturer agrees to repair or replace transient voltage suppression devices that fail in materials or workmanship within specified warranty period.

Verify available warranties and warranty periods for units and components.

1. Warranty Period: [Five] <Insert number> years from date of Substantial Completion.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

2.1 MANUFACTURERS

Retain "Products" Paragraph and list of manufacturers and products below to require specific products or a comparable product from other manufacturers.

A. Products: Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

1. Eaton Corporation, Cutler-Hammer Business Unit; Pow-R-Command Control Panelboards.

2. General Electric Company, GE Consumer & Industrial - Electrical Distribution; A-Series Control Panels.

3. Siemens Energy & Automation, Inc.; i-3 Control Technology.

4. Square D, a brand of Schneider Electric; PowerLink G3 Control Panelboards.

5. <Insert manufacturer's name; product name or designation>.

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Eaton Corporation; Cutler-Hammer Business Unit.
2. General Electric Company; GE Consumer & Industrial - Electrical Distribution.
3. Siemens Energy & Automation, Inc.
4. Square D; a brand of Schneider Electric.
5. <Insert manufacturer's name>.

C. Source Limitations: Obtain electrically operated circuit breakers and power distribution components from single manufacturer.

2.2 SYSTEM DESCRIPTION

A. Input signal from field-mounted or on-board signal source shall open or close one or more electrically operated circuit breakers in the electronically operated, circuit-breaker panelboards. Any combination of inputs shall be programmable to any combination outputs.

B. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

C. Comply with 47 CFR, Subpart A and Subpart B, for Class A digital devices.

2.3 PERFORMANCE REQUIREMENTS

Retain "Seismic Performance" Paragraph below with "Seismic Qualification Certificates" Paragraph in "Informational Submittals" Article for projects requiring seismic design. Delete paragraph if performance requirements are indicated on Drawings. Model building codes and ASCE/SEI 7 establish criteria for buildings subject to earthquake motions. Coordinate requirements with structural engineer.

A. Seismic Performance: Panelboards shall withstand the effects of earthquake motions determined according to [ASCE/SEI 7] <Insert requirement>.

Retain subparagraph below to define the term "withstand" as it applies to this Project. Definition varies with type of building and occupancy and is critical to valid certification. Option is used for essential facilities where equipment must operate immediately after an earthquake.

1. The term "withstand" means "the unit will remain in place without separation of any parts when subjected to the seismic forces specified[ and the unit will be fully operational after the seismic event]."

For life-safety components required to function after an earthquake (such as fire-sprinkler systems, components that contain hazardous content, and storage racks in structures open to the public), the Component Importance Factor is 1.5. For other components, the Component Importance Factor is 1.0 unless the structure is in Seismic Use Group III and component is necessary for continued operation of facility or failure of component could impair continued operation of facility, in which case the Component Importance Factor is 1.5.

2. Component Importance Factor: [1.5] [1.0].

See ASCE/SEI 7, Coefficients for Architectural Component Table and Seismic Coefficients for Mechanical and Electrical Components Table for requirements to be inserted in subparagraph below.

3. <Insert requirements for Component Amplification Factor and Component Response Modification Factor>.

2.4 PANELBOARDS

A. Electronically operated, circuit-breaker panelboards may contain remotely operated circuit breakers and standard branch circuit breakers specified in Section 262416 "Panelboards."

B. Assemblies: Comply with UL 67 and NEMA PB 1.

Retain one of two "Surge Protective Device" paragraphs below.

C. Surge Protective Device: Field mounted, complying with Section 264313 "Transient-Voltage Suppression for Low-Voltage Electrical Power Circuits."

D. Surge Protective Device: Integrally mounted, complying with UL 1449 Type 1.

1. Comply with IEEE C62.41, Category C, 200-kA short-circuit current rating.

2. Non-modular type with the following features and accessories:

a. Digital-display indicator lights for power and protection status.

b. <Insert features and accessories>.

E. Enclosures: Comply with UL 50 and NEMA 250.

Retain "Future Devices" Paragraph below if future provisions are required.

F. Future Devices: Mounting brackets, bus connections, filler plates, and necessary appurtenances required for future installation of devices.

G. Panelboard Short-Circuit Current Rating: Fully rated to interrupt [10-kA ]symmetrical short-circuit current available at terminals.

2.5 CIRCUIT BREAKERS

A. Remotely operated branch circuit breakers shall provide branch circuit overcurrent protection.

In "Labeled with SWD and HID Ratings" Paragraph below, SWD rating is only available for 15- and 20-A, single-pole circuit breakers. Retain option if specifying other breaker sizes.

See Editing Instruction No. 2 in the Evaluations for discussion on short-circuit current ratings for equipment complying with UL 489.

B. Labeled with SWD and HID Ratings: Comply with UL 489 for 15- and 20-A, single-pole branch devices.[ 15- and 20-A circuit breakers, if scheduled, shall be a product of same manufacturer, and be of same class as the rated circuit breakers.]

Retain "Switching Endurance Rating" Paragraph below if endurance in excess of UL 489 SWD test is required. Verify test method and available ratings with manufacturers.

C. Switching Endurance Rating: Not less than [50,000] [200,000] <Insert number> full-load open/close/open remote operations.

D. Remotely Operated Circuit Breakers: Manual override switch or handle position shall enable or disable the remote operation of the device and allow breaker handle to manually control the breaker's on-off status.

2.6 CONTROLLERS

A. Description: Controllers shall contain the power supply and electronic control for operating and monitoring remotely operated branch circuit breakers.

See Editing Instruction No. 2 in the Evaluations for discussion on short-circuit current ratings for equipment complying with UL 916.

1. Comply with UL 916 (CSA C22.2, No. 205); with a microprocessor-based, solid-state, 365-day timing and control unit.

2. Power Supply: Powered from the panelboard, sized to provide control power for the operation of the remotely operated circuit breakers, controller, bus system, low-voltage inputs, and field-installed sensors.

3. Integral keypad and digital-display front panel for local setup, including the following:

a. Log and display remotely operated breaker on-time.

b. Provision to accept downloadable firmware so that the latest features may be added in the future without replacing the module.

4. Nonvolatile memory shall retain all setup configurations. After a power failure, the controller shall automatically reboot and return to normal system operation.

In "Time Synchronization" Subparagraph below, the typical value ranges from one hour to 24 hours.

5. Time Synchronization: The timing unit shall be updated not less than every <Insert number> hour(s) with the network time server.

B. Timing Unit:

1. 365-day calendar, astronomical clock, and automatic adjustments for daylight savings and leap year.

2. Clock configurable for 12-hour (A.M./P.M.) or 24-hour format.

3. [16] <Insert number> independent schedules, each having [24] <Insert number> time periods.

4. Schedule periods settable to the minute.

5. Day of week, day of month, day of year with one-time or repeating capability.

6. [32] <Insert number> special date periods.

C. With [eight] [16] <Insert number> inputs, each configurable to the following parameters:

1. Normally open, normally closed, two-wire maintained toggle, two-wire momentary toggle, two-wire momentary on, two-wire momentary off, or three-wire momentary operation.

2. On and off-delay timers for local override operation, adjustable from five minutes to 12 hours. Local override shall be by field-installed, two-wire momentary toggle switch.

2.7 MANUAL SWITCHES AND PLATES

Coordinate use of manual switches in this article with override functions, with switch and wall-plate finish specified in Section 262726 "Wiring Devices."

A. Keypads: Programmable, designed to control functions associated with the equipment of this Section. The units shall be able to control any system output device.

B. Push-Button Switches: Modular, momentary-contact, low-voltage type.

1. Match color specified in Section 262726 "Wiring Devices."

Two subparagraphs below are optional features.

2. Integral green [digital-display] [neon] pilot light to indicate when circuit is on.

3. Internal white [digital-display] [neon] locator light to illuminate when circuit is off.

C. Manual, Maintained Contact, Full- or Low-Voltage Switch: Comply with Section 262726 "Wiring Devices."

D. Wall Plates: Single and multigang plates as specified in Section 262726 "Wiring Devices."

E. Legend: Engraved or permanently silk-screened on wall plate where indicated. Use designations indicated on Drawings.

2.8 CONDUCTORS AND CABLES

A. Power Wiring to Supply Side of Class 2 Power Source: Not smaller than No. 12 AWG. Comply with Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

B. Class 2 and Class 3 Control Cables: Multiconductor cable with copper conductors not smaller than [No. 18] [No. 22] [No. 24] AWG. Comply with Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

C. Class 1 Control Cables: Multiconductor cable with copper conductors not smaller than [No. 14] [No. 16] [No. 18] AWG. Comply with Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

PART 3 -  EXECUTION

3.1 WIRING INSTALLATION

A. Comply with NECA 1.

Retain one of two "Wiring Method" paragraphs below and coordinate with Drawings. Delete both if wiring methods for system are indicated on Drawings.

B. Wiring Method: Install cables in raceways and cable trays except within consoles, cabinets, desks, and counters[ and except in accessible ceiling spaces and in gypsum board partitions where unenclosed wiring method may be used]. Conceal raceway and cables except in unfinished spaces.

Retain first subparagraph below if retaining unenclosed wiring method option in "Wiring Method" Paragraph above.

1. Install plenum cable in environmental air spaces, including plenum ceilings.

2. Comply with requirements for cable trays specified in Section 260536 "Cable Trays for Electrical Systems."

3. Comply with requirements for raceways and boxes specified in Section 260533 "Raceways and Boxes for Electrical Systems."

C. Wiring Method: Conceal conductors and cables in accessible ceilings, walls, and floors where possible.

D. Wiring within Enclosures: Bundle, lace, and train conductors to terminal points with no excess and without exceeding manufacturer's limitations on bending radii. Install lacing bars and distribution spools.

3.2 PANELBOARD INSTALLATION

A. Comply with NECA 1.

NECA and NEMA standards in first paragraph below include similar requirements. See "Testing and Inspecting" Article in the Evaluations.

B. Install panelboards and accessories according to [NECA 407] [NEMA PB 1.1].

Retain first paragraph below if seismic controls are required for Project. Coordinate with Drawings.

C. Comply with mounting and anchoring requirements specified in Section 260548.16 "Seismic Controls for Electrical Systems."

In "Mounting Height" Paragraph below, verify that operating handle of top-most switch or circuit breaker, in on position, is not higher than 79 inches (2000 mm) above finished floor or grade.

D. Mounting Height: [90 inches (2286 mm)] <Insert dimension> to top of trim above finished floor unless otherwise indicated.

E. Mount panelboard cabinet plumb and rigid without distortion of box. Mount recessed panelboards with fronts uniformly flush with wall finish and mating with back box.

F. Install filler plates in unused spaces.

3.3 IDENTIFICATION

A. Identify system components, wiring, cabling, and terminals. Comply with requirements for identification specified in Section 260553 "Identification for Electrical Systems."

B. Identify field-installed conductors, interconnecting wiring, and components; provide warning signs complying with Section 260553 "Identification for Electrical Systems."

C. Create a directory to indicate loads served by each circuit; incorporate Owner's final room designations. Obtain approval before installing. Use a computer or typewriter to create directory; handwritten directories are unacceptable.

D. Panelboard Nameplates: Label each panelboard with a nameplate complying with requirements for identification specified in Section 260553 "Identification for Electrical Systems."

3.4 FIELD QUALITY CONTROL

Retain "Testing Agency" and "Perform the following tests and inspections" paragraphs below to identify who shall perform tests and inspections. If retaining second option in "Testing Agency" Paragraph, retain "Field quality-control reports" Paragraph in "Informational Submittals" Article.

Coordinate testing requirements with Section 262416 "Panelboards."

A. Testing Agency: [Owner will engage] [Engage] a qualified testing agency to perform tests and inspections.

Retain "Perform the following tests and inspections" Paragraph below to require Contractor to perform tests and inspections.

B. Perform the following tests and inspections[ with the assistance of a factory-authorized service representative]:

1. Perform each visual and mechanical inspection and electrical test stated in NETA Acceptance Testing Specification. Certify compliance with test parameters.

2. Correct malfunctioning units on-site, where possible, and retest to demonstrate compliance; otherwise, replace with new units and retest.

3. Perform the following infrared scan tests and inspections and prepare reports:

a. Initial Infrared Scanning: After Substantial Completion, but not more than 60 days after Final Acceptance, perform an infrared scan of each panelboard. Remove front panels so joints and connections are accessible to portable scanner.

b. Follow-up Infrared Scanning: Perform an additional follow-up infrared scan of each panelboard 11 months after date of Substantial Completion.

c. Instruments and Equipment:

1) Use an infrared scanning device designed to measure temperature or to detect significant deviations from normal values. Provide calibration record for device.

C. Acceptance Testing Preparation:

1. Test insulation resistance for each panelboard bus, component, connecting supply, feeder, and control circuit.

2. Test continuity of each circuit.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

D. Panelboard will be considered defective if it does not pass tests and inspections.

Retain paragraph below if tests and inspections are performed by Contractor or manufacturer's field-service representative engaged by Contractor.

E. Prepare test and inspection reports, including a certified report that identifies panelboards included and describes scanning results. Include notation of deficiencies detected, remedial action taken, and observations made after remedial action.

3.5 DEMONSTRATION

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain control modules.

END OF SECTION 262416.16

	ELECTRONICALLY OPERATED CIRCUIT-BREAKER PANELBOARDS
	262416.16 - 1



