Copyright 2012 AIA
MasterSpec Professional
03/12

Copyright 2012 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 262419 - MOTOR-CONTROL CENTERS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

If applying for LEED certification, LEED-NC Prerequisite EA 2 requires compliance with ASHRAE/IESNA 90.1-2004, which requires the use of mechanical or electrical variable-speed drives on fan motors used in VAV system fans that are 15 hp and larger and on motors in variable-flow hydronic systems that are larger than 50 hp.

LEED-NC Credit EA 5 requires the development of a Measurement & Verification Plan to achieve this credit.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section includes MCCs for use with ac circuits rated 600 V and less and having the following factory-installed components:

1. Incoming main lugs and OCPDs.

2. Full-voltage magnetic controllers.

3. Reduced-voltage, solid-state controllers.

4. Multispeed controllers.

5. Feeder-tap units.

6. Instrumentation.

7. Auxiliary devices.

1.2 DEFINITIONS

Retain definition(s) remaining after this Section has been edited.

A. BAS: Building automation system.

B. CPT: Control power transformer.

C. LED: Light-emitting diode.

D. MCC: Motor-control center.

E. MCCB: Molded-case circuit breaker.

F. MCP: Motor-circuit protector.

G. NC: Normally closed.

H. NO: Normally open.

I. OCPD: Overcurrent protective device.

J. PT: Potential transformer.

K. SCR: Silicon-controlled rectifier.

1.3 PERFORMANCE REQUIREMENTS

Retain this article with "Seismic Qualification Certificates" Paragraph in "Informational Submittals" Article for projects requiring seismic design. Model building codes and ASCE/SEI 7 establish criteria for buildings subject to earthquake motions. Verify requirements of authorities having jurisdiction.

A. Seismic Performance: MCCs shall withstand the effects of earthquake motions determined according to [ASCE/SEI 7] <Insert requirement>.

Retain subparagraph below to define the term "withstand" as it applies to this Project. Definition varies with type of building and occupancy and is critical to valid certification. Option is used for essential facilities where equipment must operate immediately after an earthquake.

1. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified[ and the unit will be fully operational after the seismic event]."

1.4 ACTION SUBMITTALS

A. Product Data: For each type of controller and each type of MCC.

B. LEED Submittals:

LEED-NC Credit EA 5 requires continuous metering equipment for monitoring building energy-consumption performance over time.

1. Product Data for Credit EA 5: For continuous metering equipment for energy consumption.

See Editing Instructions No. 2 and No. 3 in the Evaluations for discussion of Shop Drawing types defined in UL 845 that are available from manufacturers. If retaining "Shop Drawings" Paragraph below, coordinate with manufacturers for availability of information and include additional information to suit Project.

C. Shop Drawings: For each MCC, manufacturer's approval drawings as defined in UL 845. In addition to requirements specified in UL 845, include dimensioned plans, elevations, and sections; and conduit entry locations and sizes, mounting arrangements, and details, including required clearances and service space around equipment.

1. Show tabulations of installed devices, equipment features, and ratings.

2. Schematic[ and Connection] Wiring Diagrams: For power, signal, and control wiring for each installed controller.

3. Nameplate legends.

4. Vertical and horizontal bus capacities.

5. Features, characteristics, ratings, and factory settings of each installed unit.

6. <Insert required information>.

1.5 INFORMATIONAL SUBMITTALS

Retain "Coordination Drawings" Paragraph below if Drawings do not include detailed plans or if Project involves unusual coordination requirements. See "Installation Considerations" Article in the Evaluations for additional guidance on when to retain paragraph.

A. Coordination Drawings: Floor plans, drawn to scale, showing dimensioned layout, required working clearances, and required area above and around MCCs where pipe and ducts are prohibited. Show MCC layout and relationships between electrical components and adjacent structural and mechanical elements. Show support locations, type of support, and weight on each support. Indicate field measurements.

Retain "Seismic Qualification Certificates" Paragraph below if required by seismic criteria applicable to Project. Coordinate with Sections specifying mechanical vibration, supports, electrical supports, and seismic controls. See ASCE/SEI 7 for certification requirements for equipment and components.

B. Seismic Qualification Certificates: For MCCs, accessories, and components, from manufacturer.

C. Product certificates.

D. Source quality-control reports.

E. Field quality-control reports.

1.6 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

1.7 QUALITY ASSURANCE

Retain "Testing Agency Qualifications" Paragraph below if Contractor is required to provide services of a qualified testing agency in "Field Quality Control" Article. Qualification requirements are in addition to those specified in Section 014000 "Quality Requirements," which also includes the definition for "NRTL" (nationally recognized testing laboratory).

A. Testing Agency Qualifications: Member company of NETA or an NRTL.

B. Source Limitations: Obtain MCCs and controllers of a single type from single source from single manufacturer.

C. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

D. Comply with NFPA 70.

Retain "IEEE Compliance" Paragraph below for projects in seismic areas. If retaining, also retain "Seismic Qualification Certificates" Paragraph in "Informational Submittals" Article.

E. IEEE Compliance: Fabricate and test enclosed controllers according to IEEE 344 to withstand seismic forces defined in Section 260548.16 "Seismic Controls for Electrical Systems."

PART 2 -  PRODUCTS

2.1 MANUFACTURED UNITS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain "Manufacturers" Paragraph or "Basis-of-Design Product" Paragraph and list of manufacturers below. See Section 016000 "Product Requirements."

A. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in "Basis-of-Design Product" Paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings. See "Installation Considerations" Article in the Evaluations for additional guidance on when to retain paragraph.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. ABB; Control Products.

2. Eaton Electrical Inc.; Cutler-Hammer Business Unit.

3. General Electric Company; GE Industrial Systems.

4. Rockwell Automation, Inc.; Allen-Bradley Brand.

5. Siemens Energy & Automation, Inc.; Power Distribution.

6. Square D; a brand of Schneider Electric.

7. <Insert manufacturer's name>.

MCCs in this article include service and distribution types most commonly applied. Coordinate types of MCCs with types of controllers and OCPDs and with MCC arrangements and available spaces. Consult manufacturer to determine layout requirements. See Evaluations. Most MCCs are both front and rear aligned, with the possible exception of units with extremely large or unusual main and fixed branch cubicles. The Section Text defaults to front and rear alignment, with front-only access; coordinate with manufacturers for unusual conditions.

C. General Requirements for MCCs: Comply with NEMA ICS 18 and [UL 845] <Insert standard>.

2.2 FUNCTIONAL FEATURES

In addition to equipment and devices included in the Section Text, UL 845 and various listed manufacturers also allow in MCCs such items as automatic transfer switches, distribution transformers, lighting and appliance and distribution panelboards, combination lighting contactors, etc. Although not included in the Section Text, these items can be added if required. Coordinate with retained unit types and Drawings.

A. Description: Modular arrangement of main units, controller units, control devices, feeder-tap units, instruments, metering, auxiliary devices, and other items mounted in vertical sections of MCC.

Coordinate "Controller Units" Paragraph below with Drawings.

B. Controller Units: Combination controller units.

1. Install units up to and including Size 3 on drawout mountings with connectors that automatically line up and connect with vertical-section buses while being racked into their normal, energized positions.

2. Equip units in Type B with pull-apart terminal strips for external control connections.

Coordinate "Feeder-Tap Units" Paragraph below with Drawings.

C. Feeder-Tap Units: Through 225-A rating shall have drawout mountings with connectors that automatically line up and connect with vertical-section buses while being racked into their normal, energized positions.

Coordinate "Future Units" Paragraph below with Drawings. Indicate, in schedule, sizes of future controllers to be accommodated.

D. Future Units: Compartments fully bused and equipped with guide rails or equivalent, ready for insertion of drawout units.

Coordinate "Spare Units" Paragraph below with Drawings.

E. Spare Units: Installed in compartments indicated "spare."

2.3 INCOMING MAINS

Not all manufacturers offer all options in this article. Coordinate with manufacturers for available options. Coordinate selection of the disconnecting means and OCPD with short-circuit current ratings required for Project. See the "Main- and Feeder-Tap Disconnecting and Overcurrent Protective Devices" Article and Editing Instructions No. 5, No. 6, and No. 9 in the Evaluations for guidance on making selections.

Retain "Incoming Mains Location" Paragraph below, and coordinate with Drawings and schedules, if Project requirements include identifying specific entry locations for incoming service or feeder raceways.

A. Incoming Mains Location: [Top] [and] [bottom].

Include instructions in "Main Lugs Only" Paragraph below if special sizing or oversizing of lugs is required, if allowing optional use of aluminum for circuits sized for copper conductors, or when upsizing conductors for voltage drop.

B. Main Lugs Only: Conductor connectors suitable for use with conductor material and sizes.

1. Material: [Tin-plated aluminum] [Hard-drawn copper, 98 percent conductivity].

2. Main and Neutral Lugs: [Compression] [Mechanical] type.

C. MCCB: Comply with UL 489, with [series-connected rating] [interrupting capacity] to meet available fault currents.

1. Thermal-Magnetic Circuit Breakers: Inverse time-current element for low-level overloads, and instantaneous magnetic trip element for short circuits. Adjustable magnetic trip setting for circuit-breaker frame sizes 250 A and larger.

2. Electronic trip circuit breakers with rms sensing; field-replaceable rating plug or field-replicable electronic trip; and the following field-adjustable settings:

Retain one or more of first four subparagraphs below; coordinate required adjustable settings with Section 260573 "Overcurrent Protective Device Coordination Study." See "Electronic rms Trip versus MCCBs and ICCBs" Paragraph in "Main- and Feeder-Tap Disconnecting and Overcurrent Protective Devices" Article in the Evaluations for additional guidance on specifying full- or standard-function features.

a. Instantaneous trip.

b. Long- and short-time pickup levels.

c. Long- and short-time time adjustments.

d. Ground-fault pickup level, time delay, and I2t response.

3. MCCB Features and Accessories:

Not all accessories and options listed in subparagraphs below are available for every rating and from every listed manufacturer. Verify, with manufacturers, availability and unique characteristics.

a. Standard frame sizes, trip ratings, and number of poles.

See Editing Instruction No. 14 in the Evaluations for guidance on using mechanical versus compression lugs.

b. Lugs: [Mechanical] [Compression] style, suitable for number, size, trip ratings, and conductor material.

c. Application Listing: Appropriate for application; Type SWD for switching fluorescent lighting loads; Type HID for feeding fluorescent and high-intensity discharge (HID) lighting circuits.

Retain first option in "Ground-Fault Protection" Subparagraph below for solid-state trip units; retain second option for thermal-magnetic trip units. If retaining second option, also retain "Shunt Trip" Subparagraph below.

d. Ground-Fault Protection: [Integrally mounted] [Remote-mounted] relay and trip unit with adjustable pickup and time-delay settings, push-to-test feature, and ground-fault indicator.

e. Shunt Trip: 120-V trip coil energized from separate circuit, set to trip at [55] [75] percent of rated voltage.

f. Auxiliary Contacts: [One SPDT switch] [Two SPDT switches] with "a" and "b" contacts; "a" contacts mimic circuit-breaker contacts, "b" contacts operate in reverse of circuit-breaker contacts.

2.4 COMBINATION CONTROLLERS

A. Full-Voltage Controllers:

Show controller pole quantities, NEMA size and type, and accessories for each controller on Drawings. See "Full-Voltage Controllers" Article in the Evaluations for selection considerations. See Editing Instructions No. 4 and No. 10 in the Evaluations.

Not all features, accessories, and options in this article are available for every rating, with every type enclosure, and from every listed manufacturer. Verify, with manufacturers, availability and unique characteristics. Show on Drawings those features and accessories that apply to each controller.

1. General Requirements for Full-Voltage Enclosed Controllers: Comply with NEMA ICS 2, general purpose, Class A.

Three-pole, integral horsepower magnetic controllers are suitable for use with three-phase ac motors up to 1600 hp, and from NEMA ICS 2, Size 00 to Size 9; however, not all listed manufacturers offer enclosed controllers up to Size 9. Two- and four-pole models are also available in varying minimum and maximum horsepower ratings and NEMA sizes. See "Magnetic Controllers" Article in the Evaluations for additional guidance on their use.

2. Magnetic Controllers: Full voltage, across the line, electrically held.

a. Configuration: [Nonreversing] [and] [reversing] <Insert configuration>.

B. Reduced-Voltage, Solid-State Controllers:

Show controller pole quantities, NEMA size and type, and accessories for each controller on Drawings. See "Reduced-Voltage Controllers," "Reduced-Voltage, Solid-State Controllers," and "Solid-State Controllers" articles in the Evaluations for selection considerations. See Editing Instructions No. 4 and No. 11 in the Evaluations.

Standard and optional features vary considerably among manufacturers of solid-state controllers. Also, features and options depend on motor characteristics and operating criteria of driven equipment.

1. General Requirements for Reduced-Voltage, Solid-State Controllers: Comply with UL 508.

Three-pole, reduced-voltage, solid-state controllers are available for use with three-phase ac motors 3 to 600 hp, and in voltages from 208- to 575-V ac; however, not all listed manufacturers may offer enclosed controllers in all these ratings and voltage ranges.

2. Reduced-Voltage, Solid-State Controllers: An integrated unit with power SCRs, heat sink, microprocessor logic board, door-mounted digital display and keypad, bypass contactor, and overload relay; suitable for use with NEMA MG 1, Design B, polyphase, medium-induction motors.

a. Configuration: [Standard duty] [Severe duty]; [nonreversible] [reversible].

b. Starting Mode: [Voltage ramping] [Current limit] [Torque control] [Torque control with voltage boost][; field selectable].

c. Stopping Mode: [Coast to stop] [Adjustable torque deceleration] [Adjustable braking][; field selectable].

Most manufacturers provide shorting contactors to bypass the SCRs at full speed, instead of the controller operating continually through the SCRs. Bypass contactors are usually of less than full-voltage rating, and many are IEC-rated controllers. They are not sized or intended for starting the motor across the line. Some manufacturers, however, offer the alternative of full-voltage bypass contactors for severe-duty applications, to completely bypass the SCRs on failure (allowing use of the controller as a full-voltage controller).

d. Shorting (Bypass) Contactor: Operates automatically when full voltage is applied to motor, and bypasses the SCRs. Solid-state controller protective features shall remain active when the shorting contactor is in the bypass mode.

e. Shorting[ and Input Isolation] Contactor Coils: Pressure-encapsulated type; manufacturer's standard operating voltage, matching control power or line voltage, depending on contactor size and line-voltage rating.[ Provide coil transient suppressors.]

f. Logic Board: Identical for all ampere ratings and voltage classes, with environmental protective coating.

g. Adjustable acceleration-rate control using voltage or current ramp, and adjustable starting torque control with up to [400] <Insert number> percent current limitation for 20 seconds.

h. SCR bridge shall consist of at least two SCRs per phase, providing stable and smooth acceleration [with] [without] external feedback from the motor or driven equipment.

i. Keypad, front accessible; for programming the controller parameters, functions, and features; shall be manufacturer's standard and include not less than the following functions:

1) Adjusting motor full-load amperes, as a percentage of the controller's rating.

2) Adjusting current limitation on starting, as a percentage of the motor full-load current rating.

3) Adjusting linear acceleration and deceleration ramps, in seconds.

4) Initial torque, as a percentage of the nominal motor torque.

5) Adjusting torque limit, as a percentage of the nominal motor torque.

6) Adjusting maximum start time, in seconds.

7) Adjusting voltage boost, as a percentage of the nominal supply voltage.

8) Selecting stopping mode, and adjusting parameters.

9) Selecting motor thermal-overload protection class between 5 and 30.

10) Activating and de-activating protection modes.

11) Selecting or activating communications modes.

12) <Insert function>.

j. Digital display, front accessible; for showing motor, controller, and fault status; shall be manufacturer's standard and include not less than the following:

1) Controller Condition: Ready, starting, running, stopping.

2) Motor Condition: Amperes, voltage, power factor, power, and thermal state.

3) Fault Conditions: Controller thermal fault, motor overload alarm and trip, motor underload, overcurrent, shorted SCRs, line or phase loss, phase reversal, and line frequency over or under normal.

4) <Insert items>.

k. Controller Diagnostics and Protection:

1) Microprocessor-based thermal protection system for monitoring SCR and motor thermal characteristics, and providing controller overtemperature and motor overload alarm and trip; settings selectable via the keypad.

2) Protection from line-side reverse phasing; line-side and motor-side phase loss; motor jam, stall, and underload conditions; and line frequency over or under normal.

Retain one of first two subparagraphs below to provide motor protection on a controller fault.

3) Input isolation contactor that opens when the controller diagnostics detect a faulted solid-state component, or when the motor is stopped.

Retain first subparagraph below only if specifying combination controllers.

4) Shunt trip that opens the disconnecting means when the controller diagnostics detect a faulted solid-state component.

5) <Insert items>.

l. Remote Output Features:

1) All outputs prewired to terminal blocks.

2) Form C status contacts that change state when controller is running.

3) Form C alarm contacts that change state when a fault condition occurs.

4) <Insert items>.

m. Optional Features:

1) Analog output for field-selectable assignment of motor operating characteristics; [0 to 10-V dc] [4 to 20-mA dc].

2) Additional field-assignable Form C contacts for alarm outputs.

3) Surge suppressors in solid-state power circuits providing three-phase protection against damage from supply voltage surges 10 percent or more above nominal line voltage.

4) Full-voltage bypass contactor operating [automatically] [manually, with NORMAL/BYPASS selector switch]. Power contacts shall be totally enclosed, double break, and silver-cadmium oxide; and assembled to allow inspection and replacement without disturbing line or load wiring.

C. Multispeed Magnetic Controllers:

Show controller pole quantities, NEMA size and type, and accessories for each controller on Drawings. See "Multispeed Controllers" Article in the Evaluations for selection considerations. See Editing Instructions No. 4 and No. 11 in the Evaluations. The Section Text includes two-speed controllers only; however, most manufacturers catalog controllers offering more than two speeds. Multispeed controllers supporting more than two speeds may be added to suit Project.

1. General Requirements for Multispeed Magnetic Controllers: Comply with NEMA ICS 2, general purpose, Class A.

2. Multispeed Magnetic Controllers: Two speed, full voltage, across the line, electrically held. Compelling relay to ensure that motor will start only at low speed.

a. Configuration: [Nonreversing] [Reversing]; [consequent pole] [two winding].

Retain one or both of first two subparagraphs below. If retaining both, indicate on Drawings where each type is required. Compelling and accelerating relays cannot be specified together for the same controller. Compelling, accelerating, and decelerating relays can be used for all multispeed controllers; antiplugging relays are used only for reversing multispeed controllers.

b. Compelling relays shall ensure that motor starts only at low speed.

c. Accelerating timer relays shall ensure properly timed acceleration through speeds lower than that selected.

d. Decelerating timer relays shall ensure automatically timed deceleration through each speed.

e. Antiplugging timer relays shall ensure a time delay when transferring from FORWARD to REVERSE and back.

D. Disconnecting Means and OCPDs:

Disconnecting means and OCPDs must be closely coordinated with calculated short-circuit current values at the controller locations because they are directly related to short-circuit withstand ratings of their combination controllers. Although fusible switches (with appropriate fuses) can provide Type 2 controller protection from very high short-circuit currents, not all circuit breakers or MCPs can. See Editing Instructions No. 9 and No. 10 in the Evaluations for explanation of protection types and when they should be considered. The Section Text does not include nonfusible disconnecting means because they are usually not an option with MCCs.

1. Fusible Disconnecting Means:

a. NEMA KS 1, heavy-duty, horsepower-rated, fusible switch with clips or bolt pads to accommodate [Class J] [Class L] <Insert class> fuses.

b. Lockable Handle: Accepts three padlocks and interlocks with cover in closed position.

Retain "Auxiliary Contacts" Subparagraph below if external control power is used or for remote indication of disconnecting means position.

c. Auxiliary Contacts: NO/NC, arranged to activate before switch blades open.

MCP disconnecting means must be used in combination with integral overload relays.

2. MCP Disconnecting Means:

a. UL 489, NEMA AB 1, and NEMA AB 3, with interrupting capacity to comply with available fault currents, instantaneous-only circuit breaker with front-mounted, field-adjustable, short-circuit trip coordinated with motor locked-rotor amperes.

b. Lockable Handle: Accepts three padlocks and interlocks with cover in closed position.

Retain one or both of first two subparagraphs below. Retain first subparagraph if external control power is used or for remote indication of disconnecting means position. Retain second subparagraph for remote indication of tripped condition. If retaining auxiliary and alarm contacts, indicate "a" and "b" contact quantities and NO or NC contact requirements on Drawings.

c. Auxiliary contacts "a" and "b" arranged to activate with MCP handle.

d. [NC] [NO] alarm contact that operates only when MCP has tripped.

First subparagraph below is an optional, added-cost feature.

e. Current-limiting module to increase controller short-circuit current (withstand) rating to 100 kA.

3. MCCB Disconnecting Means:

a. UL 489, NEMA AB 1, and NEMA AB 3, with interrupting capacity to comply with available fault currents; thermal-magnetic MCCB, with inverse time-current element for low-level overloads and instantaneous magnetic trip element for short circuits.

b. Front-mounted, adjustable magnetic trip setting for circuit-breaker frame sizes 250 A and larger.

c. Lockable Handle: Accepts three padlocks and interlocks with cover in closed position.

Retain one or both of first two subparagraphs below. Retain first subparagraph if external control power is used or for remote indication of disconnecting means position. Retain second subparagraph for remote indication of tripped condition. If retaining auxiliary and alarm contacts, indicate "a" and "b" contact quantities and NO or NC contact requirements on Drawings.

d. Auxiliary contacts "a" and "b" arranged to activate with MCCB handle.

e. [NC] [NO] alarm contact that operates only when MCCB has tripped.

4. Molded-Case Switch Disconnecting Means:

a. UL 489, NEMA AB 1, and NEMA AB 3, with in-line fuse block for Class J or L power fuses (depending on ampere rating), providing an interrupting capacity to comply with available fault currents; MCCB with fixed, high-set instantaneous trip only.

b. Lockable Handle: Accepts three padlocks and interlocks with cover in closed position.

Retain one or both subparagraphs below. Retain first subparagraph if external control power is used or for remote indication of disconnecting means position. Retain second subparagraph for remote indication of tripped condition. If retaining auxiliary and alarm contacts, indicate "a" and "b" contact quantities and NO or NC contact requirements on Drawings.

c. Auxiliary contacts "a" and "b" arranged to activate with molded-case switch handle.

d. [NC] [NO] alarm contact that operates only when molded-case switch has tripped.

E. Control Power:

1. Control Circuits: [24] [120] <Insert value>-V ac; obtained from [integral CPT, with primary and secondary fuses] <Insert source of control power>, with [CPT] [control power source] of sufficient capacity to operate integral devices and remotely located pilot, indicating, and control devices.

Retain "CPT Spare Capacity" Subparagraph below if retaining "CPT" option in "Control Circuits" Subparagraph above and spare CPT capacity is required. Spare capacity is usually available in 100-VA increments. Consult manufacturers for maximum spare capacity and available CPT sizes for different NEMA and enclosure sizes because adding spare capacity and an oversized CPT may require using an enlarged enclosure.

a. CPT Spare Capacity: [50] [100] [200] <Insert value> VA.

2.5 FEEDER-TAP UNITS

Not all manufacturers offer all options in this article. Coordinate with manufacturers for available selections. Coordinate selection of the disconnecting means and OCPD with short-circuit current ratings required for Project. See "Main- and Feeder-Tap Disconnecting and Overcurrent Protective Devices" Article and Editing Instructions No. 5, No. 6, and No. 9 in the Evaluations for guidance on making selections.

A. MCCB: Comply with UL 489, with [series-connected rating] [interrupting capacity] to meet available fault currents.

1. Thermal-Magnetic Circuit Breakers: Inverse time-current element for low-level overloads, and instantaneous magnetic trip element for short circuits. Adjustable magnetic trip setting for circuit-breaker frame sizes 250 A and larger.

2. Adjustable Instantaneous-Trip Circuit Breakers: Magnetic trip element with front-mounted, field-adjustable trip setting.

3. Electronic trip circuit breakers with rms sensing; field-replaceable rating plug or field-replicable electronic trip; and the following field-adjustable settings:

Retain one or more of first four subparagraphs below; coordinate required adjustable settings with Section 260573 "Overcurrent Protective Device Coordination Study." See "Electronic rms Trip versus MCCBs and ICCBs" Paragraph in "Main- and Feeder-Tap Disconnecting and Overcurrent Protective Devices" Article in the Evaluations for additional guidance on specifying full -or standard-function features.

a. Instantaneous trip.

b. Long- and short-time pickup levels.

c. Long- and short-time time adjustments.

d. Ground-fault pickup level, time delay, and I2t response.

4. MCCB Features and Accessories:

Not all accessories and options listed in subparagraphs below are available for every rating and from every listed manufacturer. Verify, with manufacturers, availability and unique characteristics.

a. Standard frame sizes, trip ratings, and number of poles.

See Editing Instruction No. 14 in the Evaluations for guidance on using mechanical vs. compression lugs.

b. Lugs: [Mechanical] [Compression] style, suitable for number, size, trip ratings, and conductor material.

c. Application Listing: Appropriate for application; Type SWD for switching fluorescent lighting loads; Type HID for feeding fluorescent and high-intensity discharge (HID) lighting circuits.

Retain first option in "Ground-Fault Protection" Subparagraph below for solid-state trip units; retain second option for thermal-magnetic trip units. If retaining second option, also retain "Shunt Trip" Subparagraph below.

d. Ground-Fault Protection: [Integrally mounted] [Remote-mounted] relay and trip unit with adjustable pickup and time-delay settings, push-to-test feature, and ground-fault indicator.

e. Shunt Trip: 120-V trip coil energized from separate circuit, set to trip at [55] [75] percent of rated voltage.

f. Auxiliary Contacts: [One SPDT switch] [Two SPDT switches] with "a" and "b" contacts; "a" contacts mimic circuit-breaker contacts, "b" contacts operate in reverse of circuit-breaker contacts.

B. Fusible Switch: NEMA KS 1, Type HD, clips to accommodate specified fuses with lockable handle.

C. Fuses are specified in Section 262813 "Fuses."

2.6 INSTRUMENTATION

Retain this article for Owner, not utility, metering.

A. Instrument Transformers: IEEE C57.13, NEMA EI 21.1, and the following:

PTs are not frequently needed, as most digital meters can be direct-bus connected up to 600 V. Consult manufacturers on need for PTs for instruments and meters. Indicate the primary-to-secondary ratio on Drawings.

1. PTs: IEEE C57.13; 120 V, 60 Hz, [single] [tapped] [double] secondary; disconnecting type with integral fuse mountings. Burden and accuracy shall be consistent with connected metering and relay devices.

Coordinate "Current Transformers" Subparagraph below with Drawings and indicate specific accuracy classes and burdens required for each application and the primary-to-secondary ratio.

2. Current Transformers: IEEE C57.13; 5 A, 60 Hz, secondary; [wound] [bushing] [bar or window] type; [single] [double] secondary winding and secondary shorting device. Burden and accuracy shall be consistent with connected metering and relay devices.

Manufacturers typically size CPTs and normally only for equipment and devices integral to MCCs. Consider specifying additional spare capacity if required for operation of remote devices.

3. CPTs: Dry type, mounted in separate compartments for units larger than 3 kVA.

Retain "Multifunction Digital-Metering Monitor" Paragraph below if digital metering is required. Digital metering offers substantially more capabilities than analog metering in much smaller packages; however, some facility managers still prefer analog devices with large, easy-to-read dials.

B. Multifunction Digital-Metering Monitor: Microprocessor-based unit suitable for three- or four-wire systems and with the following features:

1. Listed or recognized by a nationally recognized testing laboratory.

2. Inputs from sensors or 5-A current-transformer secondaries, and potential terminals rated to 600 V.

3. Switch-selectable digital display of the following values with the indicated maximum accuracy tolerances:

a. Phase Currents, Each Phase: Plus or minus 1 percent.

b. Phase-to-Phase Voltages, Three Phase: Plus or minus 1 percent.

c. Phase-to-Neutral Voltages, Three Phase: Plus or minus 1 percent.

d. Three-Phase Real Power (Megawatts): Plus or minus 2 percent.

e. Three-Phase Reactive Power (Megavars): Plus or minus 2 percent.

f. Power Factor: Plus or minus 2 percent.

g. Frequency: Plus or minus 0.5 percent.

h. Accumulated Energy, Megawatt Hours: Plus or minus 2 percent; accumulated values unaffected by power outages up to 72 hours.

4. Mounting: Display and control unit flush or semiflush mounted in instrument compartment door.

Retain two paragraphs below if analog metering functions are required in lieu of multifunction digital meters specified above.

C. Ammeters, Voltmeters, and Power-Factor Meters: ANSI C39.1.

1. Meters: 4-inch (100-mm) diameter or 6 inches (150 mm) square, flush or semiflush, with antiparallax 250-degree scale and external zero adjustment.

2. Voltmeters: Cover an expanded-scale range of nominal voltage plus 10 percent.

D. Instrument Switches: Rotary type with off position.

1. Voltmeter Switches: Permit reading of all phase-to-phase voltages and phase-to-neutral voltages where a neutral is included.

2. Ammeter Switches: Permit reading of current in each phase and maintain current-transformer secondaries in a closed-circuit condition at all times.

2.7 MCC CONTROL POWER

Retain "Control Circuits" paragraph below if MCCs require control power for metering and central-control units not associated with combination controllers.

A. Control Circuits: 120-V ac, supplied through secondary disconnecting devices from CPT.

2.8 ENCLOSURES

See "Enclosures" Article in the Evaluations for discussion of enclosure types. Coordinate paragraphs below with Drawings by identifying the designated areas on plans or by including the required enclosure types. Enclosure materials and finishes may be added to the Section Text. Availability of some enclosure types is limited by type and rating of MCCs; special accommodations and accessories (e.g., powered/filtered ventilation) may be required for some enclosure types, especially those with solid-state controllers. Consult manufacturers for availability of and limitations on enclosures other than NEMA 250, Type 1. MCCs are not usually available in explosion-proof enclosures.

A. Enclosures: Freestanding steel cabinets unless otherwise indicated. NEMA 250, [Type 1] [Type 1A] [Type 2] [Type 12] unless otherwise indicated to comply with environmental conditions at installed location.

Retain "Space Heaters" Paragraph below if required for MCCs installed in unconditioned indoor spaces.

B. Space Heaters: Factory-installed electric space heaters of sufficient wattage in each vertical section to maintain enclosure temperature above expected dew point.

1. Space-Heater Control: [Thermostats to maintain temperature of each section above expected dew point] [Manual switching of branch-circuit protective device].

2. Space-Heater Power Source: [Transformer, factory installed in MCC] [120-V external branch circuit].

Custom colors are normally available as an option. Coordinate with Architect or Owner to determine if a special color is required.

C. Enclosure Finish: Factory-applied finish in manufacturer's [standard gray] [custom color] finish over a rust-inhibiting primer on treated metal surface.

D. Compartments: Modular; individual [lift-off ]doors with concealed hinges and quick-captive screw fasteners. Interlocks on units requiring disconnecting means in off position before door can be opened or closed, except by operating a permissive release device.

E. Interchangeability: Compartments constructed to allow for removal of units without opening adjacent doors, disconnecting adjacent compartments, or disturbing operation of other units in MCC; same size compartments to permit interchangeability and ready rearrangement of units, such as replacing three single units with a unit requiring three spaces, without cutting or welding.

F. Wiring Spaces:

1. Vertical wireways in each vertical section for vertical wiring to each unit compartment; supports to hold wiring in place.

2. Horizontal wireways in [bottom] [top] [bottom and top] of each vertical section for horizontal wiring between vertical sections; supports to hold wiring in place.

2.9 AUXILIARY DEVICES

Retain applicable accessories below. Indicate requirements for and quantities of accessories on Drawings. See "Accessories" Article in the Evaluations for additional guidance; consult manufacturers for availability of and limitations on other accessories.

A. General Requirements for Control-Circuit and Pilot Devices: NEMA ICS 5; factory installed in controller enclosure cover unless otherwise indicated.

1. Push Buttons, Pilot Lights, and Selector Switches: [Heavy] [Standard]-duty, [oiltight] type.

a. Push Buttons: [Covered] [Lockable] [Recessed] [Shielded] [Shrouded] [Unguarded] types; [maintained] [momentary] contact unless otherwise indicated.

b. Pilot Lights: [Incandescent] [LED] [Neon] [Resistor] [Transformer] types; <Insert color(s)>[; push to test].

c. Selector Switches: [Rotary] <Insert description> type.

2. Elapsed Time Meters: Heavy duty with digital readout in hours[; nonresettable] [; resettable].

Retain "Meters" Subparagraph below if metering (for amperes, voltage, frequency, watts, power factor, etc.) is required for controllers. Indicate on Drawings where and which types of metering and selector switches are required. Normally, metering is limited to enclosure Types 1 and 12; consult manufacturers on availability of meters in other types of enclosures. Some listed manufacturers offer digital metering through the communications output of the solid-state overload relays; consult manufacturers for availability.

3. Meters: Panel type, 2-1/2-inch (64-mm) minimum size with 90- or 120-degree scale and plus or minus 2 percent accuracy with selector switches having an off position.

B. [NC] [NO] [Reversible NC/NO] contactor auxiliary contact(s).

C. Control Relays: Auxiliary and adjustable [pneumatic] [solid-state] time-delay relays.

Features in "Phase-Failure, Phase-Reversal, and Undervoltage and Overvoltage Relays" Paragraph below are available in individual relays or combined into a single multipurpose relay. Consult manufacturers for availability. Consider specifying phase-failure relays for single-phasing protection in fusible-switch combination controllers if solid-state overload relays are not specified.

D. Phase-Failure, Phase-Reversal, and Undervoltage and Overvoltage Relays: Solid-state sensing circuit with isolated output contacts for hard-wired connections. Provide adjustable undervoltage, overvoltage, and time-delay settings.

E. Space heaters, with NC auxiliary contacts, to mitigate condensation in enclosures installed outdoors or in unconditioned interior spaces subject to humidity and temperature swings.

F. Terminals for connecting power factor correction capacitors to the [line] [load] side of overload relays.

Retain "Spare-Fuse Cabinet" Paragraph below if using fuses for power or control circuits.

G. Spare-Fuse Cabinet: Identified [and compartmented steel box] [cabinet with hinged lockable door].

H. <Insert auxiliary device>.

2.10 CHARACTERISTICS AND RATINGS

NEMA ICS 18 recommends that the information in this article, as a minimum, be provided for manufacturers to adequately and correctly design and furnish an MCC.

Retain one of two "Wiring" paragraphs below to denote MCC wiring class. Retain one "Type" option to denote MCC wiring type. See "Classification of MCCs" Article in the Evaluations for a discussion of alternatives.

A. Wiring: NEMA ICS 18, [Class I] [Class I-S], [Type A] [Type B, for starters above Size 3] [Type B-D, for starter Size 3 and below] [Type B-T, for starter Size 3 and below].

B. Wiring: NEMA ICS 18, [Class II] [Class II-S], [Type B, for starters above Size 3] [Type B-D, for starter Size 3 and below] [Type B-T, for starter Size 3 and below].

Retain "Control and Load Wiring" Paragraph below for Type B in either "Wiring" Paragraph.

C. Control and Load Wiring: Factory installed, with bundling, lacing, and protection included. Provide flexible conductors for No. 8 AWG and smaller, for conductors across hinges, and for conductors for interconnections between shipping units.

Retain one of three "Nominal System Voltage" paragraphs below to denote MCC voltage rating. Retain first option in first or second paragraph when MCC has no phase-to-neutral connections and is not used as service equipment; retain second option when MCC has phase-to-neutral connections or is used as service equipment, or both.

D. Nominal System Voltage: [480 V, three phase, three wire] [480Y/277 V, three phase, four wire].

E. Nominal System Voltage: [208 V, three phase, three wire] [208/120 V, three phase, four wire].

F. Nominal System Voltage: <Insert voltage and phasing>.

An MCC's short-circuit current rating and the ratings of its included units are based on a variety of conditions. See Editing Instruction No. 4 in the Evaluations for guidance on revising first two paragraphs below. Retain "Short-Circuit Current Rating for Each Unit" Paragraph below for MCCs without main overcurrent devices or used in series with upstream current-limiting overcurrent devices; retain "Short-Circuit Current Rating of MCC" Paragraph for MCCs with integral current-limiting main overcurrent devices. Although NEMA ICS 18 and UL 845 list short-circuit current ratings from 5 to 100 kA, listed manufacturers seldom, if ever, offer MCCs or units rated below 22 kA. Not all available ratings are included in these two paragraphs; consult manufacturers for available options.

G. Short-Circuit Current Rating for Each Unit: [Combination series rated] [Fully rated]; [22] [42] [65] [100] <Insert value> kA.

H. Short-Circuit Current Rating of MCC: [Combination series rated] [Fully rated] with its main overcurrent device; [22] [42] [65] [100] <Insert value> kA.

I. Environmental Ratings:

MCCs are available that are suitable for use under environmental conditions different than those indicated in four subparagraphs below, which are based on "normal service conditions" specified in UL 845. However, derating, special modifications, or both, may be required, especially if installing solid-state controllers. Consult manufacturers to accommodate unusual service conditions.

1. Ambient Temperature Rating: Not less than 0 deg F (minus 18 deg C) and not exceeding 104 deg F (40 deg C), with an average value not exceeding 95 deg F (35 deg C) over a 24-hour period.

2. Ambient Storage Temperature Rating: Not less than minus 4 deg F (minus 20 deg C) and not exceeding 140 deg F (60 deg C)
3. Humidity Rating: Less than 95 percent (noncondensing).

4. Altitude Rating: Not exceeding 6600 feet (2000 m), or 3300 feet (1000 m) if MCC includes solid-state devices.

Options in "Main-Bus Continuous Rating" Paragraph below are "preferred" ratings from UL 845, with 600 A being the lowest permissible rating.

J. Main-Bus Continuous Rating: [600] [800] [1000] [1200] [1600] [2000] <Insert value> A.

UL 845 lists bus short-circuit current ratings (also called "bus bracing" in manufacturers' literature) from 22 to 200 kA, but the upper limit in NEMA ICS 18 is 100 kA. These values can exceed the individual unit ratings if the MCC rating is based on a series rating. Retain first option in "Horizontal and Vertical Bus Bracing (Short-Circuit Current Rating)" Paragraph below unless a bus rating greater than the MCC short-circuit current rating is required.

K. Horizontal and Vertical Bus Bracing (Short-Circuit Current Rating): [Match MCC short-circuit current rating] <Insert ampere rating>.

In "Main Horizontal and Equipment Ground Buses" Paragraph below, indicate location of future extensions on Drawings if not retaining first option.

L. Main Horizontal and Equipment Ground Buses: Uniform capacity for entire length of MCC's main and vertical sections. Provide for future extensions[ from both ends].[ Brace bus extensions for busway feeder bus.]

M. Vertical Phase and Equipment Ground Buses: Uniform capacity for entire usable height of vertical sections, except for sections incorporating single units.

Retain one of two "Phase- [and Neutral-]Bus Material" paragraphs below for bus material.

N. Phase-[ and Neutral-]Bus Material: Hard-drawn copper of 98 percent conductivity, [silver] [tin] plated.

O. Phase-[ and Neutral-]Bus Material: Tin-plated, high-strength, electrical-grade aluminum alloy.

Neutral buses, when required, can be reduced in size if a substantial portion of the loads are balanced three-phase types (e.g., motors and transformers). See "Neutral buses" Paragraph in "Accessory Components and Features" Article in the Evaluations. Retain one of two "Neutral Buses" paragraphs below or delete both for three-phase, three-wire systems.

P. Neutral Buses: 50 percent of the ampacity of phase buses unless otherwise indicated, equipped with [mechanical] [compression] connectors for outgoing circuit neutral cables.[ Brace bus extensions for busway feeder neutral bus.]

Q. Neutral Buses: 100 percent of the ampacity of phase buses unless otherwise indicated, equipped with [mechanical] [compression] connectors for outgoing circuit neutral cables.[ Brace bus extensions for busway feeder neutral bus.]

R. Ground Bus: [Minimum size required by UL 845] <Insert size>, hard-drawn copper of 98 percent conductivity, equipped with [mechanical] [compression] connectors for feeder and branch-circuit equipment grounding conductors.[ For busway feeders, extend insulated equipment grounding cable to busway ground connection and support cable at intervals in vertical run.]

S. Front-Connected, Front-Accessible MCCs:

1. Main Devices: [Drawout] [Fixed] mounted.

2. Controller Units: [Drawout] [and] [fixed] mounted.

3. Feeder-Tap Units: [Drawout] [and] [fixed] mounted.

4. Sections front and rear aligned.

A pull box across the entire top of an MCC is usually only required for very many outgoing feeders and across the main incoming section for very large feeders with multiple large conductors per phase and neutral (if used). Indicate the presence and extent of pull boxes on Drawings.

T. Pull Box on Top of MCC:

1. Adequate ventilation to maintain temperature in pull box within same limits as MCC.

Retain first subparagraph below for top-mounted, circuit-breaker removal mechanism.

2. Set back from front to clear circuit-breaker removal mechanism.

3. Removable covers forming top, front, and sides. Top covers at rear easily removable for drilling and cutting.

4. Insulated bottom of fire-resistive material with separate holes for cable drops into MCC.

5. Cable supports arranged to facilitate cabling and adequate to support cables, including those for future installation.

Retain "Future Devices" Paragraph below to require provisions for future expansion.

U. Future Devices: Equip compartments with mounting brackets, supports, bus connections, and appurtenances at full rating of unit.

2.11 SOURCE QUALITY CONTROL

A. MCC Testing: Inspect and test MCCs according to requirements in [NEMA ICS 18] <Insert standard>.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

B. MCCs will be considered defective if they do not pass tests and inspections.

C. Prepare test and inspection reports.

PART 3 -  EXECUTION

3.1 INSTALLATION

Retain "Floor-Mounting Controllers" Paragraph below for equipment supported on concrete bases attached to concrete slabs. If installing MCCs on concrete bases, ensure that main and compartment disconnect operating handles will not be higher than 79 inches (2000 mm) above finished floor.

A. Floor-Mounting Controllers: Install MCCs on 4-inch (100-mm) nominal thickness concrete base. Comply with requirements for concrete base specified in [Section 033000 "Cast-in-Place Concrete."] [Section 033053 "Miscellaneous Cast-in-Place Concrete."]

1. Install dowel rods to connect concrete base to concrete floor. Unless otherwise indicated, install dowel rods on 18-inch (450-mm) centers around the full perimeter of concrete base.

2. For supported equipment, install epoxy-coated anchor bolts that extend through concrete base and anchor into structural concrete floor.

3. Place and secure anchorage devices. Use setting drawings, templates, diagrams, instructions, and directions furnished with items to be embedded.

4. Install anchor bolts to elevations required for proper attachment to supported equipment.

Retain "Seismic Bracing" Paragraph below if seismic controls are Project requirement. Coordinate with Drawings and Sections specifying vibration and seismic controls.

B. Seismic Bracing: Comply with requirements specified in Section 260548.16 "Seismic Controls for Electrical Systems."

C. Temporary Lifting Provisions: Remove temporary lifting eyes, channels, and brackets and temporary blocking of moving parts from enclosures and components.

Coordinate first five paragraphs below with product descriptions.

D. Install fuses in each fusible switch.

E. Install fuses in control circuits if not factory installed. Comply with requirements in Section 262813 "Fuses."

F. Install heaters in thermal-overload relays. Select heaters based on actual nameplate full-load amperes after motors have been installed.

G. Install, connect, and fuse thermal-protector monitoring relays furnished with motor-driven equipment.

H. Install power factor correction capacitors. Connect to the [line] [load] side of overload relays. If connected to the load side of overload relays, adjust overload heater sizes to accommodate the reduced motor full-load currents.

I. Comply with NECA 1.

3.2 IDENTIFICATION

A. Comply with requirements in Section 260553 "Identification for Electrical Systems" for identification of MCC, MCC components, and control wiring.

1. Identify field-installed conductors, interconnecting wiring, and components; provide warning signs.

2. Label MCC and each cubicle with engraved nameplate.

3. Label each enclosure-mounted control and pilot device.

3.3 CONTROL WIRING INSTALLATION

Retain this article if remote control or remote status indication is required. Coordinate options retained with wiring type(s) retained in Part 2.

A. Install wiring between [enclosed controllers] [master terminal boards] and remote devices[ and facility's BAS] [ and facility's central-control system]. Comply with requirements in Section 260523 "Control-Voltage Electrical Power Cables."

B. Bundle, train, and support wiring in enclosures.

C. Connect selector switches and other automatic-control selection devices where applicable.

1. Connect selector switches to bypass only those manual- and automatic-control devices that have no safety functions when switch is in manual-control position.

2. Connect selector switches within enclosed controller circuit in both manual and automatic positions for safety-type control devices such as low- and high-pressure cutouts, high-temperature cutouts, and motor overload protectors.

3.4 CONNECTIONS

Coordinate conduit installations and specialty arrangements with schematics on Drawings and with requirements specified. If Drawings are explicit enough, these requirements may be reduced or omitted.

A. Comply with requirements for installation of conduit in Section 260533 "Raceways and Boxes for Electrical Systems." Drawings indicate general arrangement of conduit, fittings, and specialties.

B. Comply with requirements in Section 260526 "Grounding and Bonding for Electrical Systems."

3.5 FIELD QUALITY CONTROL

See Editing Instruction No. 15 in the Evaluations for guidance on the level of field quality control that would be appropriate for Project. Retain one of first two paragraphs below to identify who shall perform tests and inspections. If retaining second option in first paragraph, or if retaining second paragraph, retain "Field quality-control reports" Paragraph in "Informational Submittals" Article.

A. Testing Agency: [Owner will engage] [Engage] a qualified testing agency to perform tests and inspections.

Retain first paragraph below to require Contractor to perform tests and inspections.

B. Perform tests and inspections.

Retain first two paragraphs below to describe tests and inspections to be performed.

C. Acceptance Testing Preparation:

1. Test insulation resistance for each enclosed controller, component, connecting supply, feeder, and control circuit.

2. Test continuity of each circuit.

D. Tests and Inspections:

1. Inspect controllers, wiring, components, connections, and equipment installation.[ Test and adjust controllers, components, and equipment.]

2. Test insulation resistance for each enclosed controller element, component, connecting motor supply, feeder, and control circuits.

3. Test continuity of each circuit.

4. Verify that voltages at controller locations are within 10 percent of motor nameplate rated voltages. If outside this range for any motor, notify [Architect] [Construction Manager] [Owner] before starting the motor(s).

5. Test each motor for proper phase rotation.

6. Perform each electrical test and visual and mechanical inspection stated in NETA Acceptance Testing Specification. Certify compliance with test parameters.

7. Correct malfunctioning units on-site, where possible, and retest to demonstrate compliance; otherwise, replace with new units and retest.

8. Test and adjust controls, remote monitoring, and safeties. Replace damaged and malfunctioning controls and equipment.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

E. Enclosed controllers will be considered defective if they do not pass tests and inspections.

Retain paragraph below if tests and inspections are performed by Contractor or manufacturer's field-service representative engaged by Contractor.

F. Prepare test and inspection reports, including a certified report that identifies enclosed controllers and that describes scanning results. Include notation of deficiencies detected, remedial action taken, and observations after remedial action.

3.6 ADJUSTING

Retain applicable paragraphs below to correspond to selections made in Part 2.

A. Set field-adjustable switches, auxiliary relays, time-delay relays, timers, and overload-relay pickup and trip ranges.

B. Adjust overload relay heaters or settings if power factor correction capacitors are connected to the load side of the overload relays.

C. Adjust the trip settings of MCPs and thermal-magnetic circuit breakers with adjustable, instantaneous trip elements. Initially adjust to six times the motor nameplate full-load amperes and attempt to start motors several times, allowing for motor cool-down between starts. If tripping occurs on motor inrush, adjust settings in increments until motors start without tripping. Do not exceed eight times the motor full-load amperes (or 11 times for NEMA Premium Efficient motors if required). Where these maximum settings do not allow starting of a motor, notify [Architect] [Construction Manager] [Owner] before increasing settings.

D. Set field-adjustable switches and program microprocessors for required start and stop sequences in reduced-voltage, solid-state controllers.

Retain option in paragraph below unless settings are included on Drawings.

E. Set field-adjustable circuit-breaker trip ranges[ as specified in Section 260573 "Overcurrent Protective Device Coordination Study."]

3.7 DEMONSTRATION

A. [Engage a factory-authorized service representative to train] [Train] Owner's maintenance personnel to adjust, operate, and maintain enclosed controllers[, and to use and reprogram microprocessor-based, reduced-voltage, solid-state controllers].

END OF SECTION 262419

	MOTOR-CONTROL CENTERS
	262419 - 1



