Copyright 2012 AIA
MasterSpec Professional
06/12

Copyright 2012 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 262713 - ELECTRICITY METERING
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section includes equipment for [electricity metering by utility company] [and] [electricity metering by Owner].

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product indicated.

B. Shop Drawings: Dimensioned plans and sections or elevation layouts and wiring diagrams.

1.3 INFORMATIONAL SUBMITTALS

A. Field quality-control reports.

1.4 CLOSEOUT SUBMITTALS

Retain paragraph below if Owner's metering includes billing software. Note that a PC is not included in this Section and, if needed, should be obtained separately.

A. Operation and Maintenance Data. In addition to items specified in Section 017823 "Operation and Maintenance Data," include the following:

1. Application and operating software documentation.

2. Software licenses.

3. Software service agreement.

4. Hard copies of manufacturer's operating specifications, design user's guides for software and hardware, and PDF files on CD-ROM of the hard-copy Submittal.

1.5 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

1.6 SOFTWARE SERVICE AGREEMENT

Services in this article may not be allowed for publicly funded projects.

Retain article if Owner's metering includes billing software. Note that a PC is not included in this Section and, if needed, should be obtained separately.

A. Technical Support: Beginning with Substantial Completion, provide software support for [two] <Insert number> years.

B. Upgrade Service: Update software to latest version at Project completion. Install and program software upgrades that become available within [two] <Insert number> years from date of Substantial Completion. Upgrading software shall include operating system. Upgrade shall include new or revised licenses for use of software.

1. Provide [30] <Insert number> days' notice to Owner to allow scheduling and access to system and to allow Owner to upgrade his computer equipment if necessary.

PART 2 -  PRODUCTS

2.1 EQUIPMENT FOR ELECTRICITY METERING BY UTILITY COMPANY

A. Meters will be furnished by utility company.

Retain and revise the remainder of this article to reflect utility company's requirements for equipment to be provided by Contractor.

B. Current-Transformer Cabinets: Comply with requirements of electrical-power utility company.

Retain one or both of first two paragraphs below. Retain both if Owner's meter is not in a modular meter center.

C. Meter Sockets: Comply with requirements of electrical-power utility company.

D. Meter Sockets: Steady-state and short-circuit current ratings shall meet indicated circuit ratings.

E. Modular Meter Center: Factory-coordinated assembly of a main service [terminal box with lugs only] [disconnect device], wireways, tenant meter socket modules, and tenant feeder circuit breakers arranged in adjacent vertical sections. Assembly shall be complete with interconnecting buses and other features as specified below.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first subparagraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Eaton Electrical Inc.; Cutler-Hammer Business Unit.

b. General Electric Company; GE Consumer & Industrial - Electrical Distribution.

c. Siemens Energy & Automation, Inc.

d. Square D; a brand of Schneider Electric.

e. <Insert manufacturer's name>.

3. Comply with requirements of utility company for meter center.

4. Housing: NEMA 250, [Type 1] [Type 3R] enclosure.

Coordinate first subparagraph below with Drawings for indication of available fault current at meter-center supply terminals.

5. Minimum Short-Circuit Rating: [22,000] [42,000] [65,000] [100,000] <Insert number> A symmetrical at rated voltage.

Retain one of first two subparagraphs below if meter center is specified to have main terminal box with main lugs. Fusible switch may require more space. Consult manufacturers' data. Coordinate with Drawings for indication of poles, frame or size, and trip or fuse.

6. Main Disconnect Device: Circuit breaker, series-combination rated for use with downstream feeder and branch circuit breakers.

7. Main Disconnect Device: Fusible switch, series-combination rated by circuit-breaker manufacturer to protect downstream feeder and branch circuit breakers.

Coordinate first subparagraph below with Drawings for indication of trip setting and interrupting capacity of circuit breakers.

8. Tenant Feeder Circuit Breakers: Series-combination-rated molded-case units, rated to protect circuit breakers in downstream tenant and to house loadcenters and panelboards that have 10,000-A interrupting capacity.

a. Identification: Complying with requirements in Section 260553 "Identification for Electrical Systems" with legend identifying tenant's address.

b. Physical Protection: Tamper resistant, with hasp for padlock.

9. Meter Socket: Rating coordinated with indicated tenant feeder circuit rating.

10. Surge Protection: For main disconnect device, comply with requirements in Section 264313 "Surge Protection for Low-Voltage Electrical Power Circuits."

2.2 EQUIPMENT FOR ELECTRICITY METERING BY OWNER

Retain this article to specify components for Owner's metering of feeders to tenants or designated loads, with or without external alarm, control, and communication capabilities, or other optional features. See Evaluations. Coordinate with Drawings.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."

A. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. E-Mon; a division of Hunt Power.

2. National Meter Industries.

3. Osaki Meter Sales, Inc.

4. Square D; a brand of Schneider Electric.

5. <Insert manufacturer's name>.

C. General Requirements for Owner's Meters:

1. Comply with UL 1244.

See Evaluations for discussion about meter accuracy.

2. Meters used for billing shall have an accuracy of [0.2] [0.5] [1.0] percent of reading, complying with requirements in ANSI C12.20.

Retain first subparagraph below if required by authorities having jurisdiction at Project location. Below may also be retained as a quality-control option even if not required by authorities having jurisdiction.

3. Meters shall be certified by [California Type Evaluation Program] <Insert agency> as complying with [Title 4, California Code of Regulations, Article 2.2] <Insert regulatory requirements>.

4. Enclosure: NEMA 250, [Type 1] [Type 3R] minimum, with hasp for padlocking or sealing.

5. Identification: Comply with requirements in Section 260553 "Identification for Electrical Systems."

6. Memory Backup: Self-contained to maintain memory throughout power outages of 72 hours, minimum.

7. Sensors: Current-sensing type, with current or voltage output, selected for optimum range and accuracy for meters indicated for this application.

Split-core sensor in first subparagraph below is installed in switchboard or panelboard without disturbing feeder connection but is less accurate. Solid-core sensor is usually installed in a separate compartment or in a separate current-transformer cabinet. Coordinate with Drawings.

a. Type: [Split] [and] [solid] core.

Current-transformer cabinet in subparagraph below may be required for some solid-core current sensors. Consult manufacturers' literature. Coordinate with Drawings.

8. Current-Transformer Cabinet: Listed or recommended by metering equipment manufacturer for use with sensors indicated.

D. Kilowatt-hour Meter: Electronic [single] [three] [single- and three]-phase meters, measuring electricity used.

1. Voltage and Phase Configuration: Meter shall be designed for use on circuits with voltage rating and phase configuration indicated for its application.

Retain one of two subparagraphs below.

2. Display: LCD with characters not less than 0.25 inch (6 mm) high, indicating accumulative kilowatt-hours and current kilowatt load. Retain accumulated kilowatt-hour in a nonvolatile memory, until reset.

3. Display: Digital electromechanical counter, indicating accumulative kilowatt-hours.

The demand interval in first paragraph below should be same as used by the utility.

E. Kilowatt-hour/Demand Meter: Electronic [single] [three] [single- and three]-phase meters, measuring electricity use and demand. Demand shall be integrated over a [15-minute] <Insert value> interval.

1. Voltage and Phase Configuration: Meter shall be designed for use on circuits with voltage rating and phase configuration indicated for its application.

2. Display: LCD with characters not less than 0.25 inch (6 mm) high, indicating accumulative kilowatt-hours, [current time and date, ]current demand,[ and] historic peak demand[, and time and date of historic peak demand]. Retain accumulated kilowatt-hour and historic peak demand in a nonvolatile memory, until reset.

F. Data Transmission Cable: Transmit KY pulse data over Class 1 control-circuit conductors in raceway. Comply with Section 260523 "Control-Voltage Electrical Power Cables."

See Evaluations for discussion about using metered data for allocation of utility costs.

G. Software: PC based, a product of meter manufacturer, suitable for calculation of utility cost allocation[ and billing].

1. Utility Cost Allocation: Automatically import energy-usage records to allocate energy costs for the following:

a. At least [15] <Insert number> departments.

b. At least [30] <Insert number> tenants.

c. At least [five] <Insert number> processes.

d. At least [five] <Insert number> buildings.

e. <Insert entity>.

2. Tenant or Activity Billing Software: Automatically import energy-usage records to automatically compute and prepare [tenant bills] [activity demand and energy-use statements] based on metering of energy use[ and peak demand]. Maintain separate directory for each tenant's historical billing information. Prepare summary reports in user-defined formats and time intervals.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Comply with equipment installation requirements in NECA 1.

Retain first paragraph below to require installation of utility company's equipment. Coordinate with Drawings. Revise to suit utility company's requirements.

B. Install meters furnished by utility company. Install raceways and equipment according to utility company's written requirements. Provide empty conduits for metering leads and extend grounding connections as required by utility company.

Retain first paragraph below if modular meter center is specified.

C. Install modular meter center according to NECA 400 switchboard installation requirements.

D. Comply with requirements for identification specified in Section 260553 "Identification for Electrical Systems."

1. Series Combination Warning Label: Self-adhesive type, with text as required by NFPA 70.

2. Equipment Identification Labels: Adhesive film labels with clear protective overlay. For residential meters, provide an additional card holder suitable for [printed, weather-resistant card] [typewritten card] with occupant's name.

3.2 FIELD QUALITY CONTROL

Retain this article if Owner's electricity-metering equipment is specified.

Retain first paragraph below to require Contractor to perform tests and inspections.

A. Perform tests and inspections.

Retain first paragraph below to describe tests and inspections to be performed.

B. Tests and Inspections:

1. Connect a load of known kilowatt rating, [1.5] <Insert number> kW minimum, to a circuit supplied by metered feeder.

2. Turn off circuits supplied by metered feeder and secure them in off condition.

3. Run test load continuously for eight hours minimum, or longer, to obtain a measurable meter indication. Use test-load placement and setting that ensures continuous, safe operation.

4. Check and record meter reading at end of test period and compare with actual electricity used, based on test-load rating, duration of test, and sample measurements of supply voltage at test-load connection. Record test results.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

C. Electricity metering will be considered defective if it does not pass tests and inspections.

D. Prepare test and inspection reports.

END OF SECTION 262713

	ELECTRICITY METERING
	262713 - 1



