Copyright 2010 AIA
MasterSpec Professional
02/10

Copyright 2010 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 262726 - WIRING DEVICES
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Receptacles, receptacles with integral GFCI, and associated device plates.

2. Weather-resistant receptacles.

3. Snap switches and wall-box dimmers.

4. Solid-state fan speed controls.

5. Wall-switch and exterior occupancy sensors.

6. Communications outlets.

1.2 ADMINISTRATIVE REQUIREMENTS

Retain this article if receptacles for Owner-furnished equipment with plugs have unknown or special configurations.

A. Coordination:

1. Receptacles for Owner-Furnished Equipment: Match plug configurations.

1.3 ACTION SUBMITTALS

A. Product Data: For each type of product.

B. Shop Drawings: List of legends and description of materials and process used for premarking wall plates.

1.4 INFORMATIONAL SUBMITTALS

A. Field quality-control reports.

1.5 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

2.1 MANUFACTURERS

A.  Manufacturers' Names: Shortened versions (shown in parentheses) of the following manufacturers' names are used in other Part 2 articles:

1. Cooper Wiring Devices; Division of Cooper Industries, Inc. (Cooper).

2. Hubbell Incorporated; Wiring Device-Kellems (Hubbell).

3. Leviton Mfg. Company Inc. (Leviton).

4. Pass & Seymour/Legrand (Pass & Seymour).

5. <Insert manufacturer's name>.

B. Source Limitations: Obtain each type of wiring device and associated wall plate from single source from single manufacturer.

2.2 GENERAL WIRING-DEVICE REQUIREMENTS

A. Wiring Devices, Components, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

B. Comply with NFPA 70.

Not all standard devices are available with a modular plug-in configuration. For example, this Section does not include specifications for modular devices.

C. Devices that are manufactured for use with modular plug-in connectors may be substituted under the following conditions:

1. Connectors shall comply with UL 2459 and shall be made with stranding building wire.

2. Devices shall comply with the requirements in this Section.

2.3 STRAIGHT-BLADE RECEPTACLES

A. Convenience Receptacles, 125 V, 20 A: Comply with NEMA WD 1, NEMA WD 6 Configuration 5-20R, UL 498, and FS W-C-596.

Retain "Products" Subparagraph and list of manufacturers and products below to require specific products or a comparable product from other manufacturers.

1. Products: Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Cooper; 5351 (single), CR5362 (duplex).

b. Hubbell; HBL5351 (single), HBL5352 (duplex).

c. Leviton; 5891 (single), 5352 (duplex).

d. Pass & Seymour; 5361 (single), 5362 (duplex).

e. <Insert manufacturer's name; catalog number(s)>.

2.4 GFCI RECEPTACLES

Non-feed-through-type GFCI unit shall be selected where no protection of downstream receptacles is required.

A. General Description:

1. Straight blade, [feed] [non-feed]-through type.

2. Comply with NEMA WD 1, NEMA WD 6, UL 498, UL 943 Class A, and FS W-C-596.

3. Include indicator light that shows when the GFCI has malfunctioned and no longer provides proper GFCI protection.

B. Duplex GFCI Convenience Receptacles, 125 V, 20 A:

Retain "Products" Subparagraph and list of manufacturers and products below to require specific products or a comparable product from other manufacturers.

1. Products: Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Cooper; VGF20.

b. Hubbell; GFR5352L.

c. Pass & Seymour; 2095.

d. Leviton; 7590.

e. <Insert manufacturer's name; catalog number(s)>.

2.5 TOGGLE SWITCHES

A. Comply with NEMA WD 1, UL 20, and FS W-S-896.

B. Switches, 120/277 V, 20 A:

Retain "Products" Subparagraph and list of manufacturers and products below to require specific products or a comparable product from other manufacturers.

1. Products: Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

Catalog numbers in lists below are for 20-A devices; revise catalog numbers to require other configurations and ratings.

1) Single Pole:

2) 
Cooper; AH1221.

3) Hubbell; HBL1221.

4) Leviton; 1221-2.

5) Pass & Seymour; CSB20AC1.

6) <Insert manufacturer's name; catalog number(s)>.

7) Two Pole:

8) 
Cooper; AH1222.

9) Hubbell; HBL1222.

10) Leviton; 1222-2.

11) Pass & Seymour; CSB20AC2.

12) <Insert manufacturer's name; catalog number(s)>.

13) Three Way:

14) 
Cooper; AH1223.

15) Hubbell; HBL1223.

16) Leviton; 1223-2.

17) Pass & Seymour; CSB20AC3.

18) <Insert manufacturer's name; catalog number(s)>.

19) Four Way:

20) 
Cooper; AH1224.

21) Hubbell; HBL1224.

22) Leviton; 1224-2.

23) Pass & Seymour; CSB20AC4.

24) <Insert manufacturer's name; catalog number(s)>.

C. Pilot-Light Switches, 20 A:

Retain "Products" Subparagraph and list of manufacturers and products below to require specific products or a comparable product from other manufacturers.

1. Products: Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Cooper; AH1221PL for 120 and 277 V.

b. Hubbell; HBL1201PL for 120 and 277 V.

c. Leviton; 1221-LH1.

d. Pass & Seymour; PS20AC1RPL for 120 V, PS20AC1RPL7 for 277 V.

e. <Insert manufacturer's name; catalog number(s)>.

2. Description: Single pole, with neon-lighted handle, illuminated when switch is "off."

D. Key-Operated Switches, 120/277 V, 20 A:

Retain "Products" Subparagraph and list of manufacturers and products below to require specific products or a comparable product from other manufacturers.

1. Products: Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Cooper; AH1221L.

b. Hubbell; HBL1221L.

c. Leviton; 1221-2L.

d. Pass & Seymour; PS20AC1-L.

e. <Insert manufacturer's name; catalog number(s)>.

2. Description: Single pole, with factory-supplied key in lieu of switch handle.

2.6 DECORATOR-STYLE DEVICES

Convenience receptacles in this article are commercial grade, 15 A, duplex.

A. Convenience Receptacles: Square face, 125 V, 15 A; comply with NEMA WD 1, NEMA WD 6 Configuration 5-15R, and UL 498.

Retain "Products" Subparagraph and list of manufacturers and products below to require specific products or a comparable product from other manufacturers.

1. Products: Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Cooper; 6252.

b. Hubbell; DR15.

c. Leviton; 16252.

d. Pass & Seymour; 26252.

e. <Insert manufacturer's name; catalog number(s)>.

B. GFCI, [Feed] [Non-Feed]-Through Type, Convenience Receptacles: Square face, 125 V, 15 A; comply with NEMA WD 1, NEMA WD 6 Configuration 5-15R, UL 498, and UL 943 Class A.

Retain "Products" Subparagraph and list of manufacturers and products below to require specific products or a comparable product from other manufacturers.

1. Products: Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Cooper; VGF15.

b. Hubbell; GF15LA.

c. Leviton; 8599.

d. Pass & Seymour; 1594.

e. <Insert manufacturer's name; catalog number(s)>.

C. Toggle Switches, Square Face, 120/277 V, 15 A: Comply with NEMA WD 1, UL 20, and FS W-S-896.

Retain "Products" Subparagraph and list of manufacturers and products below to require specific products or a comparable product from other manufacturers.

1. Products: Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Cooper; 7621 (single pole), 7623 (three way).

b. Hubbell; DS115 (single pole), DS315 (three way).

c. Leviton; 56291-2 (single pole), 5623-2 (three way).

d. Pass & Seymour; 2621 (single pole), 2623 (three way).

e. <Insert manufacturer's name; catalog number(s)>.

D. Lighted Toggle Switches, Square Face, 120 V, 15 A: Comply with NEMA WD 1 and UL 20.

Retain "Products" Subparagraph and list of manufacturers and products below to require specific products or a comparable product from other manufacturers.

1. Products: Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Cooper; 7631 (single pole), 7633 (three way).

b. Hubbell; DS120IL (single pole), DS320 (three way).

c. Leviton; 5631-2 (single pole), 5633-2 (three way).

d. Pass & Seymour; 2625 (single pole), 2626 (three way).

e. <Insert manufacturer's name; catalog number(s)>.

2. Description: With neon-lighted handle, illuminated when switch is "off."

2.7 RESIDENTIAL DEVICES

Receptacles in this article are usually considered residential grade, for installation in dwelling units.

A. Fan Speed Controls:

1. Modular, 120-V, full-wave, solid-state units with integral, quiet on-off switches and audible frequency and EMI/RFI filters.

2. Comply with UL 1917.

The 5-A rating in first subparagraph below allows more than one fan to be controlled by the same device.

3. Continuously adjustable [slider] [toggle switch] [rotary knob], [5 A] [1.5 A].

4. Three-speed adjustable [slider] [rotary knob], 1.5 A.

Coordinate "Telephone Outlet" Paragraph below with Section 271500 "Communications Horizontal Cabling."

B. Telephone Outlet:

Retain "Products" Subparagraph and list of manufacturers and products below to require specific products or a comparable product from other manufacturers.

1. Products: Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Cooper; 3560-6.

b. Leviton; 40649.

c. <Insert manufacturer's name; catalog number(s)>.

In determining cable category in "Description" Subparagraph below, Category 5e and Category 6 are covered by the referenced TIA/EIA standard. Use of Category 3 cabling may be permitted by authorities having jurisdiction; however, this category is covered by an obsolete TIA/EIA standard.

2. Description: Single RJ-45 jack for terminating 100-ohm, balanced, four-pair UTP; TIA/EIA-568-B.1; complying with [Category 5e] <Insert category>. Comply with UL 1863.

C. Combination TV and Telephone Outlet:

Retain "Products" Subparagraph and list of manufacturers and products below to require specific products or a comparable product from other manufacturers.

1. Products: Subject to compliance with requirements, [provide the following] [provide one of the following] [available products that may be incorporated into the Work include, but are not limited to, the following]:

a. Cooper; 3562.

b. Leviton; 40159.

c. <Insert manufacturer's name; catalog number(s)>.

2. Description: Single RJ-45 jack for 100-ohm, balanced, four-pair UTP; TIA/EIA-568-B.1; complying with [Category 5e] <Insert category>. Comply with UL 1863.

2.8 WALL-BOX DIMMERS

A. Dimmer Switches: Modular, full-wave, solid-state units with integral, quiet on-off switches, with audible frequency and EMI/RFI suppression filters.

Four-way switching may be added to "Control" Paragraph below after verifying availability with manufacturers.

B. Control: Continuously adjustable [slider] [toggle switch] [rotary knob]; with single-pole or three-way switching. Comply with UL 1472.

C. Incandescent Lamp Dimmers: 120 V; control shall follow square-law dimming curve. On-off switch positions shall bypass dimmer module.

Retain one of two subparagraphs below. UL 1472 covers ratings from 300 to 2000 W in increments of 50 W.

1. 600 W; dimmers shall require no derating when ganged with other devices.[ Illuminated when "off."]

2. <Insert wattage ratings and descriptions>.

Retain "Fluorescent Lamp Dimmer Switches" Paragraph below with compatible dimming-type ballasts. Coordinate with Section 265100 "Interior Lighting." Use uniform ballast and lamp types to obtain consistent dimming characteristics.

D. Fluorescent Lamp Dimmer Switches: Modular; compatible with dimmer ballasts; trim potentiometer to adjust low-end dimming; dimmer-ballast combination capable of consistent dimming with low end not greater than 20 percent of full brightness.

2.9 WALL PLATES

A. Single and combination types shall match corresponding wiring devices.

1. Plate-Securing Screws: Metal with head color to match plate finish.

Third option in "Material for Finished Spaces" Subparagraph below is also available in Type 430 but is susceptible to rust and corrosion even in finished spaces.

2. Material for Finished Spaces: [Steel with white baked enamel, suitable for field painting] [Smooth, high-impact thermoplastic] [0.035-inch- (1-mm-) thick, satin-finished, Type 302 stainless steel] [0.04-inch- (1-mm-) thick, brushed brass with factory polymer finish] [0.05-inch- (1.2-mm-) thick, anodized aluminum] [0.04-inch- (1-mm-) thick steel with chrome-plated finish].

3. Material for Unfinished Spaces: [Galvanized steel] [Smooth, high-impact thermoplastic].

4. Material for Damp Locations: [Thermoplastic] [Cast aluminum] with spring-loaded lift cover, and listed and labeled for use in wet and damp locations.

B. Wet-Location, Weatherproof Cover Plates: NEMA 250, complying with Type 3R, weather-resistant[, die-cast aluminum] [thermoplastic] with lockable cover.

2.10 FINISHES

See Editing Instruction No. 2 in the Evaluations for a discussion of wiring-device colors. Coordinate with Drawings.

A. Device Color:

Retain "Wiring Devices Connected to Normal Power System" Subparagraph below unless colors are indicated or scheduled on Drawings. If retaining subparagraph, revise title if a separate emergency power system serving wiring devices is not provided.

1. Wiring Devices Connected to Normal Power System: [Almond] [Black] [Brown] [Gray] [Ivory] [White] [As selected by Architect] <Insert color> unless otherwise indicated or required by NFPA 70 or device listing.

Retain "Wiring Devices Connected to Emergency Power System" Subparagraph below if a separate emergency power system serving wiring devices is required.

2. Wiring Devices Connected to Emergency Power System: [Red] <Insert color>.

3. TVSS Devices: Blue.

B. Wall Plate Color: For plastic covers, match device color.

PART 3 -  EXECUTION

3.1 INSTALLATION

NECA 1 referenced in first paragraph below includes device mounting-height requirements. See "Mounting Heights and Locations" Article in the Evaluations for device mounting heights in that standard.

A. Comply with NECA 1, including mounting heights listed in that standard, unless otherwise indicated.

See Editing Instruction No. 4 in the Evaluations for timing and sequencing of construction to assist in avoiding contamination of devices during construction.

B. Coordination with Other Trades:

1. Protect installed devices and their boxes. Do not place wall finish materials over device boxes and do not cut holes for boxes with routers that are guided by riding against outside of boxes.

2. Keep outlet boxes free of plaster, drywall joint compound, mortar, cement, concrete, dust, paint, and other material that may contaminate the raceway system, conductors, and cables.

3. Install device boxes in brick or block walls so that the cover plate does not cross a joint unless the joint is troweled flush with the face of the wall.

4. Install wiring devices after all wall preparation, including painting, is complete.

C. Conductors:

1. Do not strip insulation from conductors until right before they are spliced or terminated on devices.

2. Strip insulation evenly around the conductor using tools designed for the purpose. Avoid scoring or nicking of solid wire or cutting strands from stranded wire.

3. The length of free conductors at outlets for devices shall meet provisions of NFPA 70, Article 300, without pigtails.

4. Existing Conductors:

a. Cut back and pigtail, or replace all damaged conductors.

b. Straighten conductors that remain and remove corrosion and foreign matter.

c. Pigtailing existing conductors is permitted, provided the outlet box is large enough.

D. Device Installation:

1. Replace devices that have been in temporary use during construction and that were installed before building finishing operations were complete.

2. Keep each wiring device in its package or otherwise protected until it is time to connect conductors.

3. Do not remove surface protection, such as plastic film and smudge covers, until the last possible moment.

4. Connect devices to branch circuits using pigtails that are not less than 6 inches (152 mm) in length.

5. When there is a choice, use side wiring with binding-head screw terminals. Wrap solid conductor tightly clockwise, two-thirds to three-fourths of the way around terminal screw.

6. Use a torque screwdriver when a torque is recommended or required by manufacturer.

7. When conductors larger than No. 12 AWG are installed on 15- or 20-A circuits, splice No. 12 AWG pigtails for device connections.

8. Tighten unused terminal screws on the device.

9. When mounting into metal boxes, remove the fiber or plastic washers used to hold device-mounting screws in yokes, allowing metal-to-metal contact.

E. Receptacle Orientation:

Retain subparagraph below if the position of the ground pin is important for consistency. Trade and professional literature is inconsistent in recommending benefits of either orientation.

1. Install ground pin of vertically mounted receptacles [up] [down], and on horizontally mounted receptacles to the [right] [left].

F. Device Plates: Do not use oversized or extra-deep plates. Repair wall finishes and remount outlet boxes when standard device plates do not fit flush or do not cover rough wall opening.

G. Dimmers:

1. Install dimmers within terms of their listing.

2. Verify that dimmers used for fan speed control are listed for that application.

3. Install unshared neutral conductors on line and load side of dimmers according to manufacturers' device listing conditions in the written instructions.

Coordinate both paragraphs below with Drawings.

H. Arrangement of Devices: Unless otherwise indicated, mount flush, with long dimension vertical and with grounding terminal of receptacles on top. Group adjacent switches under single, multigang wall plates.

I. Adjust locations of service poles to suit arrangement of partitions and furnishings.

3.2 GFCI RECEPTACLES

A. Install non-feed-through-type GFCI receptacles where protection of downstream receptacles is not required.

3.3 FIELD QUALITY CONTROL

Retain "Perform the following tests and inspections" Paragraph below to require Contractor to perform tests and inspections.

A. Perform the following tests and inspections:

1. Test Instruments: Use instruments that comply with UL 1436.

2. Test Instrument for Convenience Receptacles: Digital wiring analyzer with digital readout or illuminated digital-display indicators of measurement.

B. Tests for Convenience Receptacles:

1. Line Voltage: Acceptable range is 105 to 132 V.

2. Percent Voltage Drop under 15-A Load: A value of 6 percent or higher is unacceptable.

3. Ground Impedance: Values of up to 2 ohms are acceptable.

4. GFCI Trip: Test for tripping values specified in UL 1436 and UL 943.

5. Using the test plug, verify that the device and its outlet box are securely mounted.

6. Tests shall be diagnostic, indicating damaged conductors, high resistance at the circuit breaker, poor connections, inadequate fault current path, defective devices, or similar problems. Correct circuit conditions, remove malfunctioning units and replace with new ones, and retest as specified above.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

C. Wiring device will be considered defective if it does not pass tests and inspections.

D. Prepare test and inspection reports.

END OF SECTION 262726

	WIRING DEVICES
	262726 - 1



