Copyright 2012 AIA
MasterSpec Professional
03/12

Copyright 2012 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 262816 - ENCLOSED SWITCHES AND CIRCUIT BREAKERS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Fusible switches.

2. Nonfusible switches.

3. Receptacle switches.

4. Shunt trip switches.

5. Molded-case circuit breakers (MCCBs).

6. Enclosures.

1.2 DEFINITIONS

Retain definition(s) remaining after this Section has been edited.

A. NC: Normally closed.

B. NO: Normally open.

C. SPDT: Single pole, double throw.

1.3 PERFORMANCE REQUIREMENTS

Retain this article with "Seismic Qualification Certificates" Paragraph in "Informational Submittals" Article for projects requiring seismic design. Model building codes and ASCE/SEI 7 establish criteria for buildings subject to earthquake motions. Verify requirements of authorities having jurisdiction.

A. Seismic Performance: Enclosed switches and circuit breakers shall withstand the effects of earthquake motions determined according to [ASCE/SEI 7] <Insert requirement>.

Retain subparagraph below to define the term "withstand" as it applies to this Project. Definition varies with type of building and occupancy and is critical to valid certification. Option is used for essential facilities where equipment must operate immediately after an earthquake.

1. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified[ and the unit will be fully operational after the seismic event]."

1.4 ACTION SUBMITTALS

A. Product Data: For each type of enclosed switch, circuit breaker, accessory, and component indicated.

B. Shop Drawings: For enclosed switches and circuit breakers. Include plans, elevations, sections, details, and attachments to other work.

1. Wiring Diagrams: For power, signal, and control wiring.

1.5 INFORMATIONAL SUBMITTALS

Retain first paragraph below if required by seismic criteria applicable to Project. Coordinate with Section 260548.16 "Seismic Controls for Electrical Systems." See ASCE/SEI 7 for certification requirements for equipment and components.

A. Seismic Qualification Certificates: For enclosed switches and circuit breakers, accessories, and components, from manufacturer.

B. Field quality-control reports.

1.6 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

1.7 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

B. Comply with NFPA 70.

PART 2 -  PRODUCTS

2.1 FUSIBLE SWITCHES

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."

A. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Eaton Electrical Inc.; Cutler-Hammer Business Unit.

2. General Electric Company; GE Consumer & Industrial - Electrical Distribution.

3. Siemens Energy & Automation, Inc.

4. Square D; a brand of Schneider Electric.

5. <Insert manufacturer's name>.

Show pole quantities and voltage and ampere ratings of switches on Drawings. In first two paragraphs below, Type GD is for switches for light-commercial applications, 240-V ac, 30 to 600 A; Type HD is for all other single-throw switch uses. See Editing Instruction No. 2 in the Evaluations.

Retain one of last two options in first paragraph below depending on whether fuse applications and class designations are indicated on Drawings or specified in Section 262813 "Fuses." Show fuse ampere ratings on Drawings.

C. Type GD, General Duty, Single Throw, 240-V ac, 800 A and Smaller: UL 98 and NEMA KS 1, horsepower rated, with cartridge fuse interiors to accommodate [specified] [indicated] fuses, lockable handle with capability to accept two padlocks, and interlocked with cover in closed position.

Retain one of last two options in first paragraph below depending on whether fuse applications and class designations are indicated on Drawings or specified in Section 262813 "Fuses." Show fuse ampere ratings on Drawings.

D. Type HD, Heavy Duty, Single Throw, [240] [600]-V ac, 1200 A and Smaller: UL 98 and NEMA KS 1, horsepower rated, with clips or bolt pads to accommodate [specified] [indicated] fuses, lockable handle with capability to accept three padlocks, and interlocked with cover in closed position.

Retain one of last two options in first paragraph below depending on whether fuse applications and class designations are indicated on Drawings or specified in Section 262813 "Fuses." Show fuse ampere ratings on Drawings.

E. Type HD, Heavy Duty, Six Pole, Single Throw, [240] [600]-V ac, 200 A and Smaller: UL 98 and NEMA KS 1, horsepower rated, with clips or bolt pads to accommodate [specified] [indicated] fuses, lockable handle with capability to accept three padlocks, and interlocked with cover in closed position.

Retain one of last two options in first paragraph below depending on whether fuse applications and class designations are indicated on Drawings or specified in Section 262813 "Fuses." Show fuse ampere ratings on Drawings.

F. Type HD, Heavy Duty, Double Throw, [240] [600]-V ac, 1200 A and Smaller: UL 98 and NEMA KS 1, horsepower rated, with clips or bolt pads to accommodate [specified] [indicated] fuses, lockable handle with capability to accept three padlocks, and interlocked with cover in closed position.

G. Accessories:

Retain subparagraphs below with applicable switch paragraphs above. Verify that accessories specified are available and applicable to switch types and ratings in this article.

1. Equipment Ground Kit: Internally mounted and labeled for copper and aluminum ground conductors.

2. Neutral Kit: Internally mounted; insulated, capable of being grounded and bonded; labeled for copper and aluminum neutral conductors.

3. Class R Fuse Kit: Provides rejection of other fuse types when Class R fuses are specified.

4. Lugs: Suitable for number, size, and conductor material.

5. Service-Rated Switches: Labeled for use as service equipment.

2.2 NONFUSIBLE SWITCHES

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."

A. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Eaton Electrical Inc.; Cutler-Hammer Business Unit.

2. General Electric Company; GE Consumer & Industrial - Electrical Distribution.

3. Siemens Energy & Automation, Inc.

4. Square D; a brand of Schneider Electric.

5. <Insert manufacturer's name>.

Show pole quantities and voltage and ampere ratings of switches on Drawings. In first two paragraphs below, Type GD is for switches for light-commercial applications, 240-V ac, 30 to 600 A; Type HD is for all other single-throw switch uses. See Editing Instruction No. 2 in the Evaluations.

C. Type GD, General Duty, Single Throw, 600 A and Smaller: UL 98 and NEMA KS 1, horsepower rated, lockable handle with capability to accept two padlocks, and interlocked with cover in closed position.

D. Type HD, Heavy Duty, Single Throw, [240] [600]-V ac, 1200 A and Smaller: UL 98 and NEMA KS 1, horsepower rated, lockable handle with capability to accept three padlocks, and interlocked with cover in closed position.

E. Type HD, Heavy Duty, Six Pole, Single Throw, [240] [600]-V ac, 200 A and Smaller: UL 98 and NEMA KS 1, horsepower rated, lockable handle with capability to accept three padlocks, and interlocked with cover in closed position.

F. Type HD, Heavy Duty, Double Throw, [240] [600]-V ac, 1200 A and Smaller: UL 98 and NEMA KS 1, horsepower rated, lockable handle with capability to accept three padlocks, and interlocked with cover in closed position.

G. Accessories:

Retain subparagraphs below with applicable switch paragraphs above. Verify that accessories specified are available and applicable to switch types and ratings in this article.

1. Equipment Ground Kit: Internally mounted and labeled for copper and aluminum ground conductors.

2. Neutral Kit: Internally mounted; insulated, capable of being grounded and bonded; labeled for copper and aluminum neutral conductors.

3. Lugs: Suitable for number, size, and conductor material.

2.3 RECEPTACLE SWITCHES

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."

A. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Eaton Electrical Inc.; Cutler-Hammer Business Unit.

2. General Electric Company; GE Consumer & Industrial - Electrical Distribution.

3. Siemens Energy & Automation, Inc.

4. Square D; a brand of Schneider Electric.

5. <Insert manufacturer's name>.

Listed manufacturers offer similar but different options for voltage and ampere ratings and the make and model of receptacles available for factory installation on their switches. See Editing Instruction No. 3 in the Evaluations. Not all listed voltage and ampere ratings and enclosure types listed in "Enclosures" Article are available from all listed manufacturers.

Show pole quantities and voltage and ampere ratings of switches on Drawings. Retain one of last two options in first paragraph below depending on whether fuse applications and class designations are indicated on Drawings or specified in Section 262813 "Fuses." Show fuse ampere ratings on Drawings.

C. Type HD, Heavy-Duty, Single-Throw Fusible Switch: [240] [600]-V ac, [30] [60] [100] A; UL 98 and NEMA KS 1; horsepower rated, with clips or bolt pads to accommodate [specified] [indicated] fuses; lockable handle with capability to accept three padlocks; interlocked with cover in closed position.

D. Type HD, Heavy-Duty, Single-Throw Nonfusible Switch: [240] [600]-V ac, [30] [60] [100] A; UL 98 and NEMA KS 1; horsepower rated, lockable handle with capability to accept three padlocks; interlocked with cover in closed position.

E. Interlocking Linkage: Provided between the receptacle and switch mechanism to prevent inserting or removing plug while switch is in the on position, inserting any plug other than specified, and turning switch on if an incorrect plug is inserted or correct plug has not been fully inserted into the receptacle.

F. Receptacle: Polarized, three-phase, four-wire receptacle (fourth wire connected to enclosure ground lug).

If more than one type or rating of receptacle-switch combination is required, consider showing location of each on Drawings and deleting subparagraph below; otherwise, insert required information.

1. Receptacle Manufacturer and Catalog Number: <Insert manufacturer and catalog number>.

2.4 SHUNT TRIP SWITCHES

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."

A. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Cooper Bussmann, Inc.

2. Ferraz Shawmut, Inc.

3. Littelfuse, Inc.

4. <Insert manufacturer's name>.

Show voltage and ampere ratings of shunt trip switches and fuses on Drawings. See Editing Instruction No. 4 and "Shunt Trip Switches" Article in the Evaluations for guidance on using shunt trip switches.

Retain option in first paragraph below if shunt trip switches are used as elevator shunt trip disconnects per ASME A17.1 and NFPA 70.

C. General Requirements: Comply with[ ASME A17.1,] UL 50, and UL 98, with 200-kA interrupting and short-circuit current rating when fitted with Class J fuses.

D. Switches: Three-pole, horsepower rated, with integral shunt trip mechanism and Class J fuse block; lockable handle with capability to accept three padlocks; interlocked with cover in closed position.

E. Control Circuit: 120-V ac; obtained from [integral control power transformer, with primary and secondary fuses,] <Insert source of control power> with a control power [transformer] [source] of enough capacity to operate shunt trip, connected pilot, and indicating and control devices.

F. Accessories:

Not all accessories listed in subparagraphs below are available from every listed manufacturer. Verify availability and unique characteristics with manufacturers selected.

1. Oiltight key switch for key-to-test function.

2. Oiltight ON pilot light.

3. Isolated neutral lug.

Retain first subparagraph below if using switch for hydraulic elevators with automatic recall. Show required interface wiring on Drawings.

4. Mechanically interlocked auxiliary contacts that change state when switch is opened and closed.

5. Form C alarm contacts that change state when switch is tripped.

Retain two subparagraphs below when interfacing elevators with the facility fire-alarm system is required. In first subparagraph, if retaining 24-V dc coil option, a separate 24-V dc source and an initiating contact must be provided by the facility fire-alarm system.

6. Three-pole, double-throw, fire-safety and alarm relay; [120-V ac] [24-V dc] coil voltage.

7. Three-pole, double-throw, fire-alarm voltage monitoring relay complying with NFPA 72.

2.5 MOLDED-CASE CIRCUIT BREAKERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."

A. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Eaton Electrical Inc.; Cutler-Hammer Business Unit.

2. General Electric Company; GE Consumer & Industrial - Electrical Distribution.

3. Siemens Energy & Automation, Inc.

4. Square D; a brand of Schneider Electric.

5. <Insert manufacturer's name>.

Show pole quantities and voltage and ampere ratings of MCCBs and switches on Drawings. See Editing Instruction No. 6 in the Evaluations.

C. General Requirements: Comply with UL 489, NEMA AB 1, and NEMA AB 3, with interrupting capacity to comply with available fault currents.

D. Thermal-Magnetic Circuit Breakers: Inverse time-current element for low-level overloads and instantaneous magnetic trip element for short circuits. Adjustable magnetic trip setting for circuit-breaker frame sizes 250 A and larger.

E. Electronic Trip Circuit Breakers: Field-replaceable rating plug, rms sensing, with the following field-adjustable settings:

Retain one or more of four subparagraphs below and coordinate required adjustable settings with Section 260573 "Overcurrent Protective Device Coordination Study."

1. Instantaneous trip.

2. Long- and short-time pickup levels.

3. Long- and short-time time adjustments.

4. Ground-fault pickup level, time delay, and I2t response.

F. Current-Limiting Circuit Breakers: Frame sizes 400 A and smaller, and let-through ratings less than NEMA FU 1, RK-5.

G. Features and Accessories:

Not all features, accessories, and options in subparagraphs below are available for every rating and from every listed manufacturer. Verify availability and unique characteristics with manufacturers selected.

1. Standard frame sizes, trip ratings, and number of poles.

2. Lugs: Suitable for number, size, trip ratings, and conductor material.

3. Application Listing: Appropriate for application; Type SWD for switching fluorescent lighting loads; Type HID for feeding fluorescent and high-intensity discharge lighting circuits.

Retain first option in first subparagraph below for solid-state trip units; retain second option for thermal-magnetic trip units.

4. Ground-Fault Protection: Comply with UL 1053; [integrally mounted, self-powered] [remote-mounted and powered] type with mechanical ground-fault indicator; relay with adjustable pickup and time-delay settings, push-to-test feature, internal memory, and shunt trip unit; and three-phase, zero-sequence current transformer/sensor.

5. Shunt Trip: Trip coil energized from separate circuit, with coil-clearing contact.

6. Auxiliary Contacts: [One SPDT switch] [Two SPDT switches] with "a" and "b" contacts; "a" contacts mimic circuit-breaker contacts, "b" contacts operate in reverse of circuit-breaker contacts.

7. Alarm Switch: One [NO] [NC] contact that operates only when circuit breaker has tripped.

2.6 ENCLOSURES

A. Enclosed Switches and Circuit Breakers: NEMA AB 1, NEMA KS 1, NEMA 250, and UL 50, to comply with environmental conditions at installed location.

See "Enclosures" Article in the Evaluations for discussion of enclosure types. Coordinate subparagraphs below with Drawings by identifying the designated areas on plans or by including the required enclosure types. Availability of some enclosure types is limited by type of switch or circuit breaker; consult manufacturers for availability of, and limitations on, other than NEMA 250, Type 1 enclosures. General-duty switches are generally only available in NEMA 250, Type 1 or NEMA 250, Type 3R enclosures.

1. Indoor, Dry and Clean Locations: NEMA 250, [Type 1] <Insert type>.

2. Outdoor Locations: NEMA 250, [Type 3R] <Insert type>.

3. [Kitchen] [Wash-Down] Areas: NEMA 250, [Type 4X] <Insert type>, [stainless steel] <Insert material>.

4. Other Wet or Damp, Indoor Locations: NEMA 250, [Type 4] <Insert type>.

5. Indoor Locations Subject to Dust, Falling Dirt, and Dripping Noncorrosive Liquids: NEMA 250, Type 12.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Install individual wall-mounted switches and circuit breakers with tops at uniform height unless otherwise indicated.

Retain first paragraph below if seismic controls are required for Project. Coordinate with Drawings.

B. Comply with mounting and anchoring requirements specified in Section 260548.16 "Seismic Controls for Electrical Systems."

C. Temporary Lifting Provisions: Remove temporary lifting eyes, channels, and brackets and temporary blocking of moving parts from enclosures and components.

D. Install fuses in fusible devices.

E. Comply with NECA 1.

3.2 IDENTIFICATION

A. Comply with requirements in Section 260553 "Identification for Electrical Systems."

1. Identify field-installed conductors, interconnecting wiring, and components; provide warning signs.

2. Label each enclosure with engraved metal or laminated-plastic nameplate.

3.3 FIELD QUALITY CONTROL

A. Perform tests and inspections.

Retain first two paragraphs below to describe tests and inspections to be performed.

B. Acceptance Testing Preparation:

1. Test insulation resistance for each enclosed switch and circuit breaker, component, connecting supply, feeder, and control circuit.

2. Test continuity of each circuit.

C. Tests and Inspections:

1. Perform each visual and mechanical inspection and electrical test stated in NETA Acceptance Testing Specification. Certify compliance with test parameters.

2. Correct malfunctioning units on-site, where possible, and retest to demonstrate compliance; otherwise, replace with new units and retest.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

D. Enclosed switches and circuit breakers will be considered defective if they do not pass tests and inspections.

E. Prepare test and inspection reports, including a certified report that identifies enclosed switches and circuit breakers and that describes scanning results. Include notation of deficiencies detected, remedial action taken, and observations after remedial action.

END OF SECTION 262816

	ENCLOSED SWITCHES AND CIRCUIT BREAKERS
	262816 - 1



