Copyright 2012 AIA
MasterSpec Professional
03/12

Copyright 2012 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 262913 - ENCLOSED CONTROLLERS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section includes the following enclosed controllers rated 600 V and less:

1. Full-voltage manual.

2. Full-voltage magnetic.

3. Multispeed.

1.2 DEFINITIONS

Retain definition(s) remaining after this Section has been edited.

A. CPT: Control power transformer.

B. MCCB: Molded-case circuit breaker.

C. MCP: Motor circuit protector.

D. N.C.: Normally closed.

E. N.O.: Normally open.

F. OCPD: Overcurrent protective device.

1.3 PERFORMANCE REQUIREMENTS

Retain this article with "Seismic Qualification Certificates" Paragraph in "Informational Submittals" Article for projects requiring seismic design; however, several listed manufacturers do not currently offer seismic certificates and they do not all test wall-mounted controllers for their ability to "withstand" a seismic event. Verify availability of seismic testing and certification with manufacturers. Model building codes and ASCE/SEI 7 establish criteria for buildings subject to earthquake motions. Verify requirements of authorities having jurisdiction.

A. Seismic Performance: Enclosed controllers shall withstand the effects of earthquake motions determined according to [ASCE/SEI 7] <Insert requirement>.

Retain subparagraph below to define the term "withstand" as it applies to this Project. Definition varies with type of building and occupancy and is critical to valid certification. Option is used for essential facilities where equipment must operate immediately after an earthquake.

1. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified[ and the unit will be fully operational after the seismic event]."

1.4 ACTION SUBMITTALS

A. Product Data: For each type of enclosed controller.

B. Shop Drawings: For each enclosed controller. Include dimensioned plans, elevations, sections, details, and required clearances and service spaces around controller enclosures.

1. Wiring Diagrams: For power, signal, and control wiring.

1.5 INFORMATIONAL SUBMITTALS

A. Seismic Qualification Certificates: For enclosed controllers, accessories, and components, from manufacturer.

B. Field quality-control reports.

1.6 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

1.7 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

B. Comply with NFPA 70.

Retain paragraph below for projects in seismic areas. If retaining, also retain "Seismic Qualification Certificates" Paragraph in "Informational Submittals" Article.

C. IEEE Compliance: Fabricate and test enclosed controllers according to IEEE 344 to withstand seismic forces defined in Section 260548.16 "Seismic Controls for Electrical Systems."

PART 2 -  PRODUCTS

2.1 FULL-VOLTAGE CONTROLLERS

Show controller pole quantities, voltage, NEMA size and type, accessories, short-circuit current rating (or available short-circuit currents), and enclosure type for each controller on Drawings. See "Full-Voltage Controllers" Article in the Evaluations for selection considerations. Enclosed controllers without integral OCPDs (e.g., fuses, MCPs, or thermal-magnetic circuit breakers) may have very low short-circuit current ratings when used in series with upstream devices. See Editing Instruction No. 2 in the Evaluations.

Not all features, accessories, and options in this article are available for every rating, with every enclosure type, and from every listed manufacturer. Verify availability and unique characteristics with manufacturers. Show on Drawings those features and accessories that apply to each controller.

A. General Requirements for Full-Voltage Controllers: Comply with NEMA ICS 2, general purpose, Class A.

Motor-starting switches do not have integral overload relays. See "Motor-Starting Switches" Article in the Evaluations for additional guidance on their use.

B. Motor-Starting Switches: "Quick-make, quick-break" toggle or push-button action; marked to show whether unit is off or on.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first subparagraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Eaton Electrical Inc.; Cutler-Hammer Business Unit.

b. General Electric Company; GE Consumer & Industrial - Electrical Distribution.

c. Rockwell Automation, Inc.; Allen-Bradley brand.

d. Siemens Energy & Automation, Inc.

e. Square D; a brand of Schneider Electric.

f. <Insert manufacturer's name>.

3. Configuration: [Nonreversing] [Reversing] [Two speed].

4. Surface mounting.

5. Pilot light.

One- and two-pole, fractional horsepower manual controllers are suitable for use with single-phase ac motors up to 1 hp. See "Fractional Horsepower Manual Controllers" Article in the Evaluations for additional guidance on their use.

C. Fractional Horsepower Manual Controllers: "Quick-make, quick-break" toggle or push-button action; marked to show whether unit is off, on, or tripped.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first subparagraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Eaton Electrical Inc.; Cutler-Hammer Business Unit.

b. General Electric Company; GE Consumer & Industrial - Electrical Distribution.

c. Rockwell Automation, Inc.; Allen-Bradley brand.

d. Siemens Energy & Automation, Inc.

e. Square D; a brand of Schneider Electric.

f. <Insert manufacturer's name>.

3. Configuration: [Nonreversing] [Two speed].

See Editing Instruction No. 5 and "Overload Protection" Article in the Evaluations for additional guidance on retaining options in first subparagraph below. Although Class 10 seems to be "standard" for this equipment, some manufacturers may offer others. Retain first option below unless another class is required and available.

4. Overload Relays: Inverse-time-current characteristics; NEMA ICS 2, [Class 10] <Insert class> tripping characteristics; heaters matched to nameplate full-load current of actual protected motor; external reset push button[; bimetallic type] [; melting alloy type].

5. Surface mounting.

6. Pilot light.

One-, two-, and three-pole integral horsepower manual controllers are suitable for use with single- and three-phase ac motors up to 10 hp at 480-V ac. See "Integral Horsepower Manual Controllers" Article in the Evaluations for additional guidance on their use.

D. Integral Horsepower Manual Controllers: "Quick-make, quick-break" toggle or push-button action; marked to show whether unit is off, on, or tripped.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first subparagraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Eaton Electrical Inc.; Cutler-Hammer Business Unit.

b. General Electric Company; GE Consumer & Industrial - Electrical Distribution.

c. Rockwell Automation, Inc.; Allen-Bradley brand.

d. Siemens Energy & Automation, Inc.

e. Square D; a brand of Schneider Electric.

f. <Insert manufacturer's name>.

3. Configuration: [Nonreversing] [Reversing] [Two speed].

See Editing Instruction No. 5 and "Overload Protection" Article in the Evaluations for additional guidance in retaining options in first subparagraph below. Although Class 10 seems to be "standard" for this equipment, some manufacturers may offer others. Retain first option below unless another class is required and available.

4. Overload Relays: Inverse-time-current characteristics; NEMA ICS 2, [Class 10] <Insert class> tripping characteristics; heaters and sensors in each phase, matched to nameplate full-load current of actual protected motor and having appropriate adjustment for duty cycle; external reset push button[; bimetallic type] [; melting alloy type].

5. Surface mounting.

6. Pilot light.

Three-pole integral horsepower magnetic controllers are suitable for use with three-phase ac motors up to 1600 hp, and from NEMA ICS 2, Size 00 to Size 9; however, not all listed manufacturers offer enclosed controllers up to Size 9. Two- and four-pole models are also available in varying minimum and maximum horsepower ratings and NEMA sizes. See "Magnetic Controllers" Article in the Evaluations for additional guidance on their use.

E. Magnetic Controllers: Full voltage, across the line, electrically held.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first subparagraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Eaton Electrical Inc.; Cutler-Hammer Business Unit.

b. General Electric Company; GE Consumer & Industrial - Electrical Distribution.

c. Rockwell Automation, Inc.; Allen-Bradley brand.

d. Siemens Energy & Automation, Inc.

e. Square D; a brand of Schneider Electric.

f. <Insert manufacturer's name>.

3. Configuration: [Nonreversing] [Reversing].

4. Contactor Coils: Pressure-encapsulated type.

a. Operating Voltage: Depending on contactor NEMA size and line-voltage rating, manufacturer's standard matching control power or line voltage.

5. Power Contacts: Totally enclosed, double-break, silver-cadmium oxide; assembled to allow inspection and replacement without disturbing line or load wiring.

6. Control Circuits: [24] [120] <Insert value>-V ac; obtained from [integral CPT, with primary and secondary fuses] <Insert source of control power>, with [CPT] [control power source] of sufficient capacity to operate integral devices and remotely located pilot, indicating, and control devices.

Retain one or more of first three subparagraphs below. If retaining more than one, show on Drawings where each type is required. See Editing Instruction No. 5 and "Overload Protection" Article in the Evaluations for additional guidance.

7. Melting Alloy Overload Relays:

a. Inverse-time-current characteristic.

b. [Class 10] [Class 20] [Class 30] tripping characteristic.

c. Heaters in each phase matched to nameplate full-load current of actual protected motor and with appropriate adjustment for duty cycle.

8. Bimetallic Overload Relays:

a. Inverse-time-current characteristic.

b. [Class 10] [Class 20] [Class 30] tripping characteristic.

c. Heaters in each phase matched to nameplate full-load current of actual protected motor and with appropriate adjustment for duty cycle.

9. Solid-State Overload Relay:

a. Switch or dial selectable for motor running overload protection.

b. Sensors in each phase.

c. [Class 10] [Class 20] [Class 10/20 selectable] tripping characteristic selected to protect motor against voltage and current unbalance and single phasing.

10. External overload reset push button.

Combination controllers are magnetic controllers combined with a disconnecting means, OCPD, or both. See Editing Instruction No. 2 and "Combination Controllers" Article in the Evaluations for guidance on using combination controllers and the different types of disconnecting means and OCPDs. Indicate requirements for disconnecting means and OCPDs on Drawings. Revise paragraph below if overload relays differ from those indicated in "Magnetic Controllers" Paragraph above.

F. Combination Magnetic Controller: Factory-assembled combination of magnetic controller, OCPD, and disconnecting means.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first subparagraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Eaton Electrical Inc.; Cutler-Hammer Business Unit.

b. General Electric Company; GE Consumer & Industrial - Electrical Distribution.

c. Rockwell Automation, Inc.; Allen-Bradley brand.

d. Siemens Energy & Automation, Inc.

e. Square D; a brand of Schneider Electric.

f. <Insert manufacturer's name>.

Disconnecting means and OCPDs must be closely coordinated with calculated short-circuit current values at the controller locations because they are directly related to the short-circuit withstand ratings of their combination controllers. Although fusible switches (with appropriate fuses) can provide Type 2 controller protection from very high short-circuit currents, not all circuit breakers or MCPs can. See Editing Instruction No. 7 in the Evaluations for explanation of protection types and when they should be considered.

3. Fusible Disconnecting Means:

a. NEMA KS 1, heavy-duty, horsepower-rated, fusible switch with clips or bolt pads to accommodate [Class J] [Class R] [indicated] fuses.

b. Lockable Handle: Accepts three padlocks and interlocks with cover in closed position.

Retain first subparagraph below if external control power is used or for remote indication of disconnecting means position.

4. Auxiliary Contacts: N.O./N.C., arranged to activate before switch blades open.

Nonfusible switches have no inherent short-circuit or interrupting current ratings and so must be used in series with upstream fuses or specific types and ratings of circuit breakers. See "Application of Switches and Circuit Breakers" Article in the Evaluations.

5. Nonfusible Disconnecting Means:

a. NEMA KS 1, heavy-duty, horsepower-rated, nonfusible switch.

b. Lockable Handle: Accepts three padlocks and interlocks with cover in closed position.

Retain first subparagraph below if external control power is used or for remote indication of disconnecting means position.

c. Auxiliary Contacts: N.O./N.C., arranged to activate before switch blades open.

MCP disconnecting means in first subparagraph below must be used in combination with integral overload relays.

6. MCP Disconnecting Means:

a. UL 489, NEMA AB 1, and NEMA AB 3, with interrupting capacity to comply with available fault currents, instantaneous-only circuit breaker with front-mounted, field-adjustable, short-circuit trip coordinated with motor locked-rotor amperes.

b. Lockable Handle: Accepts three padlocks and interlocks with cover in closed position.

Retain first subparagraph below if external control power is used or for remote indication of disconnecting means position. If retaining auxiliary contacts, indicate "a" and "b" contact quantities on Drawings.

c. Auxiliary contacts "a" and "b" arranged to activate with MCP handle.

7. MCCB Disconnecting Means:

a. UL 489, NEMA AB 1, and NEMA AB 3, with interrupting capacity to comply with available fault currents; thermal-magnetic MCCB, with inverse time-current element for low-level overloads and instantaneous magnetic trip element for short circuits.

b. Front-mounted, adjustable magnetic trip setting for circuit-breaker frame sizes 250 A and larger.

c. Lockable Handle: Accepts three padlocks and interlocks with cover in closed position.

Retain subparagraph below if external control power is used or for remote indication of disconnecting means position. If retaining auxiliary contacts, indicate "a" and "b" contact quantities on Drawings.

d. Auxiliary contacts "a" and "b" arranged to activate with MCCB handle.

2.2 MULTISPEED MAGNETIC CONTROLLERS

Show controller pole quantities, voltage, NEMA size and type, accessories, short-circuit current rating (or available short-circuit currents), and enclosure type for each controller on Drawings. See "Multispeed Controllers" Article in the Evaluations for selection considerations. Enclosed controllers without integral OCPDs (e.g., fuses, MCPs, or thermal-magnetic circuit breakers) may have very low short-circuit current ratings when used in series with upstream devices. See Editing Instruction No. 2 in the Evaluations. The Section Text includes only two-speed controllers; however, most manufacturers catalog controllers offering more than two speeds. Multispeed controllers supporting more than two speeds may be added to suit Project.

Not all features, accessories, and options in this article are available for every rating, with every enclosure type, and from every listed manufacturer. Verify availability and unique characteristics with manufacturers. Show on Drawings those features and accessories that apply to each controller.

A. General Requirements for Multispeed Magnetic Controllers: Comply with NEMA ICS 2, general purpose, Class A.

B. Multispeed Magnetic Controllers: Two speed, full voltage, across the line, electrically held.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first subparagraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Eaton Electrical Inc.; Cutler-Hammer Business Unit.

b. General Electric Company; GE Consumer & Industrial - Electrical Distribution.

c. Rockwell Automation, Inc.; Allen-Bradley brand.

d. Siemens Energy & Automation, Inc.

e. Square D; a brand of Schneider Electric.

f. <Insert manufacturer's name>.

3. Configuration: [Nonreversing] [Reversing]; [consequent pole] [two winding].

4. Contactor Coils: Pressure-encapsulated type.

a. Operating Voltage: Depending on contactor NEMA size and line-voltage rating, manufacturer's standard matching control power or line voltage.

5. Power Contacts: Totally enclosed, double break, silver-cadmium oxide; assembled to allow inspection and replacement without disturbing line or load wiring.

6. Control Circuits: [24] [120] <Insert value>-V ac; obtained from [integral CPT, with primary and secondary fuses] <Insert source of control power>, with [CPT] [control power source] of sufficient capacity to operate all integral devices and remotely located pilot, indicating, and control devices.

Retain one or both of first two subparagraphs below. If retaining both, indicate on Drawings where each type is required. Compelling and accelerating relays cannot be specified together for the same controller. Compelling, accelerating, and decelerating relays can be used for multispeed controllers; antiplugging relays are used only for reversing multispeed controllers.

7. Compelling relays shall ensure that motor will start only at low speed.

8. Accelerating timer relays shall ensure properly timed acceleration through speeds lower than that selected.

9. Decelerating timer relays shall ensure automatically timed deceleration through each speed.

10. Antiplugging timer relays shall ensure a time delay when transferring from FORWARD to REVERSE and back.

Retain one or more of first three subparagraphs below. If retaining more than one, show on Drawings where each type is required. See Editing Instruction No. 5 and "Overload Protection" Article in the Evaluations for additional guidance.

11. Melting Alloy Overload Relays:

a. Inverse-time-current characteristic.

b. [Class 10] [Class 20] [Class 30] tripping characteristic.

c. Heaters in each phase matched to nameplate full-load current of actual protected motor and with appropriate adjustment for duty cycle.

12. Bimetallic Overload Relays:

a. Inverse-time-current characteristic.

b. [Class 10] [Class 20] [Class 30] tripping characteristic.

c. Heaters in each phase matched to nameplate full-load current of actual protected motor and with appropriate adjustment for duty cycle.

13. Solid-State Overload Relay:

a. Switch or dial selectable for motor running overload protection.

b. Sensors in each phase.

c. [Class 10] [Class 20] [Class 10/20 selectable] tripping characteristic selected to protect motor against voltage and current unbalance and single phasing.

14. External overload reset push button.

Combination controllers are magnetic controllers combined with a disconnecting means, OCPD, or both. See Editing Instruction No. 2 and "Combination Controllers" Article in the Evaluations for guidance on using combination controllers and the different types of disconnecting means and OCPDs. Indicate requirements for disconnecting means and OCPDs on Drawings. Revise paragraph below if overload relays differ from those indicated in "Multispeed Magnetic Controllers" Paragraph above.

C. Combination Multispeed Magnetic Controller: Factory-assembled combination of multispeed magnetic controller, OCPD, and disconnecting means.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first subparagraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Eaton Electrical Inc.; Cutler-Hammer Business Unit.

b. General Electric Company; GE Consumer & Industrial - Electrical Distribution.

c. Rockwell Automation, Inc.; Allen-Bradley brand.

d. Siemens Energy & Automation, Inc.

e. Square D; a brand of Schneider Electric.

f. <Insert manufacturer's name>.

Disconnecting means and OCPDs must be closely coordinated with calculated short-circuit current values at the controller locations, because they are directly related to the short-circuit withstand ratings of their combination controllers. Although fusible switches (with appropriate fuses) can provide Type 2 controller protection from very high short-circuit currents, not all circuit breakers or MCPs can. See Editing Instruction No. 7 in the Evaluations for explanation of protection types and when they should be considered.

3. Fusible Disconnecting Means:

a. NEMA KS 1, heavy-duty, horsepower-rated, fusible switch with clips or bolt pads to accommodate [Class J] [Class R] [indicated] fuses.

b. Lockable Handle: Accepts three padlocks and interlocks with cover in closed position.

Retain first subparagraph below if external control power is used or for remote indication of disconnecting means position.

c. Auxiliary Contacts: N.O./N.C., arranged to activate before switch blades open.

Nonfusible switches have no inherent short-circuit or interrupting current ratings and so must be used in series with upstream fuses or specific types and ratings of circuit breakers. See "Application of Switches and Circuit Breakers" Article in the Evaluations.

4. Nonfusible Disconnecting Means:

a. NEMA KS 1, heavy-duty, horsepower-rated, nonfusible switch.

b. Lockable Handle: Accepts three padlocks and interlocks with cover in closed position.

Retain first subparagraph below if external control power is used or for remote indication of disconnecting means position.

c. Auxiliary Contacts: N.O./N.C., arranged to activate before switch blades open.

MCP disconnecting means in first subparagraph below must be used in combination with integral overload relays.

5. MCP Disconnecting Means:

a. UL 489, NEMA AB 1, and NEMA AB 3, with interrupting capacity to comply with available fault currents, instantaneous-only circuit breaker with front-mounted, field-adjustable, short-circuit trip coordinated with motor locked-rotor amperes.

b. Lockable Handle: Accepts three padlocks and interlocks with cover in closed position.

Retain first subparagraph below if external control power is used or for remote indication of disconnecting means position. If retaining auxiliary contacts, indicate "a" and "b" contact quantities on Drawings.

c. Auxiliary contacts "a" and "b" arranged to activate with MCP handle.

6. MCCB Disconnecting Means:

a. UL 489, NEMA AB 1, and NEMA AB 3, with interrupting capacity to comply with available fault currents; thermal-magnetic MCCB, with inverse time-current element for low-level overloads and instantaneous magnetic trip element for short circuits.

b. Front-mounted, adjustable magnetic trip setting for circuit-breaker frame sizes 250 A and larger.

c. Lockable Handle: Accepts three padlocks and interlocks with cover in closed position.

Retain first subparagraph below if external control power is used or for remote indication of disconnecting means position. If retaining auxiliary contacts, indicate "a" and "b" contact quantities on Drawings.

d. Auxiliary contacts "a" and "b" arranged to activate with MCCB handle.

e. [N.C.] [N.O.] alarm contact that operates only when MCCB has tripped.

2.3 ENCLOSURES

A. Enclosed Controllers: NEMA ICS 6, to comply with environmental conditions at installed location.

See "Enclosures" Article in the Evaluations for discussion of enclosure types. Coordinate subparagraphs below with Drawings by identifying the designated areas on plans or by including the required enclosure types. Enclosure materials and finishes may be added to the Section Text. Availability of some enclosure types is limited by type of controller; consult manufacturers for availability of, and limitations on, other than NEMA ICS 6, Type 1 enclosures.

1. Dry and Clean Indoor Locations: [Type 1] <Insert type>.

2. Outdoor Locations: [Type 3R] [Type 4X] <Insert type>.

3. [Kitchen] [Wash-Down] Areas: [Type 4X] <Insert type>, [stainless steel] <Insert material>.

4. Other Wet or Damp Indoor Locations: [Type 4] <Insert type>.

5. Indoor Locations Subject to Dust, Falling Dirt, and Dripping Noncorrosive Liquids: Type 12.

2.4 ACCESSORIES

Accessories listed in this article pertain primarily to enclosed magnetic controllers, with limited applications to manual controllers; they are also limited in application by controller and enclosure types. Retain applicable accessories below. Indicate requirements for and quantities of accessories on Drawings. See "Accessories" Article in the Evaluations for additional guidance; consult manufacturers for availability of, and limitations on, other accessories.

A. Push Buttons, Pilot Lights, and Selector Switches: NEMA ICS 5; heavy-duty type; factory installed in controller enclosure cover unless otherwise indicated.

B. Control Relays: Auxiliary and adjustable time-delay relays.

Features in paragraph below are available in individual relays or combined into a single multipurpose relay. Consult manufacturers for availability. Consider specifying phase-failure relays for single-phasing protection in fusible-switch combination controllers if solid-state overload relays are not specified.

C. Phase-Failure, Phase-Reversal, and Undervoltage and Overvoltage Relays: Solid-state sensing circuit with isolated output contacts for hard-wired connections. Provide adjustable undervoltage, overvoltage, and time-delay settings.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Wall-Mounted Controllers: Install enclosed controllers on walls with tops at uniform height, and with disconnect operating handles not higher than 79 inches (2006 mm) above finished floor, unless otherwise indicated, and by bolting units to wall or mounting on lightweight structural-steel channels bolted to wall. For controllers not at walls, provide freestanding racks complying with Section 260529 "Hangers and Supports for Electrical Systems."

Retain first paragraph below for equipment supported on slabs-on-grade.

B. Floor-Mounted Controllers: Install enclosed controllers on 4-inch (100-mm) nominal-thickness concrete base. Comply with requirements for concrete base specified in [Section 033000 "Cast-in-Place Concrete."] [Section 033053 "Miscellaneous Cast-in-Place Concrete."]

1. Install dowel rods to connect concrete base to concrete floor. Unless otherwise indicated, install dowel rods on 18-inch (450-mm) centers around the full perimeter of concrete base.

2. For supported equipment, install epoxy-coated anchor bolts that extend through concrete base and anchor into structural concrete floor.

3. Place and secure anchorage devices. Use setting drawings, templates, diagrams, instructions, and directions furnished with items to be embedded.

4. Install anchor bolts to elevations required for proper attachment to supported equipment.

Retain first paragraph below if seismic controls are Project requirement. Coordinate with Drawings.

C. Seismic Bracing: Comply with requirements specified in Section 260548.16 "Seismic Controls for Electrical Systems."

D. Temporary Lifting Provisions: Remove temporary lifting eyes, channels, and brackets and temporary blocking of moving parts from enclosures and components.

Retain first three paragraphs below, as appropriate, to coincide with selections made in Part 2.

E. Install fuses in each fusible-switch enclosed controller.

F. Install fuses in control circuits if not factory installed. Comply with requirements in Section 262813 "Fuses."

G. Install heaters in thermal overload relays. Select heaters based on actual nameplate full-load amperes after motors have been installed.

H. Comply with NECA 1.

3.2 IDENTIFICATION

A. Identify enclosed controllers, components, and control wiring. Comply with requirements for identification specified in Section 260553 "Identification for Electrical Systems."

1. Identify field-installed conductors, interconnecting wiring, and components; provide warning signs.

2. Label each enclosure with engraved nameplate.

3. Label each enclosure-mounted control and pilot device.

3.3 CONTROL WIRING INSTALLATION

Retain this article if remote-control or remote-status indication is required.

A. Install wiring between enclosed controllers and remote devices[ and facility's central control system]. Comply with requirements in Section 260523 "Control-Voltage Electrical Power Cables."

B. Bundle, train, and support wiring in enclosures.

C. Connect selector switches and other automatic-control selection devices where applicable.

1. Connect selector switches to bypass only those manual- and automatic-control devices that have no safety functions when switch is in manual-control position.

2. Connect selector switches with enclosed-controller circuit in both manual and automatic positions for safety-type control devices such as low- and high-pressure cutouts, high-temperature cutouts, and motor overload protectors.

3.4 FIELD QUALITY CONTROL

Retain first paragraph below to require Contractor to perform tests and inspections.

A. Perform tests and inspections.

Retain first two paragraphs below to describe tests and inspections to be performed.

B. Acceptance Testing Preparation:

1. Test insulation resistance for each enclosed controller, component, connecting supply, feeder, and control circuit.

2. Test continuity of each circuit.

C. Tests and Inspections:

1. Inspect controllers, wiring, components, connections, and equipment installation.[ Test and adjust controllers, components, and equipment.]

2. Test insulation resistance for each enclosed-controller element, component, connecting motor supply, feeder, and control circuits.

3. Test continuity of each circuit.

4. Verify that voltages at controller locations are within plus or minus 10 percent of motor nameplate rated voltages. If outside this range for any motor, notify [Architect] [Construction Manager] [Owner] before starting the motor(s).

5. Test each motor for proper phase rotation.

6. Perform each electrical test and visual and mechanical inspection stated in NETA Acceptance Testing Specification. Certify compliance with test parameters.

7. Correct malfunctioning units on-site, where possible, and retest to demonstrate compliance; otherwise, replace with new units and retest.

8. Test and adjust controls, remote monitoring, and safeties. Replace damaged and malfunctioning controls and equipment.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

D. Enclosed controllers will be considered defective if they do not pass tests and inspections.

E. Prepare test and inspection reports. Include notation of deficiencies detected, remedial action taken, and observations after remedial action.

3.5 ADJUSTING

Retain one or both paragraphs below to correspond to selections made in Part 2.

A. Set field-adjustable switches and overload-relay pickup and trip ranges.

B. Adjust the trip settings of MCPs and thermal-magnetic circuit breakers with adjustable instantaneous trip elements. Initially adjust to six times the motor nameplate full-load ampere ratings and attempt to start motors several times, allowing for motor cooldown between starts. If tripping occurs on motor inrush, adjust settings in increments until motors start without tripping. Do not exceed eight times the motor full-load amperes (or 11 times for NEMA Premium Efficient motors if required). Where these maximum settings do not allow starting of a motor, notify [Architect] [Construction Manager] [Owner] before increasing settings.

3.6 DEMONSTRATION

A. Train Owner's maintenance personnel to adjust, operate, and maintain enclosed controllers.

END OF SECTION 262913

	ENCLOSED CONTROLLERS
	262913 - 1



