Copyright 2012 AIA
MasterSpec Professional
03/12

Copyright 2012 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 262923 - VARIABLE-FREQUENCY MOTOR CONTROLLERS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

If applying for LEED certification, LEED Prerequisite EA 2 requires compliance with ASHRAE/IESNA 90.1, which requires the use of mechanical or electrical variable-speed drives on fan motors used in VAV system fans that are 15 hp and larger, and on motors in variable-flow hydronic systems that are larger than 50 hp.

Energy savings resulting from the use of variable-frequency motor controllers on motors other than those required by Prerequisite EA 2 can be combined with other energy-saving measures to meet the requirements of LEED-NC, LEED-CS, and LEED for Schools Credit EA 1.

LEED-NC and LEED for Schools Credit EA 5, LEED-CI Credit EA 3, and LEED-CS Credit EA 5.1 require the development of a Measurement & Verification Plan to achieve this credit. Energy used by each VFC can be used in the simulation calibration process required by the International Performance Measurement & Verification Protocol, Volume III, Ch. 4, "Whole Building Calibrated Simulation" (Option D) to verify the building's compliance with this credit.

PART 1 -  GENERAL

1.1 SUMMARY

This Section is limited to separately enclosed, preassembled, combination VFCs furnished by a VFC manufacturer; it does not include panel-mounted variable-frequency drives intended to be field installed in separate enclosures by contractors or incorporated into machinery or processes as part of a packaged system. The Section Text does not include VFCs for constant-horsepower loads because they are seldom used in commercial (e.g., plumbing and HVAC) applications; however, they can be added to suit Project.

A. Section includes separately enclosed, preassembled, combination VFCs, rated 600 V and less, for speed control of three-phase, squirrel-cage induction motors.

B. See Section 262419 "Motor-Control Centers" for VFCs installed in motor-control centers.

1.2 DEFINITIONS

Retain terms that remain after this Section has been edited for a project.

A. BAS: Building automation system.

B. CE: Conformite Europeene (European Compliance).

C. CPT: Control power transformer.

D. EMI: Electromagnetic interference.

E. OCPD: Overcurrent protective device.

F. PID: Control action, proportional plus integral plus derivative.

G. RFI: Radio-frequency interference.

H. VFC: Variable-frequency motor controller.

1.3 ACTION SUBMITTALS

A. Product Data: For each type and rating of VFC indicated.

B. Shop Drawings: For each VFC indicated.

1. Include details of equipment assemblies. Indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

2. Include diagrams for power, signal, and control wiring.

1.4 INFORMATIONAL SUBMITTALS

Coordinate "Qualification Data" Paragraph below with qualification requirements in Section 014000 "Quality Requirements" and as may be supplemented in "Quality Assurance" Article.

A. Qualification Data: For testing agency.

Retain "Seismic Qualification Certificates" Paragraph below if required by seismic criteria applicable to Project. Coordinate with Section 260548.16 "Seismic Controls for Electrical Systems." See ASCE/SEI 7 for certification requirements for equipment and components.

B. Seismic Qualification Certificates: For each VFC, accessories, and components, from manufacturer.

1. Certificate of compliance.

2. Dimensioned Outline Drawings of Equipment Unit: Identify center of gravity and locate and describe mounting and anchorage provisions.

3. Detailed description of equipment anchorage devices on which the certification is based, and their installation requirements.

C. Product certificates.

Retain "Field quality-control reports" Paragraph below if Contractor is responsible for field quality-control testing and inspecting.

D. Field quality-control reports.

1.5 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

1.6 QUALITY ASSURANCE

Retain "Testing Agency Qualifications" Paragraph below if Contractor selects testing agency or if Contractor is required to provide services of a qualified testing agency in "Field Quality Control" Article. Qualification requirements are in addition to those specified in Section 014000 "Quality Requirements," which also defines "NRTL" (nationally recognized testing laboratory).

A. Testing Agency Qualifications: Member company of NETA or an NRTL.

1.7 WARRANTY

A. Special Warranty: Manufacturer agrees to repair or replace VFCs that fail in materials or workmanship within specified warranty period.

1. Warranty Period: [Five] <Insert number> years from date of Substantial Completion.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

2.1 MANUFACTURERS

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Cerus Industrial, Inc.

2. Danfoss Inc; Danfoss Drives Div.

3. Eaton Electrical Sector; Eaton Corporation; Cutler-Hammer Business Unit.

4. Rockwell Automation, Inc; Allen-Bradley Brand.

5. Schneider Electric USA, Inc.

6. Siemens Energy & Automation, Inc.

7. Yaskawa Electric America, Inc.

8. <Insert manufacturer's name>.

2.2 SYSTEM DESCRIPTION

Show VFC pole quantities, voltage, accessories, size and type, short-circuit current (withstand) rating (or available short-circuit currents), enclosure type, and features and accessories for each controller on Drawings. See "Specifying VFCs" Article and Editing Instruction No. 9 in the Evaluations for selection considerations.

A. General Requirements for VFCs:

1. VFCs and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

See Editing Instruction No. 10 in the Evaluations for subparagraph below.

2. Comply with NEMA ICS 7, NEMA ICS 61800-2, and [UL 508A] [UL 508C] <Insert standard>.

Retain first option in "Application" Paragraph below for constant-torque loads such as positive-displacement pumps and reciprocating and screw compressors; retain second option for variable-torque loads such as centrifugal blowers, compressors, fans, and pumps.

B. Application: [Constant torque] [and] [variable torque] <Insert application>.

Low-voltage VFCs are available for use with three-phase ac motors from 1/2 to 500 hp (depending on voltage rating), and in single- or three-phase input voltages from 200- to 575-V ac; however, not all listed manufacturers may offer VFCs in all these ratings and voltage ranges. Using single-phase voltages for VFCs controlling three-phase motors may require substantial derating of the VFCs; consult manufacturers for limitations and derating requirements.

C. VFC Description: Variable-frequency motor controller, consisting of power converter that employs pulse-width-modulated inverter, factory built and tested in an enclosure, with integral disconnecting means and overcurrent and overload protection; listed and labeled by an NRTL as a complete unit; arranged to provide self-protection, protection, and variable-speed control of one or more three-phase induction motors by adjusting output voltage and frequency.

1. Units suitable for operation of NEMA MG 1 motors.

2. Listed and labeled for integrated short-circuit current (withstand) rating by an NRTL acceptable to authorities having jurisdiction.

D. Design and Rating: Match load type, such as fans, blowers, and pumps; and type of connection used between motor and load such as direct or through a power-transmission connection.

Retain first option in "Output Rating" Paragraph below for variable-torque drives; retain second option for constant-torque drives.

E. Output Rating: Three phase; 10 to [60 Hz, with voltage proportional to frequency throughout voltage range] [66 Hz, with torque constant as speed changes]; maximum voltage equals input voltage.

F. Unit Operating Requirements:

Consult manufacturers if Project system conditions fall outside the selected parameters in first three subparagraphs below because corrective actions or additional modifications may be required before VFCs can be applied.

1. Input AC Voltage Tolerance: Plus 10 and minus [10] [15] percent of VFC input voltage rating.

2. Input AC Voltage Unbalance: Not exceeding [3] [5] percent.

3. Input Frequency Tolerance: Plus or minus 3 percent of VFC frequency rating.

4. Minimum Efficiency: [96] [97] <Insert number> percent at 60 Hz, full load.

5. Minimum Displacement Primary-Side Power Factor: [96] [98] <Insert number> percent under any load or speed condition.

Retain "Minimum Short-Circuit Current (Withstand) Rating" Subparagraph below if all VFCs on a Project are required to have the same short-circuit current rating. Delete subparagraph if short-circuit ratings vary for individual VFCs, and indicate the ratings on Drawings.

6. Minimum Short-Circuit Current (Withstand) Rating: [10] [22] [65] [100] <Insert value> kA.

See Editing Instruction No. 2 in the Evaluations. For additional ambient compensation requirements for fuses, circuit breakers, and overload relays, see Editing Instructions No. 4, No. 5, and No. 7 in the Evaluations.

7. Ambient Temperature Rating: Not less than 32 deg F (0 deg C) and not exceeding 104 deg F (40 deg C).

8. Humidity Rating: Less than 95 percent (noncondensing).

9. Altitude Rating: Not exceeding 3300 feet (1000 m).

Retain "Vibration Withstand" Subparagraph below if VFCs are likely to be installed on vibrating equipment such as a built-up air-handling unit or skid-mounted pump assembly.

10. Vibration Withstand: Comply with NEMA ICS 61800-2.

Retain first option in "Overload Capability" Subparagraph below for variable-torque VFCs; retain second option for constant-torque VFCs.

11. Overload Capability: [1.1] [1.5] times the base load current for 60 seconds; minimum of 1.8 times the base load current for three seconds.

12. Starting Torque: Minimum 100 percent of rated torque from 3 to 60 Hz.

13. Speed Regulation: Plus or minus [5] [10] percent.

Carrier frequencies above 2.5 kHz are seldom desired for motors more than 200 hp due to the increased possibility of overheating the motor windings. For large-horsepower motors being used with VFCs, consult motor manufacturers for recommended limitations on carrier frequencies to mitigate motor winding overtemperatures.

14. Output Carrier Frequency: Selectable; 0.5 to [15] <insert number> kHz.

15. Stop Modes: Programmable; includes fast, free-wheel, and dc injection braking.

G. Inverter Logic: Microprocessor based, [16] [32] bit, isolated from all power circuits.

H. Isolated Control Interface: Allows VFCs to follow remote-control signal over a minimum 40:1 speed range.

1. Signal: Electrical.

I. Internal Adjustability Capabilities:

1. Minimum Speed: 5 to 25 percent of maximum rpm.

2. Maximum Speed: 80 to 100 percent of maximum rpm.

3. Acceleration: [0.1 to 999.9] <Insert range> seconds.

4. Deceleration: [0.1 to 999.9] <Insert range> seconds.

5. Current Limit: 30 to minimum of 150 percent of maximum rating.

6. <Insert adjustment and parameters>.

J. Self-Protection and Reliability Features:

Coordinate Project-specific self-protection and reliability features with manufacturers, because standard and optional features vary considerably among manufacturers.

Retain one of two "Surge Suppression" subparagraphs below. Be consistent when selecting field-mounted or integral SPDs throughout Project.

1. Surge Suppression: Factory installed as an integral part of the VFC, complying with UL 1449 SPD, Type 1 or Type 2.

2. Surge Suppression: Field-mounted surge suppressors complying with Section 264313 "Surge Protection for Low-Voltage Electrical Power Circuits," UL 1449 SPD, Type 2.

3. Loss of Input Signal Protection: Selectable response strategy, including speed default to a percent of the most recent speed, a preset speed, or stop; with alarm.

4. Under- and overvoltage trips.

5. Inverter overcurrent trips.

6. VFC and Motor-Overload/Overtemperature Protection: Microprocessor-based thermal protection system for monitoring VFCs and motor thermal characteristics, and for providing VFC overtemperature and motor-overload alarm and trip; settings selectable via the keypad.

7. Critical frequency rejection, with [three] <Insert number> selectable, adjustable deadbands.

8. Instantaneous line-to-line and line-to-ground overcurrent trips.

9. Loss-of-phase protection.

10. Reverse-phase protection.

11. Short-circuit protection.

12. Motor-overtemperature fault.

13. <Insert protection or reliability feature>.

"Automatic Reset/Restart" and "Power-Interruption Protection" paragraphs below are mutually exclusive in the same VFC. Retain both paragraphs if required for separate VFCs, and indicate on Drawings where each type is required.

K. Automatic Reset/Restart: Attempt three restarts after drive fault or on return of power after an interruption and before shutting down for manual reset or fault correction; adjustable delay time between restart attempts.

L. Power-Interruption Protection: To prevent motor from re-energizing after a power interruption until motor has stopped, unless "Bidirectional Autospeed Search" feature is available and engaged.

Retain "Bidirectional Autospeed Search" Paragraph below if retaining "Automatic Reset/Restart" Paragraph above, field-selectable automatic and manual "Bypass Mode" Paragraph in "Bypass Systems" Article, or both.

M. Bidirectional Autospeed Search: Capable of starting VFC into rotating loads spinning in either direction and returning motor to set speed in proper direction, without causing damage to drive, motor, or load.

N. Torque Boost: Automatically varies starting and continuous torque to at least 1.5 times the minimum torque to ensure high-starting torque and increased torque at slow speeds.

O. Motor Temperature Compensation at Slow Speeds: Adjustable current fall-back based on output frequency for temperature protection of self-cooled, fan-ventilated motors at slow speeds.

Coordinate with manufacturers for available options. Coordinate selection of the disconnecting means and OCPD with short-circuit current (withstand) ratings required for Project. See "Application of Switches and Circuit Breakers" Article and Editing Instructions No. 3, No. 4, No. 5, and No. 8 in the Evaluations for selection considerations.

P. Integral Input Disconnecting Means and OCPD: [UL 489, instantaneous-trip circuit breaker] [UL 489, molded-case switch, with power fuse block and current-limiting fuses] [UL 489, thermal-magnetic circuit breaker] [NEMA KS 1, nonfusible switch, with power fuse block and current-limiting fuses] [NEMA KS 1, fusible switch] with pad-lockable, door-mounted handle mechanism.

Retain first "Disconnect Rating" Subparagraph below for VFCs without bypass systems; retain second for VFCs with bypass systems.

1. Disconnect Rating: Not less than 115 percent of VFC input current rating.

2. Disconnect Rating: Not less than 115 percent of NFPA 70 motor full-load current rating or VFC input current rating, whichever is larger.

Retain "Auxiliary Contacts" Subparagraph below if retaining fusible or nonfusible switches in "Integral Input Disconnecting Means and OCPD" Paragraph above and using external control power; or, use for remote indication of disconnecting means position.

3. Auxiliary Contacts: NO or NC, arranged to activate before switch blades open.

Retain one of or both subparagraphs below if retaining any circuit-breaker-type disconnecting means in "Integral Input Disconnecting Means and OCPD" Paragraph above. Retain first subparagraph if using external control power or for remote indication of disconnecting means position. Retain second subparagraph for remote indication of tripped condition. If retaining auxiliary and alarm contacts, indicate "a" and "b" contact quantities and NO or NC contact requirements on Drawings.

4. Auxiliary contacts "a" and "b" arranged to activate with circuit-breaker handle.

5. [NC] [NO] alarm contact that operates only when circuit breaker has tripped.

2.3 PERFORMANCE REQUIREMENTS

Retain "Seismic Performance" Paragraph below with "Seismic Qualification Certificates" Paragraph in "Informational Submittals" Article for projects requiring seismic design. Delete paragraph if performance requirements are indicated on Drawings. Model building codes and ASCE/SEI 7 establish criteria for buildings subject to earthquake motions. Coordinate requirements with structural engineer.

A. Seismic Performance: VFCs shall withstand the effects of earthquake motions determined according to ASCE/SEI 7. The designated VFCs shall be tested and certified by an NRTL as meeting the ICC-ES AC 156 test procedure requirements.

Retain subparagraph below to define the term "withstand" as it applies to this Project. Definition varies with type of building and occupancy and is critical to valid certification. Option is used for essential facilities where equipment must operate immediately after an earthquake.

1. The term "withstand" means "the unit will remain in place without separation of any parts when subjected to the seismic forces specified[ and the unit will be fully operational after the seismic event]."

2.4 CONTROLS AND INDICATION

Coordinate local control and indication requirements with Owner or end users. Most of the indications included in "Status Lights" Paragraph below can be and are accomplished by listed manufacturers through digital displays in their panel-mounted operator stations. However, many operators still prefer the ability to "pass and glance" to determine the status of operating machinery or equipment.

A. Status Lights: Door-mounted LED indicators displaying the following conditions:

1. Power on.

2. Run.

3. Overvoltage.

4. Line fault.

5. Overcurrent.

6. External fault.

7. <Insert condition>.

B. Panel-Mounted Operator Station: Manufacturer's standard front-accessible, sealed keypad and plain-English-language digital display; allows complete programming, program copying, operating, monitoring, and diagnostic capability.

1. Keypad: In addition to required programming and control keys, include keys for HAND, OFF, and AUTO modes.

2. Security Access: Provide electronic security access to controls through identification and password with at least one level of access: View only; view and operate; and view, operate, and service.

a. Control Authority: Supports at least four conditions: Off, local manual control at VFC, local automatic control at VFC, and automatic control through a remote source.

C. Historical Logging Information and Displays:

Retain first subparagraph below if time and date stamping is not accomplished through the BAS. Several listed manufacturers treat this feature as an added-cost option.

1. Real-time clock with current time and date.

2. Running log of total power versus time.

3. Total run time.

4. Fault log, maintaining last [four] <Insert number> faults with time and date stamp for each.

5. <Insert information or display>.

D. Indicating Devices: Digital display[ and additional readout devices as required,] mounted flush in VFC door and connected to display VFC parameters including, but not limited to:

1. Output frequency (Hz).

2. Motor speed (rpm).

3. Motor status (running, stop, fault).

4. Motor current (amperes).

5. Motor torque (percent).

6. Fault or alarming status (code).

7. PID feedback signal (percent).

8. DC-link voltage (V dc).

9. Set point frequency (Hz).

10. Motor output voltage (V ac).

11. <Insert parameter>.

Coordinate "Control Signal Interfaces" and "PID Control Interface" paragraphs below with Section 230900 "Instrumentation and Control for HVAC."Section 15900 "HVAC Instrumentation and Controls." Retain paragraphs to suit Project. If retaining more than one paragraph, indicate here or on Drawings where each interface type is required.

E. Control Signal Interfaces:

1. Electric Input Signal Interface:

In first subparagraph below, some manufacturers offer an operator-selectable "x"- to "y"-mA dc signal input.

a. A minimum of [two] <Insert number> programmable analog inputs: [0- to 10-V dc] [4- to 20-mA dc] [Operator-selectable "x"- to "y"-mA dc] <Insert signal parameters>.

b. A minimum of [six] <Insert number> multifunction programmable digital inputs.

2. Remote Signal Inputs: Capability to accept any of the following speed-setting input signals from the BAS or other control systems:

a. 0- to 10-V dc.

b. 4- to 20-mA dc.

c. Potentiometer using up/down digital inputs.

d. Fixed frequencies using digital inputs.

e. <Insert signal input>.

3. Output Signal Interface: A minimum of [one] <Insert number> programmable analog output signal(s) ([0- to 10-V dc] [4- to 20-mA dc] [operator-selectable "x"- to "y"-mA dc] <Insert signal parameters>), which can be configured for any of the following:

a. Output frequency (Hz).

b. Output current (load).

c. DC-link voltage (V dc).

d. Motor torque (percent).

e. Motor speed (rpm).

f. Set point frequency (Hz).

g. <Insert indication>.

Retain "PID Control Interface" Paragraph below if VFC controls interface directly with local controls and not through a BAS.

F. PID Control Interface: Provides closed-loop set point, differential feedback control in response to dual feedback signals. Allows for closed-loop control of fans and pumps for pressure, flow, or temperature regulation.

1. Number of Loops: [One] [Two] <Insert number>.

2.5 BYPASS SYSTEMS

Retain this article only if VFCs will require bypass systems. See "Bypass Systems" Article in the Evaluations for guidance, and coordinate with manufacturers for available selections.

A. Bypass Operation: Manually transfers motor between power converter output and bypass circuit. Unit is capable of stable operation (starting, stopping, and running) with motor completely disconnected from power converter.

B. Bypass Mode: Manual operation only; requires local operator selection at VFC. Transfer between power converter and bypass contactor, and retransfer shall only be allowed with the motor at zero speed.

C. Bypass Controller: Two-contactor-style bypass allows motor operation via the power converter or the bypass controller[; with input isolating switch and barrier arranged to isolate the power converter and permit safe troubleshooting and testing, both energized and de-energized, while motor is operating in bypass mode].

In "Bypass Contactor" Subparagraph below, IEC-rated contactors are most often used for the bypass contactor in HVAC applications and for smaller motors, and they are usually smaller and less costly than equivalent NEMA-rated contactors. NEMA-rated contactors are most often used in industrial applications and for larger motors, where they must carry high motor inrush and full-load running currents. IEC-rated contactors are most often used in all applications for the isolating contactors, because they are only used to isolate the power converter and normally do not carry any current. Consult manufacturers for the types used for each.

1. Bypass Contactor: Load-break, [IEC] [NEMA]-rated contactor.

2. Output Isolating Contactor: Non-load-break, [IEC] [NEMA]-rated contactor.

Retain "Isolating Switch" Subparagraph below if retaining option in "Bypass Controller" Paragraph above.

3. Isolating Switch: Non-load-break switch arranged to isolate power converter and permit safe troubleshooting and testing of the power converter, both energized and de-energized, while motor is operating in bypass mode; pad-lockable, door-mounted handle mechanism.

D. Bypass Contactor Configuration: [Full-voltage (across-the-line)] [Reduced-voltage (autotransformer)] <Insert type> type.

1. NORMAL/BYPASS selector switch.

Retain first subparagraph below only if retaining field-selectable automatic and manual "Bypass Mode" Paragraph above.

2. HAND/OFF/AUTO selector switch.

3. NORMAL/TEST Selector Switch: Allows testing and adjusting of VFC while the motor is running in the bypass mode.

4. Contactor Coils: Pressure-encapsulated type[ with coil transient suppressors].

a. Operating Voltage: Depending on contactor NEMA size and line-voltage rating, manufacturer's standard matching control power or line voltage.

b. Power Contacts: Totally enclosed, double break, and silver-cadmium oxide; assembled to allow inspection and replacement without disturbing line or load wiring.

5. Control Circuits: [120] <Insert number>-V ac; obtained from [integral CPT, with primary and secondary fuses] <Insert source of control power>, with [CPT] [control power source] of sufficient capacity to operate all integral devices and remotely located pilot, indicating, and control devices.

a. CPT Spare Capacity: 100 VA.

6. Overload Relays: NEMA ICS 2.

2.6 OPTIONAL FEATURES

See "Optional Features" Article in the Evaluations for additional guidance, and consult manufacturers for availability of, and limitations on, other options.

A. Damper control circuit with end-of-travel feedback capability.

B. Firefighter's Override (Smoke Purge) Input: On a remote contact closure from [the firefighter's control station] [smoke-control fan controller] <Insert location>, this password-protected input:

1. Overrides all other local and external inputs (analog/digital, serial communication, and all keypad commands).

Retain one of first two subparagraphs below.

2. Forces VFC to operate motor, without any other run or speed command, at a field-adjustable, preset speed.

3. Forces VFC to transfer to bypass mode and operate motor at full speed.

4. Causes display of override mode on the VFC display.

5. Reset VFC to normal operation on removal of override signal [automatically] [manually].

C. Communication Port: RS-232 port, USB 2.0 port, or equivalent connection capable of connecting a printer[ and a notebook computer].

D. <Insert feature>.

2.7 ENCLOSURES

A. VFC Enclosures: NEMA 250, to comply with environmental conditions at installed location.

See "Enclosures" Article in the Evaluations for discussion of enclosure types.

1. Dry and Clean Indoor Locations: [Type 1] <Insert type>.

2. Outdoor Locations: [Type 3R] [Type 4X] <Insert type>.

3. [Kitchen] [Wash-Down] Areas: [Type 4X] <Insert type>, [stainless steel] <Insert material>.

4. Other Wet or Damp Indoor Locations: [Type 4] <Insert type>.

5. Indoor Locations Subject to Dust, Falling Dirt, and Dripping Noncorrosive Liquids: Type 12.

6. <Insert enclosure requirements>.

Retain "Plenum Rating" Paragraph below when installing the VFC in plenums (e.g., in the air stream inside an air-handling unit) or in a space used for environmental air (e.g., above a suspended ceiling used for return air). Some authorities having jurisdiction require that a label verifying the rating be prominently displayed on the VFC enclosure.

B. Plenum Rating: UL 1995; NRTL certification label on enclosure, clearly identifying VFC as "Plenum Rated."

2.8 ACCESSORIES

Indicate requirements for and quantities of accessories on Drawings. See "Accessories" Article in the Evaluations for additional guidance; consult manufacturers for availability of, and limitations on, other accessories.

A. General Requirements for Control-Circuit and Pilot Devices: NEMA ICS 5; factory installed in VFC enclosure cover unless otherwise indicated.

1. Push Buttons: [Covered] [Unguarded].

2. Pilot Lights: Push to test.

3. Selector Switches: Rotary type.

B. [NC] [NO] [Reversible NC/NO] bypass contactor auxiliary contact(s).

C. Control Relays: Auxiliary and adjustable [pneumatic] [solid-state] time-delay relays.

Features in "Phase-Failure, Phase-Reversal, and Undervoltage and Overvoltage Relays" Paragraph below provide one method of protecting against input circuit anomalies while in the bypass mode. They are available in individual relays or combined into a single multipurpose relay, and they would only be required if retaining "Bypass Systems" Article. Because features below may not be available from all listed manufacturers, other methods of providing redundant control of motor loads served may be required; consult manufacturers for availability. Consider specifying phase-failure relays for single-phasing protection when fuses are retained with the bypass feature, if solid-state overload relays are unspecified.

D. Phase-Failure, Phase-Reversal, and Undervoltage and Overvoltage Relays: Solid-state sensing circuit with isolated output contacts for hard-wired connections. Provide adjustable undervoltage, overvoltage, and time-delay settings.

1. Current Transformers: Continuous current rating, basic impulse insulating level (BIL) rating, burden, and accuracy class suitable for connected circuitry. Comply with IEEE C57.13.

E. Supplemental Digital Meters:

1. Elapsed-time meter.

2. Kilowatt meter.

3. Kilowatt-hour meter.

F. Breather and drain assemblies, to maintain interior pressure and release condensation in NEMA 250, [Type 4] [Type 4X] [Type 12] <Insert type> enclosures installed outdoors or in unconditioned interior spaces subject to humidity and temperature swings.

G. Space heaters, with NC auxiliary contacts, to mitigate condensation in NEMA 250, [Type 3R] [Type 4X] [Type 12] <Insert type> enclosures installed outdoors or in unconditioned interior spaces subject to humidity and temperature swings.

H. Cooling Fan and Exhaust System: For NEMA 250, [Type 1] [Type 12] <Insert enclosure type>; UL 508 component recognized: Supply fan, with [composite] [stainless-steel] <Insert material> intake and exhaust grills [and filters]; [120] <Insert number>-V ac; obtained from [integral CPT] <Insert source of control power>.

I. <Insert accessory>.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Wall-Mounting Controllers: Install with tops at uniform height and with disconnect operating handles not higher than 79 inches (2000 mm) above finished floor, unless otherwise indicated, and by bolting units to wall or mounting on lightweight structural-steel channels bolted to wall. For controllers not on walls, provide freestanding racks complying with Section 260529 "Hangers and Supports for Electrical Systems."

Retain "Roof-Mounting Controllers" Paragraph below for equipment supported on roofs.

B. Roof-Mounting Controllers: Install VFC on roofs with tops at uniform height and with disconnect operating handles not higher than 79 inches (2000 mm) above finished roof surface unless otherwise indicated, and by bolting units to curbs or mounting on freestanding, lightweight, structural-steel channels bolted to curbs. Seal roof penetrations after raceways are installed.

1. Curbs and roof penetrations are specified in Section 077200 "Roof Accessories."

2. Structural-steel channels are specified in Section 260529 "Hangers and Supports for Electrical Systems."

Retain "Seismic Bracing" Paragraph below if seismic controls are Project requirement. Coordinate with Drawings and Sections specifying vibration and seismic controls.

C. Seismic Bracing: Comply with requirements specified in Section 260548.16 "Seismic Controls for Electrical Systems."

D. Temporary Lifting Provisions: Remove temporary lifting eyes, channels, and brackets and temporary blocking of moving parts from enclosures and components.

Retain first four paragraphs below, as appropriate, to coincide with retained VFC features and attributes.

E. Install fuses in each fusible-switch VFC.

F. Install fuses in control circuits if not factory installed. Comply with requirements in Section 262813 "Fuses."

G. Install heaters in thermal-overload relays. Select heaters based on actual nameplate full-load amperes after motors are installed.

H. Install, connect, and fuse thermal-protector monitoring relays furnished with motor-driven equipment.

I. Comply with NECA 1.

3.2 CONTROL WIRING INSTALLATION

Retain this article if applicable or if remote control or indication is required.

A. Install wiring between VFCs and remote devices[ and facility's central-control system]. Comply with requirements in Section 260523 "Control-Voltage Electrical Power Cables."

B. Bundle, train, and support wiring in enclosures.

3.3 IDENTIFICATION

A. Identify VFCs, components, and control wiring. Comply with requirements for identification specified in Section 260553 "Identification for Electrical Systems."

1. Identify field-installed conductors, interconnecting wiring, and components; provide warning signs.

2. Label each VFC with engraved nameplate.

3. Label each enclosure-mounted control and pilot device.

3.4 FIELD QUALITY CONTROL

A. Perform tests and inspections[ with the assistance of a factory-authorized service representative].

B. Acceptance Testing Preparation:

1. Test insulation resistance for each VFC element, bus, component, connecting supply, feeder, and control circuit.

2. Test continuity of each circuit.

C. Tests and Inspections:

1. Inspect VFC, wiring, components, connections, and equipment installation.[ Test and adjust controllers, components, and equipment.]

2. Test insulation resistance for each VFC element, component, connecting motor supply, feeder, and control circuits.

3. Test continuity of each circuit.

In first subparagraph below, the 10 percent voltage variation is a functional issue. Where ASHRAE 90.1 is Project's applicable energy code, further restrictions in voltage drop are required.

4. Verify that voltages at VFC locations are within 10 percent of motor nameplate rated voltages. If outside this range for any motor, notify [Architect] [Construction Manager] [Owner] before starting the motor(s).

5. Test each motor for proper phase rotation.

6. Perform tests according to the Inspection and Test Procedures for Adjustable Speed Drives stated in NETA Acceptance Testing Specification. Certify compliance with test parameters.

7. Correct malfunctioning units on-site, where possible, and retest to demonstrate compliance; otherwise, replace with new units and retest.

8. Test and adjust controls, remote monitoring, and safeties. Replace damaged and malfunctioning controls and equipment.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

D. VFCs will be considered defective if they do not pass tests and inspections.

Retain paragraph below if tests and inspections are performed by Contractor or manufacturer's field-service representative engaged by Contractor.

E. Prepare test and inspection reports, including a certified report that identifies the VFC and describes scanning results. Include notation of deficiencies detected, remedial action taken, and observations made after remedial action.

3.5 ADJUSTING

Retain applicable paragraphs below to correspond to selections made in Part 2.

A. Program microprocessors for required operational sequences, status indications, alarms, event recording, and display features. Clear events memory after final acceptance testing and prior to Substantial Completion.

First two paragraphs below pertain primarily to VFCs with bypass systems. Retain if retaining "Bypass Systems" Article.

B. Set field-adjustable switches, auxiliary relays, time-delay relays, timers, and overload-relay pickup and trip ranges.

C. Adjust the trip settings of instantaneous-only circuit breakers and thermal-magnetic circuit breakers with adjustable, instantaneous trip elements. Initially adjust to 6 times the motor nameplate full-load amperes and attempt to start motors several times, allowing for motor cool-down between starts. If tripping occurs on motor inrush, adjust settings in increments until motors start without tripping. Do not exceed 8 times the motor full-load amperes (or 11 times for NEMA Premium Efficient motors if required). Where these maximum settings do not allow starting of a motor, notify [Architect] [Construction Manager] [Owner] before increasing settings.

D. Set the taps on reduced-voltage autotransformer controllers.

Retain option in first paragraph below unless settings are included on Drawings.

E. Set field-adjustable circuit-breaker trip ranges[ as specified in Section 260573 "Overcurrent Protective Device Coordination Study."]

F. Set field-adjustable pressure switches.

3.6 DEMONSTRATION

A. Train Owner's maintenance personnel to adjust, operate, reprogram, and maintain VFCs.

END OF SECTION 262923

	VARIABLE-FREQUENCY MOTOR CONTROLLERS
	262923 - 1



