Copyright 2012 AIA
MasterSpec Professional
03/12

Copyright 2012 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 263213 - ENGINE GENERATORS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. This Section includes packaged engine-generator sets for [emergency] [standby] power supply with the following features:

Adjust list below to suit Project.

1. [Gas] [Diesel] engine.

2. [Unit-mounted] [Remote-mounting] cooling system.

3. [Unit-mounted] [Remote-mounting] control and monitoring.

4. Outdoor enclosure.

B. See Section 263600 "Transfer Switches" for transfer switches including sensors and relays to initiate automatic-starting and -stopping signals for engine-generator sets.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of packaged engine generator and accessory indicated.

B. Shop Drawings: Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

1.3 INFORMATIONAL SUBMITTALS

Retain paragraph and subparagraphs below if required by seismic criteria applicable to Project. Coordinate with Section 260548.16 "Seismic Controls for Electrical Systems."

A. Manufacturer Seismic Qualification Certification: Submit certification that engine-generator set, batteries, battery racks, accessories, and components will withstand seismic forces defined in Section 260548.16 "Seismic Controls for Electrical Systems." Include the following:

1. Basis for Certification: Indicate whether withstand certification is based on actual test of assembled components or on calculation.

Retain one of first two subparagraphs below to define the term "withstand" as it applies to this Project. Definition varies with type of building and occupancy and is critical to valid certification. Second definition is used for essential facilities where equipment must operate immediately after an earthquake.

a. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified."

b. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified and the unit will be fully operational after the seismic event."

2. Dimensioned Outline Drawings of Equipment Unit: Identify center of gravity and locate and describe mounting and anchorage provisions.

3. Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

Coordinate paragraph below with Part 2 "Source Quality Control" Article.

B. Source quality-control test reports.

Retain first paragraph below if Contractor is responsible for field quality-control testing.

C. Field quality-control test reports.

D. Warranty: Special warranty specified in this Section.

1.4 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

1.5 QUALITY ASSURANCE

A. Installer Qualifications: Manufacturer's authorized representative who is trained and approved for installation of units required for this Project.

B. Manufacturer Qualifications: A qualified manufacturer. Maintain, within [200 miles (321 km)] <Insert number of miles (kilometers)> of Project site, a service center capable of providing training, parts, and emergency maintenance repairs.

C. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

D. Comply with ASME B15.1.

E. Comply with NFPA 37.

F. Comply with NFPA 70.

Retain paragraph below for healthcare facilities.

G. Comply with NFPA 99.

Retain first paragraph below if generator is automatically started. See Editing Instruction No. 4 in the Evaluations.

H. Comply with NFPA 110 requirements for Level [1] [2] emergency power supply system.

I. Comply with UL 2200.

Retain paragraph below for state or local compliance.

J. Engine Exhaust Emissions: Comply with applicable state and local government requirements.

Retain paragraph below for installations with critical noise-abatement requirements, particularly outdoor generator sets. Coordinate with noise-reduction features in the design, including those relating to cooling-air intake and discharge arrangement and muffler specification and its location and orientation as shown on Drawings.

K. Noise Emission: Comply with [applicable state and local government requirements] <Insert Project criteria> for maximum noise level at [adjacent property boundaries] <Insert critical locations> due to sound emitted by generator set including engine, engine exhaust, engine cooling-air intake and discharge, and other components of installation.

1.6 PROJECT CONDITIONS

A. Environmental Conditions: Engine-generator system shall withstand the following environmental conditions without mechanical or electrical damage or degradation of performance capability:

Retain first option in subparagraph below if generator-set start time must be within NFPA 110 limits. This temperature range usually implies installation indoors in heated space. Coordinate with Drawings.

1. Ambient Temperature: [5 to 40 deg C] [Minus 15 to plus 40 deg C].

Delete first subparagraph below for outdoor units.

2. Relative Humidity: 0 to 95 percent.

3. Altitude: Sea level to [1000 feet (300 m)] <Insert altitude>.

1.7 WARRANTY

A. Special Warranty: Manufacturer's standard form in which manufacturer agrees to repair or replace components of packaged engine generators and associated auxiliary components that fail in materials or workmanship within specified warranty period.

Verify available warranties for units and components and insert number below.

1. Warranty Period: <Insert number> years from date of Substantial Completion.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products. Retain one of three paragraphs and list of manufacturers in this Article. See Section 016000 "Product Requirements."

A. Available Manufacturers: Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

B. Manufacturers: Subject to compliance with requirements, provide products by one of the following:

C. Basis-of-Design Product: Subject to compliance with requirements, provide [the product indicated on Drawings] <Insert manufacturer's name; product name or designation> or a comparable product by one of the following:

1. Caterpillar; Engine Div.

2. Generac Power Systems, Inc.

3. Kohler Co.

4. Magnetek, Inc.

5. Onan/Cummins Power Generation; Industrial Business Group.

6. Spectrum Detroit Diesel.

7. <Insert manufacturer's name.>

2.2 ENGINE-GENERATOR SET

A. Factory-assembled and -tested, engine-generator set.

B. Mounting Frame: Maintain alignment of mounted components without depending on concrete foundation; and have lifting attachments.

Coordinate paragraph and subparagraphs below with prototype test requirements in Part 1 "Informational Submittals" Article and in Part 2 "Source Quality Control" Article.

C. Capacities and Characteristics:

1. Power Output Ratings: Nominal ratings as indicated[, with capacity as required to operate as a unit as evidenced by records of prototype testing].

2. Output Connections: Three-phase, [three] [four] wire.

3. Nameplates: For each major system component to identify manufacturer's name and address, and model and serial number of component.

Retain paragraph and subparagraphs below for loads involving little or no sensitive electronic equipment, adjustable frequency drives, or uninterruptible power supply systems. See Evaluations.

D. Generator-Set Performance:

1. Steady-State Voltage Operational Bandwidth: 3 percent of rated output voltage from no load to full load.

2. Transient Voltage Performance: Not more than 20 percent variation for 50 percent step-load increase or decrease. Voltage shall recover and remain within the steady-state operating band within three seconds.

3. Steady-State Frequency Operational Bandwidth: 0.5 percent of rated frequency from no load to full load.

4. Steady-State Frequency Stability: When system is operating at any constant load within the rated load, there shall be no random speed variations outside the steady-state operational band and no hunting or surging of speed.

5. Transient Frequency Performance: Less than 5 percent variation for 50 percent step-load increase or decrease. Frequency shall recover and remain within the steady-state operating band within five seconds.

6. Output Waveform: At no load, harmonic content measured line to line or line to neutral shall not exceed 5 percent total and 3 percent for single harmonics. Telephone influence factor, determined according to NEMA MG 1, shall not exceed 50 percent.

7. Sustained Short-Circuit Current: For a 3-phase, bolted short circuit at system output terminals, system shall supply a minimum of 250 percent of rated full-load current for not less than 10 seconds and then clear the fault automatically, without damage to generator system components.

Below requires 10-second maximum start time under specific conditions and includes startup only, not load assumption.

8. Start Time: Comply with NFPA 110, Type 10, system requirements.

2.3 ENGINE

Depending on NFPA 110 class and local codes, LP-gas standby may not be required for natural gas-fueled systems. Verify requirements with authorities having jurisdiction.

A. Fuel: [Fuel oil, Grade DF-2] [Natural gas with automatic LP-gas standby] [Natural gas].

1. <Insert specific fuel grade requirements.>

B. Rated Engine Speed: 1800 rpm.

C. Maximum Piston Speed for Four-Cycle Engines: 2250 fpm (11.4 m/s).

D. Lubrication System: The following items are mounted on engine or skid:

1. Filter and Strainer: Rated to remove 90 percent of particles 5 micrometers and smaller while passing full flow.

2. Thermostatic Control Valve: Control flow in system to maintain optimum oil temperature. Unit shall be capable of full flow and is designed to be fail-safe.

3. Crankcase Drain: Arranged for complete gravity drainage to an easily removable container with no disassembly and without use of pumps, siphons, special tools, or appliances.

E. Engine Fuel System:

Retain first two subparagraphs below for diesel-fueled engine; retain third subparagraph and associated subparagraphs for natural-gas- and LP-gas-fueled engine.

1. Main Fuel Pump: Mounted on engine. Pump ensures adequate primary fuel flow under starting and load conditions.

2. Relief-Bypass Valve: Automatically regulates pressure in fuel line and returns excess fuel to source.

3. Dual Natural Gas with LP-Gas Backup (Vapor-Withdrawal) System:

a. Carburetor.

b. Secondary Gas Regulators: One for each fuel type.

c. Fuel-Shutoff Solenoid Valves: One for each fuel source.

d. Flexible Fuel Connectors: One for each fuel source.

Retain paragraph below where required by NFPA 110, which prescribes engine water-jacket temperature requirements. Coordinate with Drawings for electrical supply.

F. Coolant Jacket Heater: Electric-immersion type, factory installed in coolant jacket system. Comply with NFPA 110 requirements for Level 1 equipment for heater capacity.

G. Governor: Adjustable isochronous, with speed sensing.

H. Cooling System: Closed loop, liquid cooled, with radiator factory mounted on engine-generator-set mounting frame and integral engine-driven coolant pump.

1. Coolant: Solution of 50 percent ethylene-glycol-based antifreeze and 50 percent water, with anticorrosion additives as recommended by engine manufacturer.

2. Temperature Control: Self-contained, thermostatic-control valve modulates coolant flow automatically to maintain optimum constant coolant temperature as recommended by engine manufacturer.

Retain one of three "Muffler/Silencer" paragraphs below. Modify dBA requirement in second subparagraph to accommodate environment in which engine-generator set is operating. If unit is specified with an enclosure, consider specifying sound level requirements at specified distance from enclosure on each of four sides.

I. Muffler/Silencer: Critical type, sized as recommended by engine manufacturer and selected with exhaust piping system to not exceed engine manufacturer's engine backpressure requirements.

1. Minimum sound attenuation of 25 dB at 500 Hz.

2. Sound level measured at a distance of 10 feet (3 m) from exhaust discharge after installation is complete shall be [85] <Insert number> dBA or less.

J. Muffler/Silencer: Residential type, sized as recommended by engine manufacturer and selected with exhaust piping system to not exceed engine manufacturer's engine backpressure requirements.

1. Minimum sound attenuation of 18 dB at 500 Hz.

2. Sound level measured at a distance of 10 feet (3 m) from exhaust discharge after installation is complete shall be [95] <Insert number> dBA or less.

K. Muffler/Silencer: Industrial type, sized as recommended by engine manufacturer and selected with exhaust piping system to not exceed engine manufacturer's engine backpressure requirements.

1. Minimum sound attenuation of 12 dB at 500 Hz.

2. Sound level measured at a distance of 25 feet (8 m) from exhaust discharge after installation is complete shall be [87] <Insert number> dBA or less.

Retain second option in paragraph below if filters may not be serviced as often as recommended. If air contaminant level is excessive, consult manufacturers to determine if special filtration of combustion air is needed.

L. Air-Intake Filter: [Standard] [Heavy]-duty, engine-mounted air cleaner with replaceable dry-filter element and "blocked filter" indicator.

Select first option in paragraph below for smaller engine-generator sets. Retain second option for units 175 kW and larger.

M. Starting System: [12] [24]-V electric, with negative ground.

1. Components: Sized so they will not be damaged during a full engine-cranking cycle with ambient temperature at maximum specified in Part 1 "Project Conditions" Article.

2. Cranking Motor: Heavy-duty unit that automatically engages and releases from engine flywheel without binding.

Retain first option in first subparagraph below if system description in Part 1 "Quality Assurance" Article specifies NFPA 110, Level 1 or 2; otherwise, retain second. See Editing Instruction No. 7 in the Evaluations.

3. Cranking Cycle: [As required by NFPA 110 for system level specified] [60 seconds].

4. Battery: Adequate capacity within ambient temperature range specified in Part 1 "Project Conditions" Article to provide specified cranking cycle at least twice without recharging.

5. Battery-Charging Alternator: Factory mounted on engine with solid-state voltage regulation and 35-A minimum continuous rating.

Coordinate subparagraph below with Section 263600 "Transfer Switches." Retain if battery charger is not specified to be integral with transfer switch.

a. Battery Charger: Current-limiting, automatic-equalizing and float-charging type. Unit shall comply with UL 1236.

2.4 FUEL OIL STORAGE

Retain this Article for diesel-engine units.

A. Comply with NFPA 30.

B. Base-Mounted Fuel Oil Tank: Factory installed and piped, complying with UL 142 fuel oil tank. Features include the following:

1. Tank level indicator.

Consult tank manufacturers about capacities available for size of set in Project.

2. Capacity: Fuel for [eight] <Insert number> hours' continuous operation at 100 percent rated power output.

3. Vandal-resistant fill cap.

Determine applicable codes and regulations, and coordinate subparagraph below with Drawings.

4. Containment Provisions: Comply with requirements of authorities having jurisdiction.

2.5 CONTROL AND MONITORING

This Article specifies the subsystem that monitors, protects, and controls the engine generator. See Editing Instruction No. 8 in the Evaluations.

Retain first paragraph below for automatically starting systems; retain second paragraph for manually starting systems.

A. Automatic Starting System Sequence of Operation: When mode-selector switch on the control and monitoring panel is in the automatic position, remote-control contacts in one or more separate automatic transfer switches initiate starting and stopping of generator set. When mode-selector switch is switched to the on position, generator set starts. The off position of same switch initiates generator-set shutdown. When generator set is running, specified system or equipment failures or derangements automatically shut down generator set and initiate alarms.

B. Manual Starting System Sequence of Operation: Switching on-off switch on the generator control panel to the on position starts generator set. The off position of same switch initiates generator-set shutdown. When generator set is running, specified system or equipment failures or derangements automatically shut down generator set and initiate alarms.

C. Configuration: Operating and safety indications, protective devices, basic system controls, and engine gages shall be grouped in a common control and monitoring panel mounted on the generator set. Mounting method shall isolate the control panel from generator-set vibration.

D. Indicating and Protective Devices and Controls: As required by NFPA 110 for Level [1] [2] system, and the following:

1. AC voltmeter.

2. AC ammeter.

3. AC frequency meter.

4. DC voltmeter (alternator battery charging).

5. Engine-coolant temperature gage.

6. Engine lubricating-oil pressure gage.

7. Running-time meter.

8. Ammeter-voltmeter, phase-selector switch(es).

9. Generator-voltage adjusting rheostat.

Two subparagraphs below are optional devices.

10. Fuel tank derangement alarm.

11. Fuel tank high-level shutdown of fuel supply alarm.

Retain subparagraph below for units with "generator-protector" feature.

12. Generator overload.

E. Supporting Items: Include sensors, transducers, terminals, relays, and other devices and include wiring required to support specified items. Locate sensors and other supporting items on engine or generator, unless otherwise indicated.

F. Common Remote Audible Alarm: Comply with NFPA 110 requirements for Level 1 systems. Include necessary contacts and terminals in control and monitoring panel.

1. Overcrank shutdown.

2. Coolant low-temperature alarm.

3. Control switch not in auto position.

4. Battery-charger malfunction alarm.

5. Battery low-voltage alarm.

Retain paragraph below and coordinate with Drawings for systems required to comply with NFPA 99 or where otherwise needed. Revise if all indications required by NFPA 99 are not needed.

G. Remote Alarm Annunciator: Comply with NFPA 99. An LED labeled with proper alarm conditions shall identify each alarm event and a common audible signal shall sound for each alarm condition. Silencing switch in face of panel shall silence signal without altering visual indication. Connect so that after an alarm is silenced, clearing of initiating condition will reactivate alarm until silencing switch is reset. Cabinet and faceplate are surface- or flush-mounting type to suit mounting conditions indicated.

2.6 GENERATOR OVERCURRENT AND FAULT PROTECTION

Retain paragraph and subparagraphs below for units smaller than 200 kW where initial cost is a concern. Device provides little or no generator protection and no selectivity with downstream circuit protective devices.

A. Generator Circuit Breaker: Molded-case, thermal-magnetic type; 100 percent rated; complying with NEMA AB 1 and UL 489.

1. Tripping Characteristic: Designed specifically for generator protection.

2. Trip Rating: Matched to generator rating.

3. Shunt Trip: Connected to trip breaker when generator set is shut down by other protective devices.

4. Mounting: Adjacent to or integrated with control and monitoring panel.

Retain paragraph below and coordinate with Drawings for legally required emergency generator sets rated 1000 A and more at 277/480 V.

B. Ground-Fault Indication: Comply with NFPA 70, "Emergency System" signals for ground-fault. Integrate ground-fault alarm indication with other generator-set alarm indications.

2.7 GENERATOR, EXCITER, AND VOLTAGE REGULATOR

A. Comply with NEMA MG 1.

B. Drive: Generator shaft shall be directly connected to engine shaft. Exciter shall be rotated integrally with generator rotor.

C. Electrical Insulation: Class H or Class F.

D. Stator-Winding Leads: Brought out to terminal box to permit future reconnection for other voltages if required.

E. Construction shall prevent mechanical, electrical, and thermal damage due to vibration, overspeed up to 125 percent of rating, and heat during operation at 110 percent of rated capacity.

F. Enclosure: Dripproof.

Delete first paragraph below if instrument transformers are housed in control and power panel.

G. Instrument Transformers: Mounted within generator enclosure.

H. Voltage Regulator: Solid-state type, separate from exciter, providing performance as specified.

1. Adjusting rheostat on control and monitoring panel shall provide plus or minus 5 percent adjustment of output-voltage operating band.

Retain paragraph below for high-humidity environments to limit condensation in alternator windings.

I. Strip Heater: Thermostatically controlled unit arranged to maintain stator windings above dew point.

Retain both paragraphs below for units specified for "critical" performance. Coordinate with generator-set performance Paragraph selected in "Engine-Generator Set" Article. See "Specifying Considerations" Article in the Evaluations for discussions on sensitive electronic equipment and nonlinear generator loads and on supplying significant harmonic currents.

J. Windings: Two-thirds pitch stator winding and fully linked amortisseur winding.

K. Subtransient Reactance: [12] <Insert number> percent, maximum.

2.8 OUTDOOR GENERATOR-SET ENCLOSURE

Retain one of two paragraphs and associated subparagraphs below and coordinate with Drawings to define basic outdoor-enclosure type. Edit to specify enclosure features required.

A. Description: Vandal-resistant, weatherproof steel housing, wind resistant up to 100 mph (160 km/h). Multiple panels shall be lockable and provide adequate access to components requiring maintenance. Panels shall be removable by one person without tools. Instruments and control shall be mounted within enclosure.

B. Engine Cooling Airflow through Enclosure: Maintain temperature rise of system components within required limits when unit operates at 110 percent of rated load for 2 hours with ambient temperature at top of range specified in system service conditions.

1. Louvers: Fixed-engine, cooling-air inlet and discharge. Storm-proof and drainable louvers prevent entry of rain and snow.

2. Automatic Dampers: At engine cooling-air inlet and discharge. Dampers shall be closed to reduce enclosure heat loss in cold weather when unit is not operating.

Coordinate two paragraphs and associated subparagraphs below with Drawings for lighting types and location, and supply circuits.

C. Interior Lights with Switch: Factory-wired, vaporproof-type fixtures within housing; arranged to illuminate controls and accessible interior. Arrange for external electrical connection.

1. AC lighting system and connection point for operation when remote source is available.

2. DC lighting system for operation when remote source and generator are both unavailable.

D. Convenience Outlets: Factory wired[, GFCI]. Arrange for external electrical connection.

2.9 VIBRATION ISOLATION DEVICES

Copy "Elastomeric Isolation Pads" Paragraph below and re-edit for each product.

The configuration and materials of elastomeric isolation pads depend on the equipment being supported. It is possible to have more than one type of elastomeric isolation pad on the same Project. Insert drawing designation for each elastomeric isolation pad type required. Use these designations on Drawings to identify each product.

A. Elastomeric Isolation Pads: <Insert drawing designation>.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Ace Mountings Co., Inc.

b. California Dynamics Corporation.

c. Isolation Technology, Inc.

d. Kinetics Noise Control, Inc.

e. Mason Industries, Inc.

f. Vibration Eliminator Co., Inc.

g. Vibration Isolation.

h. Vibration Mountings & Controls, Inc.

i. <Insert manufacturer's name>.

3. Fabrication: Single or multiple layers of sufficient durometer stiffness for uniform loading over pad area.

4. Size: Factory or field cut to match requirements of supported equipment.

Verify availability of various pad materials and their properties with manufacturers.

5. Pad Material: Oil and water resistant with elastomeric properties.

6. Surface Pattern: [Smooth] [Ribbed] [Waffle] pattern.

Retain first subparagraph below if pad is infused with synthetic fibers.

7. Infused nonwoven cotton or synthetic fibers.

Retain first subparagraph below if galvanized-steel baseplates are adhered to the isolation pad to facilitate load distribution.

8. Load-bearing metal plates adhered to pads.

Copy "Restrained Spring Isolators" Paragraph below and re-edit for each product.

The configuration and materials of housed-restrained-spring isolators depend on the equipment being supported. It is possible to have more than one type of housed-restrained-spring isolator on the same Project. Insert drawing designation for each housed-restrained-spring isolator type required. Use these designations on Drawings to identify each product.

B. Restrained Spring Isolators: Freestanding, Steel, Open-Spring Isolators with Vertical-Limit Stop Restraint in Two-Part Telescoping Housing: <Insert drawing designation>.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. Ace Mountings Co., Inc.

b. California Dynamics Corporation.

c. Isolation Technology, Inc.

d. Kinetics Noise Control, Inc.

e. Mason Industries, Inc.

f. Vibration Eliminator Co., Inc.

g. Vibration Isolation.

h. Vibration Mountings & Controls, Inc.

i. <Insert manufacturer's name>.

3. Two-Part Telescoping Housing: A steel top and bottom frame separated by an elastomeric material and enclosing the spring isolators. Housings are equipped with [adjustable] [non-adjustable] snubbers to limit vertical movement.

a. Drilled base housing for bolting to structure with an elastomeric isolator pad attached to the underside. Bases shall limit floor load to 500 psig (3447 kPa).

b. Threaded top housing with adjustment bolt and cap screw to fasten and level equipment.

4. Outside Spring Diameter: Not less than 80 percent of the compressed height of the spring at rated load.

5. Minimum Additional Travel: 50 percent of the required deflection at rated load.

6. Lateral Stiffness: More than 80 percent of rated vertical stiffness.

7. Overload Capacity: Support 200 percent of rated load, fully compressed, without deformation or failure.

2.10 FINISHES

A. Indoor and Outdoor Enclosures and Components: Manufacturer's standard finish over corrosion-resistant pretreatment and compatible primer.

2.11 SOURCE QUALITY CONTROL

A. Prototype Testing: Factory test engine-generator set using same engine model, constructed of identical or equivalent components and equipped with identical or equivalent accessories.

Consider requiring Level 1 compliance in first subparagraph below for other than Level 1 installations to obtain benefits of specific standard requirements.

1. Tests: Comply with NFPA 110, Level 1 Energy Converters and with IEEE 115.

2. Report factory test results within 10 days of completion of test.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Comply with packaged engine-generator manufacturers' written installation and alignment instructions and with NFPA 110.

B. Install packaged engine generator to provide access, without removing connections or accessories, for periodic maintenance.

C. Install packaged engine generator on cast-in-place concrete equipment bases. Comply with requirements for equipment bases and foundations specified in [Section 033000 "Cast-in-Place Concrete."] [Section 033053 "Miscellaneous Cast-in-Place Concrete."]

Retain first subparagraph below for projects in seismic areas. Indicate seismic-control device type and minimum deflection in supported equipment schedule on Drawings.

1. Comply with requirements for seismic control devices specified in Section 260548.16 "Seismic Controls for Electrical Systems."

2. Comply with requirements for vibration isolation devices specified in this section.

D. Install Schedule 40, black steel piping with welded joints and connect to engine muffler. Install thimble at wall. Piping shall be same diameter as muffler outlet. Flexible connectors and steel piping materials and installation requirements are specified in Section 232116 "Hydronic Piping Specialties."Section 15179 "Hydronic Piping Specialties."

Coordinate subparagraph below with Drawings.

1. Install condensate drain piping to muffler drain outlet full size of drain connection with a shutoff valve, stainless-steel flexible connector, and Schedule 40, black steel pipe with welded joints. Flexible connectors and piping materials and installation requirements are specified in Section 232116 "Hydronic Piping Specialties."Section 15179 "Hydronic Piping Specialties."

E. Electrical Wiring: Install electrical devices furnished by equipment manufacturers but not specified to be factory mounted.

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems. If Drawings are explicit enough, these requirements may be reduced or omitted.

F. Piping installation requirements are specified in other Sections. Drawings indicate general arrangement of piping and specialties.

G. Connect fuel, cooling-system, and exhaust-system piping adjacent to packaged engine generator to allow service and maintenance.

H. Connect engine exhaust pipe to engine with flexible connector.

I. Connect fuel piping to engines with a gate valve and union and flexible connector.

1. Natural-gas piping, valves, and specialties for gas distribution are specified in Section 231123 "Facility Natural-Gas Piping."

2. LP-gas piping, valves, and specialties for gas piping are specified in Section 231126 "Facility Liquefied-Petroleum Gas Piping."

J. Ground equipment according to Section 260526 "Grounding and Bonding for Electrical Systems."

K. Connect wiring according to Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

L. Identify system components according to Section 230553 "Identification for HVAC Piping and Equipment" and Section 260553 "Identification for Electrical Systems."

3.2 FIELD QUALITY CONTROL

A. Perform tests and inspections and prepare test reports.

Retain subparagraph below to require a factory-authorized service representative to assist Contractor with inspections, tests, and adjustments.

1. Manufacturer's Field Service: Engage a factory-authorized service representative to inspect components, assemblies, and equipment installations, including connections, and to assist in testing.

B. Tests and Inspections:

NETA and other testing requirements indicated in subparagraphs below may be in excess of those required for Project. Review NETA and other tests listed and revise subparagraphs below to retain only those tests deemed necessary.

1. Perform tests recommended by manufacturer and each electrical test and visual and mechanical inspection[ (except those indicated to be optional)] for "AC Generators and for Emergency Systems" specified in NETA Acceptance Testing Specification. Certify compliance with test parameters.

2. NFPA 110 Acceptance Tests: Perform tests required by NFPA 110 that are additional to those specified here including, but not limited to, single-step full-load pickup test.

3. Battery Tests: Equalize charging of battery cells according to manufacturer's written instructions. Record individual cell voltages.

a. Measure charging voltage and voltages between available battery terminals for full-charging and float-charging conditions. Check electrolyte level and specific gravity under both conditions.

b. Test for contact integrity of all connectors. Perform an integrity load test and a capacity load test for the battery.

c. Verify acceptance of charge for each element of the battery after discharge.

d. Verify that measurements are within manufacturer's specifications.

4. Battery-Charger Tests: Verify specified rates of charge for both equalizing and float-charging conditions.

5. System Integrity Tests: Methodically verify proper installation, connection, and integrity of each element of engine-generator system before and during system operation. Check for air, exhaust, and fluid leaks.

Retain subparagraph below for long, restricted exhaust systems.

6. Exhaust-System Back-Pressure Test: Use a manometer with a scale exceeding 40-inch wg (120 kPa). Connect to exhaust line close to engine exhaust manifold. Verify that back pressure at full-rated load is within manufacturer's written allowable limits for the engine.

Verify local requirements and delete first subparagraph below for most projects. Few jurisdictions require this test for emergency or standby generator sets.

7. Exhaust Emissions Test: Comply with applicable government test criteria.

8. Voltage and Frequency Transient Stability Tests: Use recording oscilloscope to measure voltage and frequency transients for 50 and 100 percent step-load increases and decreases, and verify that performance is as specified.

9. Harmonic-Content Tests: Measure harmonic content of output voltage under 25 percent and at 100 percent of rated linear load. Verify that harmonic content is within specified limits.

Retain subparagraph below for projects subject to unwanted or illegal generator-set noise intrusion into adjacent properties or activities. Coordinate with Drawings and with requirements in Part 1 "Action Submittals" and "Quality Assurance" articles and in Part 2 "Engine" Article.

10. Noise Level Tests: Measure A-weighted level of noise emanating from generator-set installation, including engine exhaust and cooling-air intake and discharge, at [four] <Insert number> locations [on the property line] <Insert location for measurement>, and compare measured levels with required values.

C. Coordinate tests with tests for transfer switches and run them concurrently.

D. Leak Test: After installation, charge system and test for leaks. Repair leaks and retest until no leaks exist.

E. Operational Test: After electrical circuitry has been energized, start units to confirm proper motor rotation and unit operation.

F. Test and adjust controls and safeties. Replace damaged and malfunctioning controls and equipment.

G. Remove and replace malfunctioning units and [retest] [reinspect] as specified above.

H. Retest: Correct deficiencies identified by tests and observations and retest until specified requirements are met.

I. Report results of tests and inspections in writing. Record adjustable relay settings and measured insulation resistances, time delays, and other values and observations. Attach a label or tag to each tested component indicating satisfactory completion of tests.

3.3 DEMONSTRATION

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain packaged engine generators. Refer to Section 017900 "Demonstration and Training."

END OF SECTION 263213

	ENGINE GENERATORS
	263213 - 1



