Copyright 2012 AIA
MasterSpec Professional
03/12

Copyright 2012 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 263600 - TRANSFER SWITCHES
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section includes automatic transfer switches rated 600 V and less.

B. See Section 213113 "Electric-Drive, Centrifugal Fire Pumps" for automatic transfer switches for fire pumps.

C. See Section 213213 "Electric-Drive, Vertical-Turbine Fire Pumps" for automatic transfer switches for fire pumps.

1.2 ACTION SUBMITTALS

A. Product Data: Include rated capacities, weights, operating characteristics, furnished specialties, and accessories.

B. Shop Drawings: Dimensioned plans, elevations, sections, and details showing minimum clearances, conductor entry provisions, gutter space, installed features and devices, and material lists for each switch specified.

1.3 INFORMATIONAL SUBMITTALS

Retain paragraph and subparagraphs below if required by seismic criteria applicable to Project. Coordinate with Section 260548.16 "Seismic Controls for Electrical Systems."

A. Manufacturer Seismic Qualification Certification: Submit certification that transfer switches accessories, and components will withstand seismic forces defined in Section 260548.16 "Seismic Controls for Electrical Systems." Include the following:

1. Basis for Certification: Indicate whether withstand certification is based on actual test of assembled components or on calculation.

Definition in first subparagraph below varies with type of building and occupancy and is critical to valid certification. Retain optional text for essential facilities where equipment must operate immediately after an earthquake.

a. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified[ and the unit will be fully operational after the seismic event]."

2. Dimensioned Drawings of Equipment Unit: Identify center of gravity and locate and describe mounting and anchorage provisions.

3. Detailed description of equipment anchorage devices on which the certification is based.

Retain "Field quality-control reports" Paragraph below if Contractor is responsible for field quality-control testing and inspecting.

B. Field quality-control reports.

1.4 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

1.5 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

Retain applicable standards in five paragraphs below.

B. Comply with NEMA ICS 1.

C. Comply with NFPA 70.

D. Comply with NFPA 99.

E. Comply with NFPA 110.

F. Comply with UL 1008 unless requirements of these Specifications are stricter.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

2.1 MANUFACTURED UNITS

A. Contactor Transfer Switches:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. AC Data Systems, Inc.

b. Caterpillar; Engine Div.

c. Emerson; ASCO Power Technologies, LP.

d. Generac Power Systems, Inc.

e. GE Zenith Controls.

f. Kohler Power Systems; Generator Division.

g. Onan/Cummins Power Generation; Industrial Business Group.

h. Russelectric, Inc.

i. Spectrum Detroit Diesel.

j. <Insert manufacturer's name>.

B. Transfer Switches Using Molded-Case Switches or Circuit Breakers:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

1. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. AC Data Systems, Inc.

b. Eaton Electrical Inc.; Cutler-Hammer.

c. GE Zenith Controls.

d. Hubbell Industrial Controls, Inc.

e. Lake Shore Electric Corporation.

f. <Insert manufacturer's name>.

2.2 GENERAL TRANSFER-SWITCH PRODUCT REQUIREMENTS

Coordinate paragraph below with Drawings and indicate percentage of tungsten filament lamp load for switches where it exceeds 30 percent. This percentage may affect switch selection. Some manufacturers' ratings for some switch lines apply to all classes of load, including tungsten lamps.

A. Indicated Current Ratings: Apply as defined in UL 1008 for continuous loading and total system transfer, including tungsten filament lamp loads not exceeding 30 percent of switch ampere rating, unless otherwise indicated.

Indicate required ratings on Drawings. See Editing Instruction No. 3 in the Evaluations.

B. Tested Fault-Current Closing and Withstand Ratings: Adequate for duty imposed by protective devices at installation locations in Project under the fault conditions indicated, based on testing according to UL 1008.

Retain subparagraph below if this Section includes automatic transfer switches based on molded-case-switch or circuit-breaker products or if design includes fault-current protection internal to transfer switch.

1. Where transfer switch includes internal fault-current protection, rating of switch and trip unit combination shall exceed indicated fault-current value at installation location.

C. Solid-State Controls: Repetitive accuracy of all settings shall be plus or minus 2 percent or better over an operating temperature range of minus 20 to plus 70 deg C.

D. Resistance to Damage by Voltage Transients: Components shall meet or exceed voltage-surge withstand capability requirements when tested according to IEEE C62.41. Components shall meet or exceed voltage-impulse withstand test of NEMA ICS 1.

E. Electrical Operation: Accomplish by a nonfused, momentarily energized solenoid or electric-motor-operated mechanism, mechanically and electrically interlocked in both directions.

F. Switch Characteristics: Designed for continuous-duty repetitive transfer of full-rated current between active power sources.

Delete first subparagraph below if units using switching components designed for molded-case switches or insulated-case circuit breakers are permissible.

1. Limitation: Switches using molded-case switches or circuit breakers or insulated-case circuit-breaker components are not acceptable.

2. Switch Action: Double throw; mechanically held in both directions.

3. Contacts: Silver composition or silver alloy for load-current switching. Conventional automatic transfer-switch units, rated 225 A and higher, shall have separate arcing contacts.

Retain paragraph below and select appropriate option if four-pole transfer switches are required. See Editing Instruction No. 4 in the Evaluations. Coordinate with Drawings.

G. Neutral Switching. Where four-pole switches are indicated, provide [neutral pole switched simultaneously with phase poles] [overlapping neutral contacts].

Retain paragraph below for single-phase, three-wire systems or three-phase, four-wire systems without neutral switching. Coordinate with Drawings.

H. Neutral Terminal: Solid and fully rated, unless otherwise indicated.

Retain paragraph below if required for heavy nonlinear loads. This requirement may result in some suppliers' oversizing certain switches to provide an oversize neutral. Coordinate with Drawings.

I. Oversize Neutral: Ampacity and switch rating of neutral path through units indicated for oversize neutral shall be double the nominal rating of circuit in which switch is installed.

Retain paragraph and subparagraphs below if charger for generator starting batteries is to be located in transfer switch. Select first option in first subparagraph for same generator units; consider second option for units 250 kW and larger.

J. Battery Charger: For generator starting batteries.

1. Float type rated [2] [10] A.

2. Ammeter to display charging current.

3. Fused ac inputs and dc outputs.

Use NEMA 250, Type 12 enclosure if environment is generally dusty.

K. Enclosures: General-purpose NEMA 250, Type [1] [3R] [12], complying with NEMA ICS 6 and UL 508, unless otherwise indicated.

2.3 AUTOMATIC TRANSFER SWITCHES

A. Comply with Level 1 equipment according to NFPA 110.

B. Switching Arrangement: Double-throw type, incapable of pauses or intermediate position stops during normal functioning, unless otherwise indicated.

Retain paragraph below if required for control to minimize elevator disruption or for other purposes.

C. Signal-Before-Transfer Contacts: A set of normally open/normally closed dry contacts operates in advance of retransfer to normal source. Interval is adjustable from 1 to 30 seconds.

Retain paragraph below if transfer switches based on molded-case-switch or circuit-breaker components are acceptable for Project.

D. Transfer Switches Based on Molded-Case-Switch Components: Comply with NEMA AB 1, UL 489, and UL 869A.

Retain one of three paragraphs below to specify alternatives for switching large-motor loads. Indicate on Drawings which switches require these features. See Editing Instruction No. 5 in the Evaluations.

E. In-Phase Monitor: Factory-wired, internal relay controls transfer so it occurs only when the two sources are synchronized in phase.

F. Motor Disconnect and Timing Relay: Controls designate starters so they disconnect motors before transfer and reconnect them selectively at an adjustable time interval after transfer. Time delay for reconnecting individual motor loads is adjustable between 1 and 60 seconds, and settings are as indicated.

G. Programmed Neutral Switch Position: Switch operator has a programmed neutral position arranged to provide a midpoint between the two working switch positions, with an intentional, time-controlled pause at midpoint during transfer.

Edit paragraph and subparagraphs below to coordinate terminology for sources, such as "normal," "preferred," "emergency," and "alternate," if such terms are used elsewhere in the Construction Documents.

H. Automatic Transfer-Switch Features:

Revise pickup, dropout, and time-delay settings in first four subparagraphs below to suit application, and retain required features.

First subparagraph specifies three-phase undervoltage monitor. Retain if loss of one phase of normal source would be a problem for loads downstream from transfer switch. Similar option is available for emergency source.

1. Undervoltage Sensing for Each Phase of Normal Source: Sense low phase-to-ground voltage on each phase. Pickup voltage shall be adjustable from 85 to 100 percent of nominal, and dropout voltage is adjustable from 75 to 98 percent of pickup value. Factory set for pickup at 90 percent and dropout at 85 percent.

2. Adjustable Time Delay: For override of normal-source voltage sensing to delay transfer and engine start signals. Adjustable from zero to six seconds, and factory set for one second.

3. Voltage/Frequency Lockout Relay: Prevent premature transfer to generator. Pickup voltage shall be adjustable from 85 to 100 percent of nominal. Factory set for pickup at 90 percent. Pickup frequency shall be adjustable from 90 to 100 percent of nominal. Factory set for pickup at 95 percent.

4. Time Delay for Retransfer to Normal Source: Adjustable from 0 to 30 minutes, and factory set for 10 minutes to automatically defeat delay on loss of voltage or sustained undervoltage of emergency source, provided normal supply has been restored.

5. Test Switch: Simulate normal-source failure.

6. Switch-Position Pilot Lights: Indicate source to which load is connected.

7. Source-Available Indicating Lights: Supervise sources via transfer-switch normal- and emergency-source sensing circuits.

a. Normal Power Supervision: Green light with nameplate engraved "Normal Source Available."

b. Emergency Power Supervision: Red light with nameplate engraved "Emergency Source Available."

8. Unassigned Auxiliary Contacts: Two normally open, single-pole, double-throw contacts for each switch position, rated 10 A at 240-V ac.

9. Transfer Override Switch: Overrides automatic retransfer control so automatic transfer switch will remain connected to emergency power source regardless of condition of normal source. Pilot light indicates override status.

Retain subparagraph below if needed to coordinate with engine generator. Do not duplicate control features furnished with generator. See Editing Instruction No. 6 in the Evaluations.

10. Engine Starting Contacts: One isolated and normally closed, and one isolated and normally open; rated 10 A at 32-V dc minimum.

Retain one of first two subparagraphs below.

11. Engine Shutdown Contacts: Instantaneous; shall initiate shutdown sequence at remote engine-generator controls after retransfer of load to normal source.

12. Engine Shutdown Contacts: Time delay adjustable from zero to five minutes, and factory set for five minutes. Contacts shall initiate shutdown at remote engine-generator controls after retransfer of load to normal source.

13. Engine-Generator Exerciser: Solid-state, programmable-time switch starts engine generator and transfers load to it from normal source for a preset time, then retransfers and shuts down engine after a preset cool-down period. Initiates exercise cycle at preset intervals adjustable from 7 to 30 days. Running periods are adjustable from 10 to 30 minutes. Factory settings are for 7-day exercise cycle, 20-minute running period, and 5-minute cool-down period. Exerciser features include the following:

a. Exerciser Transfer Selector Switch: Permits selection of exercise with and without load transfer.

b. Push-button programming control with digital display of settings.

c. Integral battery operation of time switch when normal control power is not available.

2.4 SOURCE QUALITY CONTROL

A. Factory test and inspect components, assembled switches, and associated equipment. Ensure proper operation. Check transfer time and voltage, frequency, and time-delay settings for compliance with specified requirements. Perform dielectric strength test complying with NEMA ICS 1.

PART 3 -  EXECUTION

3.1 INSTALLATION

Retain applicable mounting paragraphs in this article. Coordinate with Drawings.

Retain paragraph below if seismic controls are a project requirement. Coordinate with Drawings.

A. Design each fastener and support to carry load indicated by seismic requirements and according to seismic-restraint details. See Section 260548.16 "Seismic Controls for Electrical Systems."

Retain paragraph below for floor-mounting switches and coordinate with Drawings.

B. Floor-Mounting Switch: Anchor to floor by bolting.

Retain subparagraph below to require floor-mounting switches to be installed on concrete bases. Coordinate with Drawings.

1. Concrete Bases: 4 inches (100 mm) high, reinforced, with chamfered edges. Extend base no more than 4 inches (100 mm) in all directions beyond the maximum dimensions of switch, unless otherwise indicated or unless required for seismic support. Construct concrete bases according to Section 260529 "Hangers and Supports for Electrical Systems."

C. Identify components according to Section 260553 "Identification for Electrical Systems."

D. Set field-adjustable intervals and delays, relays, and engine exerciser clock.

3.2 CONNECTIONS

A. Ground equipment according to Section 260526 "Grounding and Bonding for Electrical Systems."

B. Connect wiring according to Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

3.3 FIELD QUALITY CONTROL

Retain "Manufacturer's Field Service" Paragraph below to require a factory-authorized service representative to perform tests and inspections.

A. Manufacturer's Field Service: Engage a factory-authorized service representative to test and inspect components, assemblies, and equipment installations, including connections.

Retain "Perform the following tests and inspections" Paragraph below to require Contractor to perform tests and inspections.

B. Perform the following tests and inspections[ with the assistance of a factory-authorized service representative]:

1. After installing equipment and after electrical circuitry has been energized, test for compliance with requirements.

2. Perform each visual and mechanical inspection and electrical test stated in NETA Acceptance Testing Specification. Certify compliance with test parameters.

3. Measure insulation resistance phase-to-phase and phase-to-ground with insulation-resistance tester. Use test voltages and procedure recommended by manufacturer. Comply with manufacturer's specified minimum resistance.

a. Check for electrical continuity of circuits and for short circuits.

b. Inspect for physical damage, proper installation and connection, and integrity of barriers, covers, and safety features.

c. Verify that manual transfer warnings are properly placed.

d. Perform manual transfer operation.

4. After energizing circuits, demonstrate interlocking sequence and operational function for each switch at least three times.

a. Simulate power failures of normal source to automatic transfer switches and of emergency source with normal source available.

Retain test in first subparagraph below if three-phase undervoltage sensing is specified in Part 2. Test requires advance preparation by testing agency.

b. Simulate loss of phase-to-ground voltage for each phase of normal source.

c. Verify time-delay settings.

d. Verify pickup and dropout voltages by data readout or inspection of control settings.

Usually require test in first subparagraph below only for critical and extensive installations and for switches rated 1600 A and more in other installations.

e. Perform contact-resistance test across main contacts and correct values exceeding 500 microhms and values for 1 pole deviating by more than 50 percent from other poles.

f. Verify proper sequence and correct timing of automatic engine starting, transfer time delay, retransfer time delay on restoration of normal power, and engine cool-down and shutdown.

Retain subparagraph and associated subparagraph below if protective devices for circuits connected to transfer switches include ground-fault protection.

5. Ground-Fault Tests: Coordinate with testing of ground-fault protective devices for power delivery from both sources.

a. Verify grounding connections and locations and ratings of sensors.

Observe reaction of circuit-interrupting devices when simulated fault current is applied at sensors. Retain first paragraph below if automatic transfer switch is associated with generator.

C. Coordinate tests with tests of generator and run them concurrently.

D. Report results of tests and inspections in writing. Record adjustable relay settings and measured insulation and contact resistances and time delays. Attach a label or tag to each tested component indicating satisfactory completion of tests.

E. Remove and replace malfunctioning units and retest as specified above.

F. Prepare test and inspection reports.

Edit paragraph and subparagraphs below to suit types of switches specified.

G. Infrared Scanning: After Substantial Completion, but not more than 60 days after Final Acceptance, perform an infrared scan of each switch. Remove all access panels so joints and connections are accessible to portable scanner.

1. Follow-up Infrared Scanning: Perform an additional follow-up infrared scan of each switch 11 months after date of Substantial Completion.

2. Instrument: Use an infrared scanning device designed to measure temperature or to detect significant deviations from normal values. Provide calibration record for device.

3. Record of Infrared Scanning: Prepare a certified report that identifies switches checked and that describes scanning results. Include notation of deficiencies detected, remedial action taken, and observations after remedial action.

3.4 DEMONSTRATION

A. [Engage a factory-authorized service representative to train] [Train] Owner's maintenance personnel to adjust, operate, and maintain transfer switches and related equipment as specified below. Refer to Section 017900 "Demonstration and Training."

Retain paragraph below if generators are in Project.

B. Coordinate this training with that for generator equipment.

END OF SECTION 263600

	TRANSFER SWITCHES
	263600 - 1



