Copyright 2012 AIA
MasterSpec Professional
03/12

Copyright 2012 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 264113 - LIGHTNING PROTECTION FOR STRUCTURES
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section includes lightning protection for [structures] [structure elements] [building site components].

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product indicated.

B. Shop Drawings: For air terminals and mounting accessories.

1. Layout of the lightning protection system, along with details of the components to be used in the installation.

2. Include indications for use of raceway, data on how concealment requirements will be met, and calculations required by NFPA 780 for bonding of grounded and isolated metal bodies.

1.3 INFORMATIONAL SUBMITTALS

A. Field quality-control reports.

1.4 QUALITY ASSURANCE

A. Installer Qualifications: Certified by [UL] [or] [LPI as a Master Installer/Designer], trained and approved for installation of units required for this Project.

B. System Certificate:

Retain one of three subparagraphs below. See "Lightning Protection Standards and System Certifications" Article in the Evaluations.

1. UL Master Label.

2. LPI System Certificate.

Retain subparagraph below if Project includes addition to existing UL Master Label building.

3. UL Master Label Recertification.

C. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 780, "Definitions" Article.

PART 2 -  PRODUCTS

2.1 LIGHTNING PROTECTION SYSTEM COMPONENTS

See Editing Instruction No. 2 in the Evaluations for discussion of whether the requirement of complying with NFPA 780 should be retained. Specified standards stipulate minimum size requirements for components, depending on selected metal and class of building. To require components larger than minimum size, add requirements here.

A. Comply with UL 96[ and NFPA 780].

Retain material classification in NFPA 780; see Table 2 in the Evaluations.

B. Roof-Mounted Air Terminals: NFPA 780, [Class I] [Class II], [aluminum] [copper] unless otherwise indicated.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of first two subparagraphs and list of manufacturers below. See Section 016000 "Product Requirements."

1. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain option in first subparagraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

2. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

a. East Coast Lightning Equipment Inc.

b. ERICO International Corporation.

c. Harger.

d. Heary Bros. Lightning Protection Co. Inc.

e. Independent Protection Co.

f. Preferred Lightning Protection.

g. Robbins Lightning, Inc.

h. Thompson Lightning Protection, Inc.

i. <Insert manufacturer's name>.

3. Air Terminals More than 24 Inches (600 mm) Long: With brace attached to the terminal at not less than half the height of the terminal.

Retain subparagraph below for single-membrane roof system.

4. Single-Membrane, Roof-Mounted Air Terminals: Designed specifically for single-membrane roof system materials. Comply with requirements in roofing Sections.

C. Main and Bonding Conductors: [Copper] [Aluminum].

Retain first paragraph below for structures exceeding 60 feet (18 m) in height. Revise if Project conditions require use of an above-ground, ground-level, potential equalization conductor.

D. Ground Loop Conductor: The same size and type as the main conductor except tinned.

Copper-clad, steel ground rods are the most common grounding electrodes. See Editing Instruction No. 4 in the Evaluations for assistance in selecting ground rod material. UL 94 and NFPA 780 allow the use of ground rods 1/2 inch (12.7 mm) in diameter and 96 inches (2400 mm) long. Sectional rods are used when electrodes longer than 10 feet (3 m) are required.

E. Ground Rods: [Copper-clad] [Zinc-coated] [Stainless] steel[, sectional type]; [3/4 inch (19 mm) in diameter by 10 feet (3 m)] [5/8 inch (16 mm) in diameter by 96 inches (2400 mm)] long.

PART 3 -  EXECUTION

3.1 INSTALLATION

See Editing Instruction No. 2 in the Evaluations for discussion of whether the requirement of complying with NFPA 780 should be retained. Specified standards stipulate minimum size requirements for components, depending on selected metal and class of building. To require components larger than minimum size, add requirements here.

A. Install lightning protection components and systems according to [UL 96A] [and] [NFPA 780].

B. Conceal the following conductors:

Retain one or more of four subparagraphs below depending on degree of concealment needed for lightning protection components. If deleting all four subparagraphs, there will be no restrictions on exposed conductors.

1. System conductors.

2. Down conductors.

3. Interior conductors.

4. Conductors within normal view of exterior locations at grade within 200 feet (60 m) of building.

Retain one of first two paragraphs below. Exothermic-welded connections are considered more permanent than crimped or bolted connections.

C. Cable Connections: Use crimped or bolted connections for all conductor splices and connections between conductors and other components. Use exothermic-welded connections in underground portions of the system.

D. Cable Connections: Use exothermic-welded connections for all conductor splices and connections between conductors and other components.

1. Exception: In single-ply membrane roofing, exothermic-welded connections may be used only below the roof level.

Retain first paragraph below for single-ply membrane roofing.

E. Air Terminals on Single-Ply Membrane Roofing: Comply with roofing membrane and adhesive manufacturer's written instructions.

Delete first two paragraphs below if NFPA 780 compliance is specified; retain if specifying bonding requirements that exceed minimum UL 96A requirements. See Editing Instruction No. 3 in the Evaluations. Coordinate with Drawings for counterpoise requirements if any.

F. Bond extremities of vertical metal bodies exceeding 60 feet (18 m) in length to lightning protection components.

G. Ground Loop: Install ground-level, potential equalization conductor and extend around the perimeter of [structure] [area or item indicated].

1. Bury ground ring not less than [24 inches (600 mm)] <Insert dimension> from building foundation.

2. Bond ground terminals to the ground loop.

3. Bond grounded building systems to the ground loop conductor within 12 feet (3.6 m) of grade level.

Retain paragraph below for structures exceeding 60 feet (18 m) in height unless the structure is an electrically continuous steel frame. NFPA 70 lists other instances where paragraph below is not required.

H. Bond lightning protection components with intermediate-level interconnection loop conductors to grounded metal bodies of building at 60-foot (18-m) intervals.

3.2 SLEEVE AND SLEEVE-SEAL INSTALLATION FOR ELECTRICAL PENETRATIONS

A. Install sleeves and sleeve seals at penetrations of exterior floor and wall assemblies. Comply with requirements in Section 260544 "Sleeves and Sleeve Seals for Electrical Raceways and Cabling."

3.3 CORROSION PROTECTION

See Evaluations for discussion of corrosion protection issues.

A. Do not combine materials that can form an electrolytic couple that will accelerate corrosion in the presence of moisture unless moisture is permanently excluded from junction of such materials.

B. Use conductors with protective coatings where conditions cause deterioration or corrosion of conductors.

3.4 FIELD QUALITY CONTROL

A. Notify Architect at least 48 hours in advance of inspection before concealing lightning protection components.

Revise this article to specify inspections for UL Master Label or LPI System Certificate. See Evaluations.

Retain one of two paragraphs below.

B. UL Inspection: Meet requirements to obtain a UL Master Label for system.

C. LPI System Inspection: Meet requirements to obtain an LPI System Certificate.

END OF SECTION 264113

	LIGHTNING PROTECTION FOR STRUCTURES
	264113 - 1



