Copyright 2012 AIA
MasterSpec Professional
03/12

Copyright 2012 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 275116 - PUBLIC ADDRESS AND MASS NOTIFICATION SYSTEMS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Preamplifiers.

2. Power amplifiers.

3. Microphones.

4. Control console.

5. Loudspeakers.

6. Microphone outlets.

7. Conductors and cables.

8. Raceways.

1.2 PERFORMANCE REQUIREMENTS

Retain first paragraph below if Contractor is required to assume responsibility for design.

A. Delegated Design: Design supports and seismic restraints for control consoles and components, including comprehensive engineering analysis by a qualified professional engineer, using performance requirements and design criteria indicated.

Retain paragraph below with "Seismic Qualification Certificates" Paragraph in "Informational Submittals" Article for projects requiring seismic design. Model building codes and SEI/ASCE 7 establish criteria for buildings subject to earthquake motions. Verify requirements of authorities having jurisdiction.

B. Seismic Performance: Supports and seismic restraints for control consoles and components shall withstand the effects of earthquake motions determined according to [SEI/ASCE 7] <Insert requirement>.

Retain subparagraph below to define the term "withstand" as it applies to this Project. Definition varies with type of building and occupancy and is critical to valid certification. Option is used for essential facilities where equipment must operate immediately after an earthquake.

1. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified[ and the unit will be fully operational after the seismic event]."

1.3 ACTION SUBMITTALS

A. Product Data: For each type of product indicated.

Paragraph below is defined in Section 013300 "Submittal Procedures" as a "Delegated-Design Submittal." Retain if Work of this Section is required to withstand specific design loads and design responsibilities have been delegated to Contractor or if structural data are required as another way to verify compliance with performance requirements. Professional engineer qualifications are specified in Section 014000 "Quality Requirements."

B. Delegated-Design Submittal: For supports and seismic restraints for control consoles and components indicated to comply with performance requirements and design criteria, including analysis data signed and sealed by the qualified professional engineer responsible for their preparation.

1. Detail fabrication and assembly of supports and seismic restraints for control consoles and components.

1.4 INFORMATIONAL SUBMITTALS

Retain first paragraph below if required by seismic criteria applicable to Project. Coordinate with Sections specifying supports and seismic controls. See SEI/ASCE 7 for certification requirements for equipment and components.

A. Seismic Qualification Certificates: For control consoles, accessories, and components, from manufacturer.

1. Basis for Certification: Indicate whether withstand certification is based on actual test of assembled components or on calculation.

2. Dimensioned Outline Drawings of Equipment Unit: Identify center of gravity and locate and describe mounting and anchorage provisions.

3. Detailed description of equipment anchorage devices on which the certification is based and their installation requirements.

B. Field quality-control reports.

1.5 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

1.6 QUALITY ASSURANCE

A. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

B. Comply with NFPA 70.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain paragraph and list of manufacturers below. See Section 016000 "Product Requirements."

A. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

1. Alpha Communications.

2. Altec Lansing Technologies, Inc.

3. Atlas Sound LP.

4. Bogen Communications, Inc.

5. Dukane Communication Systems; part of GE Infrastructure, Security.

6. Edwards Signaling & Security Systems; part of GE Infrastructure, Security.

7. Electro-Voice; Telex Communications, Inc.

8. Federal Signal Corporation; Electrical Products Division.

9. Peavey Electronics.

10. Rauland-Borg Corporation.

11. Whelen Engineering Company, Inc.

12. <Insert manufacturer's name>.

2.2 FUNCTIONAL DESCRIPTION OF SYSTEM

Descriptions in this article are examples only; revise to indicate actual design intent.

A. System Functions:

1. Selectively connect any zone to any available signal channel.

2. Selectively control sound from microphone outlets and other inputs.

3. "All-call" feature shall connect the all-call sound signal simultaneously to all zones regardless of zone or channel switch settings.

4. Reproduce high-quality sound that is free of noise and distortion at all loudspeakers at all times during equipment operation including standby mode with inputs off; output free of nonuniform coverage of amplified sound.

2.3 GENERAL EQUIPMENT AND MATERIAL REQUIREMENTS

A. Compatibility of Components: Coordinate component features to form an integrated system. Match components and interconnections for optimum performance of specified functions.

B. Equipment: Comply with UL 813. Equipment shall be modular, using solid-state components, and fully rated for continuous duty unless otherwise indicated. Select equipment for normal operation on input power usually supplied at 110 to 130 V, 60 Hz.

C. Weather-Resistant Equipment: Listed and labeled by a qualified testing agency for duty outdoors or in damp locations.

2.4 PREAMPLIFIERS

Retain one of first two paragraphs below.

A. Preamplifier: Separately mounted.

B. Preamplifier: Integral to power amplifier.

C. Output Power: Plus 4 dB above 1 mW at matched power-amplifier load.

D. Total Harmonic Distortion: Less than 1 percent.

E. Frequency Response: Within plus or minus 2 dB from 20 to 20,000 Hz.

F. Input Jacks: Minimum of two. One matched for low-impedance microphone; the other matchable to cassette deck, CD player, or radio tuner signals without external adapters.

G. Minimum Noise Level: Minus 55 dB below rated output.

H. Controls: On-off, input levels, and master gain.

2.5 POWER AMPLIFIERS

A. Mounting: Console.

B. Output Power: 70-V balanced line. [80 percent of the sum of wattage settings of connected] <Insert wattage> for each station and speaker connected in all-call mode of operation, plus an allowance for future stations.

C. Total Harmonic Distortion: Less than 3 percent at rated power output from 50 to 12,000 Hz.

D. Minimum Signal-to-Noise Ratio: 60 dB, at rated output.

E. Frequency Response: Within plus or minus 2 dB from 50 to 12,000 Hz.

F. Output Regulation: Less than 2 dB from full to no load.

G. Controls: On-off, input levels, and low-cut filter.

H. Input Sensitivity: Matched to preamplifier and to provide full-rated output with sound-pressure level of less than 10 dynes/sq. cm impinging on speaker microphone or handset transmitter.

2.6 MICROPHONES

A. Paging Microphone:

1. Type: Dynamic, with [cardioid] [omni] polar characteristic.

2. Impedance: 150 ohms.

3. Frequency Response: Uniform, 50 to 14,000 Hz.

4. Output Level: Minus 58 dB, minimum.

5. Finish: Satin chrome.

6. Cable: C25J.

7. Mounting: Desk stand with integral-locking, press-to-talk switch.

B. <Insert microphone type>.

2.7 CONTROL CONSOLE

A. Cabinet: Modular, [desktop] [desk style]; complying with TIA/EIA-310-D.

B. Housing: Steel, 0.0478 inch (1.2 mm) minimum, with removable front and rear panels. Side panels are removable for interconnecting side-by-side mounting.

C. Controls:

1. Switching devices to select signal sources for distribution channels.

2. Program selector switch to select source for each program channel.

3. Switching devices to select zones for paging.

4. All-call selector switch.

D. Indicators: A visual annunciation for each distribution channel to indicate source being used.

Retain first paragraph below for consoles using self-contained power and control units with integral power amplifiers. Amplifiers are available with up to 40-W rating.

E. Self-Contained Power and Control Unit: A single assembly of basic control, electronics, and power supply necessary to accomplish specified functions.

F. Spare Positions: 20 percent spare zone control and annunciation positions on console.

G. Microphone jack.

2.8 LOUDSPEAKERS

A. Cone-Type Loudspeakers:

1. Minimum Axial Sensitivity: 91 dB at one meter, with 1-W input.

2. Frequency Response: Within plus or minus 3 dB from 50 to 15,000 Hz.

3. Size: 8 inches (200 mm) with 1-inch (25-mm) voice coil and minimum 5-oz. (140-g) ceramic magnet.

4. Minimum Dispersion Angle: 100 degrees.

5. Rated Output Level: 10 W.

6. Matching Transformer: Full-power rated with four taps. Maximum insertion loss of 0.5 dB.

7. Surface-Mounting Units: Ceiling, wall, or pendant mounting, as indicated, in steel back boxes, acoustically dampened. Front face of at least 0.0478-inch (1.2-mm) steel and whole assembly rust proofed and shop primed for field painting.

8. Flush-Ceiling-Mounting Units: In steel back boxes, acoustically dampened. Metal ceiling grille with [white] <Insert color> baked enamel.

Device in paragraph below is an example only; revise to suit Project requirements. Coordinate with Drawings.

B. Horn-Type Loudspeakers:

1. Type: Single-horn units, double-reentrant design, with minimum full-range power rating of 15 W.

2. Matching Transformer: Full-power rated with four standard taps. Maximum insertion loss of 0.5 dB.

3. Frequency Response: Within plus or minus 3 dB from 250 to 12,000 Hz.

4. Dispersion Angle: 130 by 110 degrees.

5. Mounting: Integral bracket.

6. Units in Hazardous (Classified) Locations: Listed and labeled for environment in which they are located.

2.9 OUTLETS

A. Microphone Outlet: Three-pole, polarized, locking-type, microphone receptacles in single-gang boxes. Equip wall outlets with brushed stainless-steel device plates. Equip floor outlets with gray tapered rubber or plastic cable nozzles and fixed outlet covers.

2.10 CONDUCTORS AND CABLES

Retain this article unless cabling is specified in Section 271500 "Communications Horizontal Cabling."

A. Jacketed, twisted pair and twisted multipair, untinned solid copper.

1. Insulation for Wire in Conduit: Thermoplastic, not less than 1/32 inch (0.8 mm) thick.

2. Microphone Cables: Neoprene jacketed, not less than 2/64 inch (0.8 mm) thick, over shield with filled interstices. Shield No. 34 AWG, tinned, soft-copper strands formed into a braid or approved equivalent foil. Shielding coverage on conductors is not less than 60 percent.

3. Plenum Cable: Listed and labeled for plenum installation.

2.11 RACEWAYS

A. Conduit and Boxes: Comply with Section 260533 "Raceway and Boxes for Electrical Systems."[ Flexible metal conduit shall not be used.]

1. Outlet boxes shall be not less than 2 inches (50 mm) wide, 3 inches (75 mm) high, and 2-1/2 inches (64 mm) deep.

PART 3 -  EXECUTION

3.1 WIRING METHODS

Retain one of first two paragraphs below and coordinate with Drawings. Delete both if wiring methods for system are indicated on Drawings. Coordinate selection with "Raceways" Article.

A. Wiring Method: Install cables in raceways and cable trays except within consoles, cabinets, desks, and counters[, and except in accessible ceiling spaces and in gypsum board partitions where unenclosed wiring method may be used]. Conceal raceway and cables except in unfinished spaces.

Retain first subparagraph below if selecting option in paragraph above.

1. Install plenum cable in environmental air spaces, including plenum ceilings.

2. Comply with requirements for raceways and boxes specified in Section 260533 "Raceway and Boxes for Electrical Systems."

B. Wiring Method: Conceal conductors and cables in accessible ceilings, walls, and floors where possible.

C. Wiring within Enclosures: Bundle, lace, and train cables to terminal points with no excess and without exceeding manufacturer's limitations on bending radii. Provide and use lacing bars and distribution spools.

3.2 INSTALLATION OF RACEWAYS

A. Comply with requirements in Section 260533 "Raceway and Boxes for Electrical Systems" for installation of conduits and wireways.

B. Install manufactured conduit sweeps and long-radius elbows whenever possible.

3.3 INSTALLATION OF CABLES

A. Comply with NECA 1.

B. General Cable Installation Requirements:

1. Terminate conductors; no cable shall contain unterminated elements. Make terminations only at outlets and terminals.

2. Splices, Taps, and Terminations: Arrange on numbered terminal strips in junction, pull, and outlet boxes; terminal cabinets; and equipment enclosures. Cables may not be spliced.

3. Secure and support cables at intervals not exceeding 30 inches (760 mm) and not more than 6 inches (150 mm) from cabinets, boxes, fittings, outlets, racks, frames, and terminals.

4. Bundle, lace, and train conductors to terminal points without exceeding manufacturer's limitations on bending radii. Install lacing bars and distribution spools.

5. Do not install bruised, kinked, scored, deformed, or abraded cable. Do not splice cable between termination, tap, or junction points. Remove and discard cable if damaged during installation and replace it with new cable.

6. Cold-Weather Installation: Bring cable to room temperature before dereeling. Heat lamps shall not be used.

C. Open-Cable Installation:

1. Install cabling with horizontal and vertical cable guides in telecommunications spaces with terminating hardware and interconnection equipment.

2. Suspend speaker cable not in a wireway or pathway a minimum of 8 inches (200 mm) above ceiling by cable supports not more than [60 inches (1524 mm)] <Insert dimension> apart.

3. Cable shall not be run through structural members or be in contact with pipes, ducts, or other potentially damaging items.

D. Separation of Wires: Separate speaker-microphone, line-level, speaker-level, and power wiring runs. Install in separate raceways or, where exposed or in same enclosure, separate conductors at least 12 inches (300 mm) apart for speaker microphones and adjacent parallel power and telephone wiring. Separate other intercommunication equipment conductors as recommended by equipment manufacturer.

3.4 INSTALLATION

A. Match input and output impedances and signal levels at signal interfaces. Provide matching networks where required.

B. Identification of Conductors and Cables: Color-code conductors and apply wire and cable marking tape to designate wires and cables so they identify media in coordination with system wiring diagrams.

C. Wall-Mounted Outlets: Flush mounted.

D. Floor-Mounted Outlets: Conceal in floor and install cable nozzles through outlet covers. Secure outlet covers in place. Trim with carpet in carpeted areas.

E. Conductor Sizing: Unless otherwise indicated, size speaker circuit conductors from racks to loudspeaker outlets not smaller than No. 18 AWG and conductors from microphone receptacles to amplifiers not smaller than No. 22 AWG.

F. Weatherproof Equipment: For units that are mounted outdoors, in damp locations, or where exposed to weather, install consistent with requirements of weatherproof rating.

G. Speaker-Line Matching Transformer Connections: Make initial connections using tap settings indicated on Drawings.

H. Connect wiring according to Section 260519 "Low-Voltage Electrical Power Conductors and Cables."

3.5 FIELD QUALITY CONTROL

A. Perform tests and inspections.

Retain subparagraph below to require a factory-authorized service representative to assist Contractor with inspections, tests, and adjustments.

1. Manufacturer's Field Service: Engage a factory-authorized service representative to inspect components, assemblies, and equipment installations, including connections, and to assist in testing.

Retain first paragraph below to describe tests and inspections to be performed.

B. Tests and Inspections:

1. Schedule tests with at least seven days' advance notice of test performance.

2. After installing public address and mass notification systems and after electrical circuitry has been energized, test for compliance with requirements.

3. Operational Test: Perform tests that include originating program and page messages at microphone outlets, preamplifier program inputs, and other inputs. Verify proper routing and volume levels and that system is free of noise and distortion.

4. Acoustic Coverage Test: Feed pink noise into system using octaves centered at 500 and 4000 Hz. Use sound-level meter with octave-band filters to measure level at five locations in each zone. For spaces with seated audiences, maximum permissible variation in level is plus or minus 2 dB. In addition, the levels between locations in same zone and between locations in adjacent zones must not vary more than plus or minus 3 dB.

5. Power Output Test: Measure electrical power output of each power amplifier at normal gain settings of 50, 1000, and 12,000 Hz. Maximum variation in power output at these frequencies must not exceed plus or minus 1 dB.

C. Inspection: Verify that units and controls are properly labeled and interconnecting wires and terminals are identified. Prepare a list of final tap settings of paging speaker-line matching transformers.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

D. Public address and mass notification systems will be considered defective if they do not pass tests and inspections.

E. Prepare test and inspection reports.

1. Include a record of final speaker-line matching transformer-tap settings, and signal ground-resistance measurement certified by Installer.

END OF SECTION 275116

	PUBLIC ADDRESS AND MASS NOTIFICATION SYSTEMS
	275116 - 1



