Copyright 2012 AIA
MasterSpec Professional
03/12

Copyright 2012 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 275119 - SOUND MASKING SYSTEMS
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Electronic noise generators.

2. Amplifiers.

3. Wiring.

4. Masking speaker assemblies.

5. Controls.

6. Component mounting racks.

1.2 DEFINITIONS

Retain definition(s) remaining after this Section has been edited.

A. Covered Spaces: Spaces above which masking speakers are installed.

1.3 SYSTEM DESCRIPTION

Revise this article to indicate extent of system coverage required. Coordinate with Drawings to indicate extent of system or individual zones to be covered. Revise number of channels and modify number of zones to suit Project. See Evaluations.

A. Zones: [Single] [Multiple]-zone coverage.

Retain one of first two paragraphs below to specify number of channels. See Evaluations.

B. Channels: Single channel of masking sound to each zone.

C. Channels: Separate channel of masking sound to each of [two] [three] groups of speakers in each zone.

D. Signal Levels: Individually adjustable for each of 14 one-third octave bands centered at 200 through 4000 Hz, for sound-masking noise channels.

Options in first paragraph below specify system performance for typical office occupancies. Revise to suit Project.

E. Sound-Power Level Produced by System: Match [NC 40] <Insert value> contour between [400 and 2000 Hz] <Insert value>, with smooth roll-off above and below those frequencies.

1. Initial Level: [40 dB] <Insert value>, A-weighted.

2. Final Adjusted Level: [40 to 50 dB] <Insert value>, A-weighted. Determine final level for each space individually by measurement as specified in Part 3.

3. Measurements: Made under calibration conditions.

F. Maximum Local Variance of Sound-Power Level: [6 dB] <Insert value> for the 500-Hz octave band and [3 dB] <Insert value> for the 1000-, 2000-, and 4000-Hz octave bands for 75 percent of the locations in covered spaces.

G. Maximum Average Range of Sound-Power-Level Deviation: [2 dB] <Insert value> in the 250-, 2000-, and 4000-Hz octave bands and [1.5 dB] <Insert value> for the 500- and 1000-Hz octave bands for all locations.

H. Directional Effect: People in covered spaces under calibration conditions cannot determine source of masking sound.

I. Uniformity with Respect to Time: One-minute time-averaged sound-pressure level of any octave band of masking sound from [250 to 8000 Hz] <Insert value> remains constant in any space to within a standard deviation of [2 dB] <Insert value> when measured over a 30-minute period.

J. Sound Quality: No audible hum or noise from this system in covered spaces when noise generators are off and power amplifiers are on with input volume controls set at [50] <Insert number> percent.

1.4 ACTION SUBMITTALS

A. Product Data: For each type of product indicated. Include nationally recognized testing laboratory listing data.

B. Shop Drawings: Dimensioned plans and elevations showing minimum clearances and installed features and devices for system components. Show types and locations of masking speakers and their wiring connections, channel assignments, and axis orientations. Show ducts, beams, and other significant sound-reflecting and -absorbing elements in ceiling space and show locations of partitions below ceiling. Include a diagram showing interconnection of major system components for each zone and channel and indicating grounding connections.

1. Wiring Diagrams: For power, signal, and control wiring.

1.5 INFORMATIONAL SUBMITTALS

A. Field quality-control reports.

1.6 CLOSEOUT SUBMITTALS

A. Operation and maintenance data.

1.7 QUALITY ASSURANCE

A. Installer Qualifications: An experienced installer trained and approved by manufacturer of sound-masking equipment.

B. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

C. Comply with NFPA 70.

D. Comply with UL 813 unless a more stringent standard is specified in Part 2.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers. Retain one of two paragraphs and list of manufacturers below. See Section 016000 "Product Requirements."

A. Manufacturers: Subject to compliance with requirements, [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. American Sound Masking, LLC.

2. Atlas Sound LP.

3. Dynasound, Inc.

4. GE Security, Sound and Communications.

5. Lencore.

6. LynTec, Inc.

7. Moeller, K. R. Associates Ltd.

8. Proudfoot Company, Inc. (The).

9. Sound Advance.

10. <Insert manufacturer's name.>

2.2 GENERAL REQUIREMENTS FOR SOUND-MASKING EQUIPMENT

A. Components: Modular plug-in, heavy-duty, industrial-grade integrated circuit devices.

B. Protection from Power Line Surges: Integral surge protection devices listed in UL 1449.

2.3 NOISE GENERATOR AND FILTER UNITS

A. Digital Masking Generator Spectra: Pink, white, and superwhite.

B. Pink Noise Generator: Output octave bands from 30 to 4000 Hz.

C. Filters for One-Third Octave Bands: Adjustable from 10 dB of boost to 10 dB of cut at each center frequency.

D. Mixer Inputs: Two high level and one microphone level.

E. High-Pass Filter: Approximate range of cutoff adjustment is 37 to 400 Hz.

F. Low-Pass Filter: Adjustable roll-off frequency 100 Hz to 10 kHz.

G. High-Cut Filter: Approximate range of cutoff adjustment is 180 to 9000 Hz with slope varying to 12 dB per octave.

H. Auxiliary Inputs: Able to accept two, high-level, auxiliary signals such as music and telephone paging as well as general paging.

I. Mounting: Shelf or rack 3-1/2 inches (90 mm) high.

2.4 POWER AMPLIFIERS

A. Power Amplifiers: Comply with CEA-426, and have the following minimum features:

1. Mounting: Rack mounted.

2. Output Regulation: Less than 2 dB from zero to full load.

3. Total Harmonic Distortion: Less than 3 percent, at rated power output from 50 to 12,000 Hz.

4. Signal-to-Noise Ratio: 60 dB or greater, at rated output.

5. Frequency Response: Within plus or minus 2 dB from 50 to 12,000 Hz.

6. Input: From internal masking or mixer board, or from an exterior source such as an automatic level control or other mixer.

2.5 MASKING SPEAKER ASSEMBLIES

A. Speakers: Cone type, with the following minimum features:

1. Minimum Axial Sensitivity: 45 dB.

2. Frequency Response: Within plus or minus 3 dB from 50 to 15,000 Hz.

3. Size: 8 inches (200 mm) with 1-inch (25-mm) voice coil and minimum 5-oz. (142-g) ceramic magnet unless otherwise indicated.

4. Dispersion Angle: 100 degrees.

5. Rated Output Level: 10 W.

B. Configuration: Dual 8-inch (200-mm) and dual 5-inch (125-mm) units mounted on metal baffles and arranged for optimum, multidirectional, angular sound distribution. Arrange units for suspension from the building structure above the ceiling.

C. Matching Transformers: Full-power rated with 4 standard taps, and a maximum insertion loss of 0.5 dB.

D. Assemblies installed in air-handling spaces shall comply with NFPA 70 requirements for rate of heat-release and rate of smoke-release characteristics. Tests for these requirements shall be according to UL 2043.

2.6 WIRE

A. Speaker Wire: UTP cable complying with manufacturer's requirements; listed and labeled for environmental air plenums where cable is indicated in plenum spaces and is not indicated to be in raceway. Comply with requirements in Section 271500 "Communications Horizontal Cabling."

2.7 COMPONENT MOUNTING RACKS

A. Configuration: Comply with CEA-310-E. Factory-fabricated units designed for interchangeable mounting and enclosure of standard 19-inch (482-mm) relay rack modules.

Coordinate first paragraph below with Drawings.

B. Mounting Provisions: Equipped for freestanding floor mounting.

C. Cabinet: Factory-finished steel with component mounting rails and prewired plug strips for component power connections. Full front and rear doors with continuous hinges, handles, and cylindrical keyed locks.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Speaker Assemblies: Suspend with chains from building structure above ceilings so bottom of assembly is 6 to 8 inches (150 to 200 mm) above upper plane of finished ceiling material. Use eyebolts on speaker assemblies for attachment. Suspend independently of supports for components of other building systems.

Retain first paragraph below if piping is required to withstand seismic design loads.

B. Install seismic restraints on speakers. Comply with requirements for seismic-restraint devices specified in Section 260548.16 "Seismic Controls for Electrical Systems."

C. Speaker Connections: For two- or three-channel systems, connect speaker assemblies alternatively so masking sound is redundant throughout zones of coverage.

Retain one of first two paragraphs below and coordinate with Drawings. Delete both paragraphs if wiring methods for system are indicated on Drawings.

D. Wiring Method: Install cables in raceways and cable trays except within consoles, cabinets, desks, and counters and unless otherwise indicated.

Retain one or both of first two subparagraphs below to make exceptions to the wiring method specified above.

1. Except raceways are not required in accessible indoor ceiling spaces and attics.

2. Except raceways are not required in hollow gypsum board partitions.

3. Conceal raceways and wiring except in unfinished spaces.

E. Wiring Method: Conceal conductors and cables in accessible ceilings, walls, and floors where possible.

Retain first subparagraph below if retaining option for unenclosed wiring method.

1. Install plenum cable in environmental air spaces, including plenum ceilings.

2. Comply with requirements specified in Section 271500 "Communications Horizontal Cabling" for cable trays

3. Comply with requirements for raceways and boxes specified in Section 260533 "Raceway and Boxes for Electrical Systems."

4. Comply with requirements in Section 271500 "Communications Horizontal Cabling."

F. Wiring within Enclosures: Bundle, lace, and train conductors to terminal points with no excess and without exceeding manufacturer's limitations on bending radii. Provide and use lacing bars and distribution spools.

Retain first paragraph below for cable wiring method.

G. Exposed Cable: Install parallel to building lines, follow surface contours, and support as recommended by manufacturer.

Coordinate first paragraph below with Drawings.

H. Grounding: As recommended by manufacturers unless more stringent requirements are indicated. Ground equipment and conductors to eliminate shock hazard and to minimize ground loops, common-mode returns, noise pickup, cross talk, and other impairments with a maximum of 5-ohm to ground at main equipment location. Measure, record, and report ground resistance.

I. Impedance Matching: For system components, including connecting cable, provide end-to-end level and impedance-matched signal paths. Use matching networks and balancing devices at connections where necessary to avoid mismatches.

J. Splices, Taps, and Terminations: Make splices, taps, and terminations on numbered terminal strips in junction, pull, and outlet boxes; terminal cabinets; and equipment enclosures.

3.2 IDENTIFICATION

A. Use color-coded conductors and apply wire and cable marking tape to designate wires and cables so media are identified in coordination with system wiring diagrams. Comply with requirements for identification specified in Section 260553 "Identification for Electrical Systems."

B. Label speaker assemblies as to channel, zone, and address.

3.3 FIELD QUALITY CONTROL

Retain first paragraph below to require Contractor to perform tests and inspections.

A. Perform tests and inspections.

Retain subparagraph below to require a factory-authorized service representative to assist Contractor with inspections, tests, and adjustments.

1. Manufacturer's Field Service: Engage a factory-authorized service representative to inspect components, assemblies, and equipment installations, including connections, and to assist in testing.

Retain first paragraph below to describe tests and inspections to be performed.

B. Tests and Inspections:

1. Operational Test: Start system to confirm proper operation. Remove malfunctioning units, replace with new units, and retest. Make initial sound-spectrum and -level adjustments for each zone.

2. Test and adjust controls and safeties. Replace damaged and malfunctioning controls and equipment.

3. Inspection: Verify that units and controls are properly labeled and interconnecting wires and terminals are identified.

4. Masking Sound-Power-Level Adjustments: Adjust independently for each space to minimum level between 40 and 50 dB that will provide speech privacy between adjacent workstations while complying with other system requirements.

C. Final Acceptance Testing: Provide a minimum of 10 days' notice of acceptance test performance schedule.

1. Tests and Calibration Conditions: Spaces shall be completely furnished but unoccupied; lights and HVAC systems shall be on; HVAC system testing and balancing shall be completed; and electronic ballasts, lighting relay panels, and low voltage transformers shall be in place.

2. Test Conditions: Complying with ASTM E 1130 and calculated according to ANSI S3.5.

3. Instrumentation: Use a professional-quality, sound-level meter with octave-band filters and documentation of recent calibration against recognized standards.

4. Record test observations, readings, and corrective actions.

5. System Tests: Include the following for each system zone:

a. Speaker Circuit Impedance Test: Measure impedance at 1000 Hz with amplifier disconnected, using a professional impedance meter or bridge. Locate and correct faults denoted by abnormal readings.

b. Ambient Sound-Level Tests: With system off, measure ambient sound level in one-third octave bands. Also measure ambient sound level as a single, wide-band, A-weighted reading.

c. Amplifier Noise Test: Check for performance specified in "System Description" Article with masking noise generator off and amplifiers on.

d. System Noise Test: With masking noise signal on and amplifiers adjusted at a working level 10 dB above ambient sound level, check for hum, buzz, rattle, or other operating deficiencies.

e. Spatial Uniformity Test: Measure sound level at locations no greater than 15 feet (4.6 m) o.c. throughout covered spaces to determine compliance with specified performance level.

f. Frequency Response Adjustment and Test: Adjust one-third octave frequency bands and other unit filters to provide response. Adjust to meet requirement of space speech intelligibility and quality of background sound. Comply with ANSI S3.2, CEA 426, and ASTM E 1110.

6. Adjust level of masking sound for each space so one-third octave band centered at 500 Hz has final selected sound-power level for that space. Measure deviation from listed values in one-third octave bands from 100 to 1000 Hz. Measured values must not deviate from those listed by more than 4 dB for open plan areas and 8 dB for enclosed offices. The total of individual band deviations in eight bands must not exceed 16 dB for open plan areas and 30 dB for enclosed offices.

7. Walk-through Test: People in covered spaces cannot discern speaker locations.

8. Temporal Stability Test: Check for uniformity of time by measuring sound level in each of 14 octave bands at one-minute intervals over a 30-minute test period. Deviations must not exceed limits specified in "System Description" Article.

9. Where required, space shall meet the Health Insurance Portability and Accountability Act for privacy and the Gramm-Leach Bliley Act to protect consumer personal and financial information in open office layouts.

D. Retest: Correct deficiencies identified by tests and observations and retest until meeting specified requirements.

E. Recording Control Settings and System Adjustments: Record final control settings and programming, and final tap setting of speaker matching transformers. Record final sound-level measurements and observations.

3.4 DEMONSTRATION

A. [Engage a factory-authorized service representative to train] [Train] Owner's maintenance personnel to adjust, operate, and maintain services.

END OF SECTION 275119

	SOUND MASKING SYSTEMS
	275119 - 1



