Copyright 2011 AIA
MasterSpec Professional
06/11

Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 280526 - GROUNDING AND BONDING FOR ELECTRONIC SAFETY AND SECURITY
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Grounding conductors.

2. Grounding connectors.

3. Grounding busbars.

1.2 DEFINITIONS

A. Signal Ground: The ground reference point designated by manufacturer of the system that is considered to have zero voltage.

1.3 ACTION SUBMITTALS

A. Product Data: For each type of product.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

2.1 CONDUCTORS

See "Grounding Products" Article in the Evaluations for discussion on alternative conductor materials.

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

1. Harger Lightning and Grounding.

2. Panduit Corp.

3. Tyco Electronics Corp.

4. <Insert manufacturer's name>.

B. Comply with UL 486A-486B.

C. Insulated Conductors: Stranded copper wire, green or green with yellow stripe insulation, insulated for 600 V, and complying with UL 83.

1. Ground wire for custom-length equipment ground jumpers shall be No. 6 AWG, 19-strand, UL-listed, Type THHN wire.

D. Bare Copper Conductors:

1. Solid Conductors: ASTM B 3.

2. Stranded Conductors: ASTM B 8.

3. Tinned Conductors: ASTM B 33.

Sizes and types of conductors in three subparagraphs below are typical examples. 28-kcmil (14.2-sq. mm) bonding cable in "Bonding Cable" Subparagraph is slightly larger than No. 6 AWG.

4. Bonding Cable: 28 kcmils (14.2 sq. mm), 14 strands of No. 17 AWG conductor, and 1/4 inch (6.3 mm) in diameter.

5. Bonding Conductor: No. 4 or No. 6 AWG, stranded conductor.

6. Bonding Jumper: Tinned-copper tape, braided conductors terminated with two-hole copper ferrules; 1-5/8 inches (41 mm) wide and 1/16 inch (1.6 mm) thick.

2.2 CONNECTORS

A. Irreversible connectors listed for the purpose. Listed by an NRTL as complying with NFPA 70 for specific types, sizes, and combinations of conductors and other items connected. Comply with UL 486A-486B.

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

B. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

C. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Burndy; Part of Hubbell Electrical Systems.

2. Chatsworth Products, Inc.

3. Harger Lightning and Grounding.

4. Panduit Corp.

5. Tyco Electronics Corp.

6. <Insert manufacturer's name>.

D. Compression Wire Connectors: Crimp-and-compress connectors that bond to the conductor when the connector is compressed around the conductor. Comply with UL 467.

1. Electroplated tinned copper, C and H shaped.

E. Busbar Connectors: Cast silicon bronze, solderless [compression] [or] [exothermic]-type mechanical connector; with a long barrel and two holes spaced on 5/8- or 1-inch (15.8- or 25.4-mm) centers for a two-bolt connection to the busbar.

F. Welded Connectors: Exothermic-welding kits of types recommended by kit manufacturer for materials being joined and installation conditions.

2.3 GROUNDING BUSBARS

Retain this article if size of grounding bus and mounting details are not indicated on Drawings. The default dimension is recommended by BICSI for telecommunications busbar.

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Chatsworth Products, Inc.

2. Harger Lightning and Grounding.

3. Panduit Corp.

4. <Insert manufacturer's name>.

Retain "Rack and Cabinet Grounding Busbars" Paragraph below if equipment cabinets and racks are not specified with grounding busbars.

C. Rack and Cabinet Grounding Busbars: Rectangular bars of hard-drawn solid copper, accepting conductors ranging from No. 14 to No. 2/0 AWG, NRTL listed as complying with UL 467, and complying with J-STD-607-A. Predrilling shall be with holes for use with lugs specified in this Section.

1. Cabinet-Mounted Busbar: Terminal block, with stainless-steel or copper-plated hardware for attachment to the cabinet.

2. Rack-Mounted Horizontal Busbar: Designed for mounting in 19- or 23-inch (483- or 584-mm) equipment racks. Include a copper splice bar for transitioning to an adjoining rack, and stainless-steel or copper-plated hardware for attachment to the rack.

3. Rack-Mounted Vertical Busbar: 72 or 36 inches (1827 or 914 mm long, with)stainless-steel or copper-plated hardware for attachment to the rack.

PART 3 -  EXECUTION

3.1 INSTALLATION

A. Comply with IEEE 1100, "Recommended Practice for Power and Grounding Electronic Equipment."

1. Ground cable shields, drain conductors, and equipment to eliminate shock hazard and to minimize ground loops, common-mode returns, noise pickup, cross talk, and other impairments.

2. Bond shields and drain conductors to ground at only one point in each circuit.

B. Signal Ground:

1. For each system, establish the signal ground and label that location as such.

Retain wire size option in subparagraph below if sized on Drawings. Retain only those listed locations that are suitable for this Project; delete if the location is indicated on Drawings.

2. Bond the signal ground to the alternating-current (ac) power system service by connecting to one of the following listed locations, using insulated[ No. 6 AWG,] stranded, Type THHN wire:

a. Grounding bar in an electrical power panelboard if located in the same room or space as the signal ground.

b. Telecommunications grounding busbar.

c. <Insert location>.

C. Comply with NECA 1.

3.2 APPLICATION

A. Conductors: Install solid conductor for [No. 8] <Insert number> AWG and smaller and stranded conductors for [No. 6] <Insert number> AWG and larger unless otherwise indicated.

B. Grounding and Bonding Conductors:

1. Install in the straightest and shortest route between the origination and termination point, and no longer than required. The bend radius shall not be smaller than eight times the diameter of the conductor. No one bend may exceed 90 degrees.

2. Install without splices.

3. Support at not more than 36-inch (900-mm) intervals.

3.3 CONNECTIONS

A. Stacking of conductors under a single bolt is not permitted when connecting to busbars.

B. Assemble the wire connector to the conductor, complying with manufacturer's written instructions and as follows:

1. Use crimping tool and the die specific to the connector.

2. Pretwist the conductor.

3. Apply an antioxidant compound to all bolted and compression connections.

Retain "Shielded Cable" Paragraph below if screened twisted-pair cables and coaxial cables are installed in communications equipment rooms.

C. Shielded Cable: Bond the shield of shielded cable to the signal ground. Comply with TIA/EIA-568-B.1 and TIA/EIA-568-B.2 when grounding screened, balanced, twisted-pair cables.

D. Rack- and Cabinet-Mounted Equipment: Bond powered equipment chassis to the cabinet or rack grounding bar. Power connection shall comply with NFPA 70; the equipment grounding conductor in the power cord of cord- and plug-connected equipment shall be considered as a supplement to bonding requirements in this Section.

3.4 FIELD QUALITY CONTROL

Retain "Perform tests and inspections" Paragraph below to require Contractor to perform tests and inspections.

A. Perform tests and inspections.

Retain "Tests and Inspections" Paragraph below to describe tests and inspections to be performed.

B. Tests and Inspections:

1. Inspect physical and mechanical condition. Verify tightness of accessible, bolted, electrical connections with a calibrated torque wrench according to manufacturer's written instructions.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

C. Grounding system will be considered defective if it does not pass tests and inspections.

D. Prepare test and inspection reports.

END OF SECTION 280526

	GROUNDING AND BONDING FOR ELECTRONIC SAFETY AND SECURITY
	280526 - 1



