Copyright 2012 AIA
MasterSpec Professional
03/12

Copyright 2012 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 283112 - ZONED (DC LOOP) FIRE-ALARM SYSTEM
TIPS:
To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single‑File Formatting/Toggle/Editor's Notes.
To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Fire-alarm control unit.

2. Manual fire-alarm boxes.

3. System smoke detectors.

4. Nonsystem smoke detectors.

5. Heat detectors.

6. Notification appliances.

7. Magnetic door holders.

8. Remote annunciator.

9. Digital alarm communicator transmitter.

B. Related Requirements:

Retain subparagraph below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

1. Section 280513 "Conductors and Cables for Electronic Safety and Security" for cables and conductors for fire-alarm systems.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product, including furnished options and accessories.

B. Shop Drawings: For fire-alarm system.

1. Comply with recommendations and requirements in the "Documentation" section of the "Fundamentals" chapter in NFPA 72.

2. Include plans, elevations, sections, details, and attachments to other work.

3. Include details of equipment assemblies. Indicate dimensions, weights, loads, required clearances, method of field assembly, components, and locations. Indicate conductor sizes, indicate termination locations and requirements, and distinguish between factory and field wiring.

4. Detail assembly and support requirements.

5. Include voltage drop calculations for notification-appliance circuits.

6. Include battery size calculations.

7. Include input/output matrix.

8. Include statement from manufacturer that all equipment and components have been tested as a system and meet all requirements in this Specification and in NFPA 72.

9. Include performance parameters and installation details for each detector.

10. Verify that each duct smoke detector is listed for the complete range of air velocity, temperature, and humidity possible when air-handling system is operating.

11. Include plans, sections, and elevations of heating, ventilating, and air-conditioning ducts, drawn to scale; coordinate location of duct smoke detectors and access to them.

a. Show critical dimensions that relate to placement and support of sampling tubes, detector housing, and remote status and alarm indicators.

b. Show field wiring required for HVAC unit shutdown on alarm.

c. Locate detectors according to manufacturer's written recommendations.

Retain subparagraph below for projects where routing of cable or conduit is critical and only outlet locations are indicated on Drawings.

12. Include floor plans to indicate final outlet locations showing zone designation of each device. Show size and route of cable and conduits and point-to-point wiring diagrams.

C. General Submittal Requirements:

Retain first subparagraph below if a fire-alarm construction permit is required prior to the Work of this Section and the permit is issued by authorities having jurisdiction after the review and approval of Shop Drawings.

1. Submittals shall be approved by authorities having jurisdiction prior to submitting them to Architect.

See Editing Instruction No. 2 in the Evaluations for discussion about qualifications for system design and installation. Coordinate subparagraph below with "Quality Assurance" Article.

2. Shop Drawings shall be prepared by persons with the following qualifications:

a. Trained and certified by manufacturer in fire-alarm system design.

b. NICET-certified fire-alarm technician; [Level III] [Level IV] minimum.

Retain subparagraph below if authorities having jurisdiction have licensing requirements.

c. Licensed or certified by authorities having jurisdiction.

Retain "Delegated-Design Submittal" Paragraph below if design services have been delegated to Contractor.

D. Delegated-Design Submittal: For notification appliances and smoke and heat detectors, in addition to submittals listed above, indicate compliance with performance requirements and design criteria, including analysis data, signed and sealed by the qualified professional engineer responsible for their preparation.

1. Drawings showing the location of each smoke and heat detector, ratings of each, and installation details as needed to comply with listing conditions of the device.

2. Design Calculations: Calculate requirements for selecting the spacing and sensitivity of detection, complying with NFPA 72. Calculate spacing and intensities for strobe signals and sound-pressure levels for audible appliances.

3. Indicate audible appliances required to produce square wave signal per NFPA 72.

1.3 INFORMATIONAL SUBMITTALS

Coordinate "Qualification Data" Paragraph below with qualification requirements in Section 014000 "Quality Requirements" and as may be supplemented in "Quality Assurance" Article.

A. Qualification Data: For Installer.

Retain "Seismic Qualification Certificates" Paragraph below if required by seismic criteria applicable to Project. Coordinate with Section 260548.16 "Seismic Controls for Electrical Systems." See ASCE/SEI 7 for certification requirements for equipment and components.

B. Seismic Qualification Certificates: For fire-alarm control unit, accessories, and components, from manufacturer.

C. Field quality-control reports.

D. Sample warranty.

1.4 CLOSEOUT SUBMITTALS

A. Operation and Maintenance Data: For fire-alarm systems and components to include in emergency, operation, and maintenance manuals.

1. In addition to items specified in Section 017823 "Operation and Maintenance Data," include the following[ and deliver copies to authorities having jurisdiction]:

a. Comply with the "Records" section of the "Inspection, Testing and Maintenance" chapter in NFPA 72.

b. Provide the "Fire Alarm and Emergency Communications System Record of Completion Documents" according to the "Completion Documents" article in the "Documentation" section of the "Fundamentals" chapter in NFPA 72.

c. Complete wiring diagrams showing connections between all devices and equipment.

d. Riser diagram.

e. Record copy of site-specific software.

f. Provide the "Inspection and Testing Form" according to the "Inspection, Testing and Maintenance" chapter in NFPA 72, and include the following:

1) Equipment tested.

2) Frequency of testing of installed components.

3) Frequency of inspection of installed components.

4) Requirements and recommendations related to results of maintenance.

5) Manufacturer's user training manuals.

g. Manufacturer's required maintenance related to system warranty requirements.

h. Abbreviated operating instructions for mounting at fire-alarm control unit and each annunciator unit.

1.5 QUALITY ASSURANCE

Retain one of or both "Installer Qualifications" paragraphs below. See Editing Instruction No. 2 in the Evaluations for a discussion about Installer qualifications. Coordinate with "Informational Submittals" Article.

A. Installer Qualifications: Personnel shall be trained and certified by manufacturer for installation of units required for this Project.

B. Installer Qualifications: Installation shall be by personnel certified by NICET as fire-alarm [Level II] [Level III] [Level IV] technician.

Retain one of four "NFPA Certification" paragraphs below to require independent system verification.

C. NFPA Certification: Obtain certification according to NFPA 72 by an NRTL (nationally recognized testing laboratory).

D. NFPA Certification: Obtain certification according to NFPA 72 by a UL-listed alarm company.

E. NFPA Certification: Obtain certification according to NFPA 72 in the form of a placard by an FM Global-approved alarm company.

F. NFPA Certification: Obtain certification according to NFPA 72 by <Insert certification agency>.

1.6 WARRANTY

A. Special Warranty: Manufacturer agrees to repair or replace fire-alarm system equipment and components that fail in materials or workmanship within specified warranty period.

Verify available warranties and warranty periods for units and components.

1. Warranty Extent: All equipment and components not covered in the Maintenance Service Agreement.

2. Warranty Period: [Five] <Insert number> years from date of Substantial Completion.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

2.1 SYSTEM DESCRIPTION

Descriptions in this article are examples only; revise to suit Project.

Retain "Source Limitations for Fire-Alarm System and Components" Paragraph below for fire-alarm projects that are renovations of or additions to existing facilities.

A. Source Limitations for Fire-Alarm System and Components: Components shall be compatible with and operate as an extension of existing system. Provide system manufacturer's certification that all components provided have been tested as, and will operate as, a system.

B. Noncoded system dedicated to fire-alarm service only.

C. All components provided shall be listed for use with the selected system.

D. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

2.2 SYSTEMS OPERATIONAL DESCRIPTION

Revise this article to provide a functional description applicable to Project.

The word "systems" in the option in first paragraph below refers to systems specified in other Sections that initiate fire-alarm signals. An example is smoke detectors supplied under Section 087100 "Door Hardware" that provide for closing of smoke doors or unlocking of related doors. Coordinate with requirements in other Sections that specify those other systems.

A. Fire-alarm signal initiation shall be by one or more of the following devices[ and systems]:

Retain only those devices and systems in subparagraphs below applicable to Project. Coordinate with requirements in other Sections that specify listed devices and systems.

1. Manual stations.

2. Heat detectors.

3. Smoke detectors.

4. Duct smoke detectors.

5. Carbon monoxide detectors.

6. Automatic sprinkler system water flow.

7. Fire-extinguishing system operation.

8. Fire standpipe system.

9. Dry system pressure flow switch.

10. <Insert alarm-initiating devices and systems>.

B. Fire-alarm signal shall initiate the following actions:

Retain only those actions in subparagraphs below applicable to Project. Coordinate with requirements in other Sections that specify listed devices and systems.

1. Continuously operate alarm notification appliances.

2. Identify alarm zone at fire-alarm control unit[ and remote annunciators].

3. Transmit an alarm signal to the remote alarm receiving station.

4. Unlock electric door locks in designated egress paths.

5. Release fire and smoke doors held open by magnetic door holders.

6. Switch heating, ventilating, and air-conditioning equipment controls to fire-alarm mode.

7. Close smoke dampers in air ducts of designated air-conditioning duct systems.

8. Activate elevator power shunt trip.

9. Activate emergency lighting control.

If supplies are not essential to life safety, retain first subparagraph below for shutoffs installed in supplies that may be hazardous.

10. Activate emergency shutoffs for gas and fuel supplies.

11. Record events in the system memory.

12. <Insert signal-initiating actions>.

C. Supervisory signal initiation shall be by one or more of the following devices and systems:

Retain first subparagraph below if applicable to Project. Coordinate with requirements in other Sections that specify listed devices and systems.

1. Valve supervisory switch.

2. Elevator shunt-trip supervision.

3. Loss of communication with any panel on the network.

4. <Insert supervisory signal-initiating devices or systems>.

D. System trouble signal initiation shall be by one or more of the following devices and actions:

Retain only those devises and actions in subparagraphs below applicable to Project. Coordinate with requirements in other Sections that specify listed devices and systems.

1. Open circuits, shorts, and grounds in designated circuits.

2. Opening, tampering with, or removing alarm-initiating and supervisory signal-initiating devices.

3. Loss of primary power at fire-alarm control unit.

4. Ground or a single break in internal circuits of fire-alarm control unit.

5. Abnormal ac voltage at fire-alarm control unit.

6. Break in standby battery circuitry.

7. Failure of battery charging.

8. Abnormal position of any switch at fire-alarm control unit[ or annunciator].

9. <Insert trouble signal-initiating devices and actions>.

E. System Trouble and Supervisory Signal Actions:

1. Initiate notification appliances.

2. Annunciate at fire-alarm control unit[ and remote annunciators].

3. After a time delay of [200 seconds] <Insert time delay>, transmit a trouble or supervisory signal to the remote alarm receiving station.

2.3 PERFORMANCE REQUIREMENTS

Insert other Project-specific system requirements, such as Owner's insurance company standards.

Retain "Seismic Performance" Paragraph below with "Seismic Qualification Certificates" Paragraph in "Informational Submittals" Article for projects requiring seismic design. Delete paragraph if performance requirements are indicated on Drawings. Model building codes and ASCE/SEI 7 establish criteria for buildings subject to earthquake motions. Coordinate requirements with structural engineer. Verify requirements of authorities having jurisdiction.

A. Seismic Performance: Fire-alarm control unit and raceways shall withstand the effects of earthquake motions determined according to [ASCE/SEI 7] <Insert requirement>.

Retain subparagraph below to define the term "withstand" as it applies to this Project. Definition varies with type of building and occupancy and is critical to valid certification. Option is used for essential facilities where equipment must operate immediately after an earthquake.

1. The term "withstand" means "the unit will remain in place without separation of any parts from the device when subjected to the seismic forces specified[ and the unit will be fully operational after the seismic event]."

2.4 FIRE-ALARM CONTROL UNIT

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Bosch Security Systems.

2. Faraday.

3. Fike Corporation.

4. Fire-Lite Alarms.

5. GAMEWELL.

6. GE UTC Fire & Security; A United Technologies Company.

7. Keltron Corporation.

8. Mircom Technologies, Ltd.

9. Notifier.

10. Siemens Industry, Inc.; Fire Safety Division.

11. Silent Knight.

12. SimplexGrinnell LP.

13. <Insert manufacturer's name>.

Coordinate "General Requirements for Fire-Alarm Control Unit" Paragraph below with implementation details and Drawings.

C. General Requirements for Fire-Alarm Control Unit:

1. Modular, power-limited design with electronic modules, UL 864 listed.

a. Include a real-time clock for time annotation of events.

b. The FACP shall be listed for connection to a central-station signaling system service.

D. Alphanumeric Display and System Controls: Display alarm, supervisory, and component status messages and the programming and control menu.

1. Annunciator and Display: Liquid-crystal type, [one line] [two lines] of [40] [80] characters, minimum.

Fire-alarm circuits are defined by both a pathway class designation, which gives performance requirements, and a pathway survivability designation, which gives fire-resistance requirements during abnormal operating conditions. Retain one or more options in "Circuits" Paragraph below. Indicate class on Drawings if more than one pathway class is required. Class A and Class X pathways are generally used only in larger systems and where the critical nature of the protected premises dictates the use of redundant pathways. Class B has been, in the past, the most used pathway type. Class C is for network communications and is unlikely to be used in a zoned fire-alarm system. Class D is for devices that fail in a safe condition such as door locks that fail to open. Class E is for specific circuits that do not require circuit integrity monitoring. Classes X, C, D, and E are not likely to be used in a zoned fire-alarm system, but they can be added if necessary. See NFPA 72 for these circuit types. Class A circuits are included in this Short Form Specification only because they are typically provided as standard for one circuit that can be used as either Class A or Class B. See Editing Instruction No. 3 in the Evaluations for further discussion of pathway class designation.

E. Circuits:

1. No Fewer Than [Five] <Insert number> Initiating-Device Circuits:

Number in subparagraph above should be the sum of numbers in first two subparagraphs below.

a. [Four] <Insert number> circuits, NFPA 72, Class B.

b. [One] <Insert number> circuit(s), NFPA 72, Class A.

2. No Fewer Than [Two] <Insert number> Notification-Appliance Circuits: NFPA 72, Class B.

NFPA 72 requires that fire-alarm system design include the designation of system pathway survivability unless no provisions for pathway survivability are included. Capacities on a single circuit should be determined based on the amount of detection that is lost during a fault condition and the resulting impact on life safety or property protection. See Editing Instruction No. 3 in the Evaluations for discussion about determining circuit survivability.

3. Pathway Survivability: [Level 0] [Level 1].

Retain "Serial Interfaces" Subparagraph below for connection of remote annunciators. Insert requirements if other accessories are added to fire-alarm control unit. Verify which type of serial interfaces the specified system uses for accessories.

4. Serial Interfaces:

a. One RS 485 port for remote annunciators.

b. One RS 232 port for personal computer configuration.

Retain "Notification-Appliance Circuit" Paragraph below if connecting to an existing system and retaining the use of the existing evacuation scheme that is different from ANSI S3.41.

F. Notification-Appliance Circuit: Operation shall sound a <Insert pattern>.

The ICC requires that smoke detectors in "Door Controls" Paragraph below be system detectors. NFPA 101 and NFPA 5000 allow them to be nonsystem detectors.

G. Door Controls: Door hold-open devices that are controlled by smoke detectors at doors in smoke-barrier walls shall [be] [not be] connected to fire-alarm system.

H. Transmission to Remote Alarm Receiving Station: Automatically transmit alarm, supervisory, and trouble signals to a remote alarm station.

"Primary Power" Paragraph below is for two-wire supply; revise if three-wire supply or an external dc supply is provided.

I. Primary Power: 24-V dc obtained from 120-V ac service and a power-supply module. Initiating devices, notification appliances, signaling lines, trouble signals, [supervisory signals] [and] [supervisory and digital alarm communicator transmitters] shall be powered by the 24-V dc source.

1. Alarm current draw of the entire fire-alarm system shall not exceed 80 percent of the power-supply module rating.

J. Secondary Power: 24-V dc supply system with batteries, automatic battery charger, and automatic transfer switch.

2.5 MANUAL FIRE-ALARM BOXES

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. AMSECO - A Potter Brand.

2. Bosch Security Systems.

3. Cooper Wheelock.

4. Faraday.

5. Federal Signal Corporation.

6. Fike Corporation.

7. Fire-Lite Alarms.

8. GAMEWELL.

9. GE UTC Fire & Security; A United Technologies Company.

10. Keltron Corporation.

11. Mircom Technologies, Ltd.

12. Notifier.

13. Siemens Industry, Inc.; Fire Safety Division.

14. Silent Knight.

15. SimplexGrinnell LP.

16. System Sensor.

17. <Insert manufacturer's name>.

C. General Requirements for Manual Fire-Alarm Boxes: Comply with UL 38.

1. Single-action mechanism, [breaking-glass or plastic-rod] [pull-lever] type.

2. Double-action mechanism requiring two actions to initiate an alarm, [breaking-glass or plastic-rod] [pull-lever] type.

3. Station Reset: Key- or wrench-operated switch.

2.6 SYSTEM SMOKE DETECTORS

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Bosch Security Systems.

2. Faraday.

3. Fenwal Protection Systems; A UTC Fire & Security Company.

4. Fire-Lite Alarms.

5. GAMEWELL.

6. GE UTC Fire & Security; A United Technologies Company.

7. Gentex Corporation.

8. Harrington Signal, Inc.

9. Keltron Corporation.

10. Mircom Technologies, Ltd.

11. Notifier.

12. Siemens Industry, Inc.; Fire Safety Division.

13. Silent Knight.

14. SimplexGrinnell LP.

15. System Sensor.

16. <Insert manufacturer's name>.

C. General Requirements for System Smoke Detectors:

See Editing Instruction No. 7 in the Evaluations for discussion about detector locations.

1. Operating at 24-V dc, nominal.

In first subparagraph below, retain first option for additions to existing four-wire systems or if detector auxiliary contacts are used for critical control functions such as air-handler shutdowns. Otherwise, retain type based on class of initiating-device circuit.

2. Detectors shall be [four] [two]-wire type.

Retain "Base Mounting" Subparagraph below if mounting directly to outlet box is not required. Base-mounted detectors should be used for units with auxiliary alarm outputs.

3. Base Mounting: Detector and associated electronic components shall be mounted in a twist-lock module that connects to a fixed base. Provide terminals in the fixed base for connection to building wiring.

4. Self-Restoring: Detectors do not require resetting or readjustment after actuation to restore them to normal operation.

5. Integral Visual-Indicating Light: LED type, indicating detector has operated[ and power-on status].

Number of settable levels in fire-alarm control unit varies among manufacturers and between detector types. Indicate specific number of levels on Drawings or in the "Remarks" column of a detector schedule.

6. Provide multiple levels of detection sensitivity for each sensor[, with alarm-verification feature].

D. Photoelectric Smoke Detectors: Comply with UL 268.

If retaining "Ionization Smoke Detector" Paragraph below, indicate location of each detector type on Drawings.

E. Ionization Smoke Detector: Comply with UL 268.

Coordinate "Duct Smoke Detectors" Paragraph below with Drawings for power supply and fire-alarm control unit connections. Review two- and four-wire options in "General Requirements for System Smoke Detectors" Paragraph above. Delete paragraph below and retain "Nonsystem Smoke Detectors" Article for two-wire standalone operation where shutdown of fan is not required.

F. Duct Smoke Detectors: Photoelectric type complying with UL 268A.

1. Remote indication[ and test] station.[ Operating key switch initiates an alarm test.]

2. Weatherproof Duct Housing Enclosure: NEMA 250, Type 4X; NRTL listed for use with the supplied detector for smoke detection in HVAC system ducts.

3. Sampling Tubes: Design and dimensions as recommended by manufacturer for specific duct size, air velocity, and installation conditions where applied.

Retain "Relay Fan Shutdown" Subparagraph below if required for direct shutdown of the fan associated with the detector.

4. Relay Fan Shutdown: Rated to interrupt fan motor-control circuit.

2.7 CARBON MONOXIDE DETECTORS

A. Description: Listed for connection to fire-alarm system.

1. Mounting: Adapter plate for outlet box mounting.

2. Detector shall provide a means to test by introducing test carbon monoxide into the sensing cell.

3. Detector shall provide alarm contacts and trouble contacts.

4. Detector shall send trouble alarm when nearing end-of-life, power supply problems, or internal faults.

5. Detector shall be listed to comply with UL 2075.

6. Detectors shall be located, mounted, and wired according to manufacturer's written instructions.

7. Test button simulates an alarm condition.

2.8 NONSYSTEM SMOKE DETECTORS

See Editing Instruction No. 4 in the Evaluations for discussion about nonsystem smoke detectors.

A. General Requirements for Nonsystem Smoke Detectors:

1. Nonsystem smoke detectors shall be listed as compatible with the fire-alarm equipment installed or shall have a contact closure interface listed for the connected load.

2. Nonsystem smoke detectors shall meet the monitoring for integrity requirements in NFPA 72.

B. Single-Station Smoke Detectors:

Verify options in subparagraphs below with manufacturer; certain combinations of options may be unavailable.

1. Comply with UL 217; suitable for NFPA 101, residential occupancies; operating at 120-V ac[ with 9-V dc battery as the secondary power source. Provide with "low" or "missing" battery chirping-sound device].

2. Auxiliary Relays: One [Form C, rated at 0.5 A] [Form A and one Form C, both rated at 0.5 A].

3. Audible Notification Appliance: Piezoelectric sounder rated at 90 dBA at 10 feet (3 m) according to UL 464.

4. Visible Notification Appliance: 177-cd strobe.

5. Heat sensor, 135 deg F (57 deg C) [combination rate-of-rise and ]fixed temperature.

6. Test Switch: Push to test; simulates smoke at rated obscuration.

7. Tandem Connection: Allow tandem connection of number of indicated detectors; alarm on one detector shall actuate notification on all connected detectors.

8. Plug-in Arrangement: Detector and associated electronic components shall be mounted in a plug-in module that connects to a fixed base. Provide terminals in the fixed base for connection to building wiring.

9. Self-Restoring: Detectors shall not require resetting or readjustment after actuation to restore them to normal operation.

10. Integral Visual-Indicating Light: LED type, indicating detector has operated[ and power-on status].

C. Single-Station Duct Smoke Detectors:

1. Comply with UL 268A; operating at 120-V ac.

2. Base Mounting: Detector and associated electronic components shall be mounted in a twist-lock module that connects to a fixed base. The fixed base shall be designed for mounting directly to air duct. Provide terminals in the fixed base for connection to building wiring.

a. Weatherproof Duct Housing Enclosure: NEMA 250, Type 4X; listed for use with the supplied detector.

3. Sampling Tubes: Design and dimensions as recommended by manufacturer for specific duct size, air velocity, and installation conditions where applied.

Verify, with mechanical Drawings and Specifications, that shutdown in "Relay Fan Shutdown" Subparagraph below is required; if not required, delete subparagraph.

4. Relay Fan Shutdown: Rated to interrupt fan motor-control circuit.

2.9 HEAT DETECTORS

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Bosch Security Systems.

2. Faraday.

3. Fire-Lite Alarms.

4. GAMEWELL.

5. GE UTC Fire & Security; A United Technologies Company.

6. Gentex Corporation.

7. Harrington Signal, Inc.

8. Keltron Corporation.

9. Mircom Technologies, Ltd.

10. Notifier.

11. Siemens Industry, Inc.; Fire Safety Division.

12. Silent Knight.

13. SimplexGrinnell LP.

14. System Sensor.

15. <Insert manufacturer's name>.

C. General Requirements for Heat Detectors: Comply with UL 521.

Coordinate "Heat Detector, Combination Type" and "Heat Detector, Fixed-Temperature Type" paragraphs below with Drawings. Indicate fixed-temperature values on Drawings. See Editing Instruction No. 7 in the Evaluations for discussion about detector locations.

D. Heat Detector, Combination Type: Actuated by either a fixed temperature or a rate of rise.

1. Mounting: [Adapter plate for outlet box mounting] [Twist-lock base interchangeable with smoke-detector bases].

E. Heat Detector, Fixed-Temperature Type: Actuated by temperature that exceeds a fixed temperature.

1. Mounting: [Adapter plate for outlet box mounting] [Twist-lock base interchangeable with smoke-detector bases].

2.10 NOTIFICATION APPLIANCES

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

B. Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

1. Cooper Wheelock.

2. Federal Signal Corporation.

3. GE UTC Fire & Security; A United Technologies Company.

4. Gentex Corporation.

5. Harrington Signal, Inc.

6. Keltron Corporation.

7. Mircom Technologies, Ltd.

8. Siemens Industry, Inc.; Fire Safety Division.

9. SimplexGrinnell LP.

10. System Sensor.

11. <Insert manufacturer's name>.

C. General Requirements for Notification Appliances: Connected to notification-appliance signal circuits, zoned as indicated, equipped for mounting as indicated, and with screw terminals for system connections.

Retain "Combination Devices" Subparagraph below where applicable.

1. Combination Devices: Factory-integrated audible and visible devices in a single-mounting assembly, equipped for mounting as indicated, and with screw terminals for system connections.

Sound-level values in "Chimes, High-Level Output" and "Horns" paragraphs below are typical. Indicate sound output ratings on Drawings. Comply with interpretations of ADA-ABA Accessibility Guidelines by authorities having jurisdiction. See Editing Instruction No. 5 in the Evaluations for a discussion about audible system sound levels.

D. Chimes, High-Level Output: Vibrating type.

E. Horns: Electric-vibrating-polarized type, 24-V dc; with provision for housing the operating mechanism behind a grille. Comply with UL 464.

Indicate rated light output on Drawings. Required light output for visible alarm strobe lights varies from 75 to 177 cd, depending on the floor area and ceiling height of the space, the mounting height of the device, and whether the space is a sleeping area. See Editing Instruction No. 6 in the Evaluations for discussion about determining the light output of visible notification appliances.

F. Visible Notification Appliances: Xenon strobe lights complying with UL 1971, with clear or nominal white polycarbonate lens mounted on an aluminum faceplate. The word "FIRE" is engraved in minimum 1-inch- (25-mm-) high letters on the lens.

1. Mounting: Wall mounted unless otherwise indicated.

2. Flashing shall be in a temporal pattern, synchronized with other units.

3. Strobe Leads: Factory connected to screw terminals.

4. Mounting Faceplate: Factory finished, [red] [white].

2.11 MAGNETIC DOOR HOLDERS

Retain this article unless door holders are specified in Section 087100 "Door Hardware." If retaining, coordinate "Description" Paragraph below with Drawings and with Section 087100 "Door Hardware."

A. Description: Units are equipped for wall or floor mounting as indicated and are complete with matching doorplate.

1. Electromagnets: Require no more than 3 W to develop 25-lbf (111-N) holding force.

2. Wall-Mounted Units: Flush mounted unless otherwise indicated.

Retain one of two "Rating" subparagraphs below.

3. Rating: 24-V ac or dc.

4. Rating: 120-V ac.

B. Material and Finish: Match door hardware.

2.12 REMOTE ANNUNCIATOR

A. Description: Annunciator functions shall match those of fire-alarm control unit for alarm, supervisory, and trouble indications. Manual switching functions shall match those of fire-alarm control unit, including acknowledging, silencing, resetting, and testing.

1. Mounting: [Flush] [Surface] cabinet, NEMA 250, Type 1.

B. Display Type and Functional Performance: Alphanumeric display and LED indicating lights shall match those of fire-alarm control unit. Provide controls to acknowledge, silence, reset, and test functions for alarm, supervisory, and trouble signals.

2.13 DIGITAL ALARM COMMUNICATOR TRANSMITTER

Transmitter in this article is compatible with most central-station receiving equipment; however, verify specific compatibility and acceptability of this signal-transmission method for each project. NFPA 72 and UL 632 require dual telephone lines or other redundant communications.

A. Digital alarm communicator transmitter shall be acceptable to the remote central station and shall comply with UL 632.

B. Functional Performance: Unit shall receive an alarm, supervisory, or trouble signal from fire-alarm control unit and automatically capture [one] [two] telephone line(s) and dial a preset number for a remote central station. When contact is made with central station(s), signals shall be transmitted. If service on [either ]line is interrupted for longer than 45 seconds, transmitter shall initiate a local trouble signal and transmit the signal indicating loss of telephone line to the remote alarm receiving station over the remaining line. Transmitter shall automatically report telephone service restoration to the central station. If service is lost on both telephone lines, transmitter shall initiate the local trouble signal.

C. Local functions and display at the digital alarm communicator transmitter shall include the following:

1. Verification that both telephone lines are available.

2. Programming device.

3. LED display.

4. Manual test report function and manual transmission clear indication.

5. Communications failure with the central station or fire-alarm control unit.

6. <Insert local function>.

D. Digital data transmission shall include the following:

Retain applicable subparagraphs below; revise to match characteristics of fire-alarm control unit and requirements of the central station.

1. Zone of the alarm initiating device.

2. Zone of the supervisory signal.

3. Zone of the trouble initiating device.

4. Loss of ac supply.

5. Loss of power.

6. Low battery.

7. Abnormal test signal.

8. Communication bus failure.

9. <Insert signal to be transmitted>.

Retain "Secondary Power" Paragraph below if secondary power supply at fire-alarm control unit is inadequate or if additional supply is required by Project conditions.

E. Secondary Power: Integral rechargeable battery and automatic charger.

F. Self-Test: Conducted automatically every 24 hours with report transmitted to central station.

PART 3 -  EXECUTION

3.1 EQUIPMENT INSTALLATION

A. Comply with NFPA 72, NFPA 101, and requirements of authorities having jurisdiction for installation and testing of fire-alarm equipment. Install all electrical wiring to comply with requirements in NFPA 70 including, but not limited to, Article 760, "Fire Alarm Systems."

B. Connecting to Existing Equipment: Verify that existing fire-alarm system is operational before making changes or connections.

C. Install wall-mounted equipment, with tops of cabinets not more than 78 inches (1980 mm) above the finished floor.

Retain subparagraph below if Project requires seismic bracing. Coordinate with Section 260548.16 "Seismic Controls for Electrical Systems."

1. Comply with requirements for seismic-restraint devices specified in Section 260548.16 "Seismic Controls for Electrical Systems."

D. Manual Fire-Alarm Boxes:

1. Install manual fire-alarm box in the normal path of egress within 60 inches (1520 mm) of the exit doorway.

2. Mount manual fire-alarm box on a background of a contrasting color.

3. The operable part of manual fire-alarm box shall be between 42 inches (1060 mm) and 48 inches (1220 mm) above floor level. All devices shall be mounted at the same height unless otherwise indicated.

Indicate smoke- or heat-detector spacing on Drawings, based on the listing of the detectors and on space/ceiling-plane configurations. See Editing Instruction No. 7 in the Evaluations for discussion about detector locations.

E. Smoke- or Heat-Detector Spacing: Comply with NFPA 72.

F. Duct Smoke Detectors: Comply with NFPA 72 and NFPA 90A. Install sampling tubes so they extend the full width of duct. Tubes more than 36 inches (9100 mm) long shall be supported at both ends.

G. Elevator Shafts: Install a heat detector within 24 inches (610 mm) of each sprinkler head. Coordinate temperature rating and location with sprinkler rating and location. Do not install smoke detectors in sprinklered elevator shafts.

H. Single-Station Smoke Detectors: Where more than one smoke alarm is installed within a dwelling or suite, they shall be connected so that the operation of any smoke alarm causes the alarm in all smoke alarms to sound.

I. Remote Status and Alarm Indicators: Install in a visible location near each smoke detector, sprinkler water-flow switch, and valve-tamper switch that is not readily visible from normal viewing position.

Coordinate "Audible Alarm-Indicating Devices" Paragraph below with Drawings.

J. Audible Alarm-Indicating Devices: Install not less than 6 inches (150 mm) below the ceiling. Install bells and horns on flush-mounted back boxes with the device-operating mechanism concealed behind a grille. Install all devices at the same height unless otherwise indicated.

K. Visible Alarm-Indicating Devices: Install adjacent to each alarm bell or alarm horn and at least 6 inches (150 mm) below the ceiling. Install all devices at the same height unless otherwise indicated.

L. Device Location-Indicating Lights: Locate in public space near the device they monitor.

3.2 PATHWAYS

Retain one of first two paragraphs below.

A. Pathways above recessed ceilings and in nonaccessible locations may be routed exposed.

1. Exposed pathways located less than 96 inches (2440 mm) above the floor shall be installed in EMT.

B. Pathways shall be installed in EMT.

C. Exposed EMT shall be painted red enamel.

3.3 CONNECTIONS

Coordinate installations and specialty arrangements with Drawings and with requirements specified in related Sections. If Drawings are explicit enough, these requirements may be reduced or omitted.

Retain first paragraph below if smoke detectors specified in Section 087100 "Door Hardware" are alarm-initiating devices. Coordinate with "Door Controls" Paragraph in "Fire-Alarm Control Unit" Article.

A. For fire-protection systems related to doors in fire-rated walls and partitions and to doors in smoke partitions, comply with requirements in Section 087100 "Door Hardware." Connect hardware and devices to fire-alarm system.

1. Verify that hardware and devices are listed for use with installed fire-alarm system before making connections.

B. Connect supervised interface devices to the following devices and systems. Install the interface device less than 36 inches (910 mm) from the device controlled.

Coordinate list below with "Systems Operational Description" Article.

1. Smoke dampers in air ducts of designated HVAC duct systems.

2. Magnetically held-open doors.

3. Electronically locked doors and access gates.

4. Supervisory connections at valve supervisory switches.

Retain one of first two subparagraphs below.

5. Supervisory connections at fire-pump power failure including a dead-phase or phase-reversal condition.

6. Supervisory connections at fire-pump engine control panel.

7. <Insert connections>.

3.4 IDENTIFICATION

A. Identify system components, wiring, cabling, and terminals. Comply with requirements for identification specified in Section 260553 "Identification for Electrical Systems."

B. Install framed instructions in a location visible from fire-alarm control unit.

3.5 GROUNDING

A. Ground fire-alarm control unit and associated circuits; comply with IEEE 1100. Install a ground wire from main service ground to fire-alarm control unit.

B. Ground shielded cables at the control panel location only. Insulate shield at device location.

3.6 FIELD QUALITY CONTROL

Retain first paragraph below to require that field quality-control tests be witnessed. Local ordinance or custom may require that authorities having jurisdiction witness the testing.

A. Field tests shall be witnessed by [Architect] [authorities having jurisdiction] <Insert names or titles of witnesses>.

Retain "Perform the following tests and inspections" Paragraph below to describe tests and inspections to be performed.

If Owner selects and contracts with a central station or another remote alarm receiving station for continuing services, consider making the initial tests and inspections and reacceptance testing the obligation of Contractor and making the monthly, quarterly, semiannual, and annual tests and inspections the obligation of the remote alarm receiving station.

B. Perform the following tests and inspections[ with the assistance of a factory-authorized service representative]:

1. Visual Inspection: Conduct the visual inspection prior to testing.

a. Inspection shall be based on completed record Drawings and system documentation that is required by the "Completion Documents, Preparation" table in the "Documentation" section of the "Fundamentals" chapter in NFPA 72.

b. Comply with the "Visual Inspection Frequencies" table in the "Inspection" section of the "Inspection, Testing and Maintenance" chapter in NFPA 72; retain the "Initial/Reacceptance" column and list only the installed components.

2. System Testing: Comply with the "Test Methods" table in the "Testing" section of the "Inspection, Testing, and Maintenance" chapter in NFPA 72.

Retain first two subparagraphs below for additional tests not required by NFPA 72 but required by some jurisdictions. Engineer's calculations may be accepted by some jurisdictions in lieu of testing.

3. Test audible appliances for the public operating mode according to manufacturer's written instructions. Perform the test using a portable sound-level meter complying with Type 2 requirements in ANSI S1.4.

4. Test visible appliances for the public operating mode according to manufacturer's written instructions.

5. Factory-authorized service representative shall prepare the "Fire Alarm System Record of Completion" in the "Documentation" section of the "Fundamentals" chapter in NFPA 72 and the "Inspection and Testing Form" in the "Records" section of the "Inspection, Testing and Maintenance" chapter in NFPA 72.

C. Reacceptance Testing: Perform reacceptance testing to verify the proper operation of added or replaced devices and appliances.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

D. Fire-alarm system will be considered defective if it does not pass tests and inspections.

E. Prepare test and inspection reports.

Work in "Maintenance Test and Inspection" and "Annual Test and Inspection" paragraphs below is normally the responsibility of Owner. Retain one or both paragraphs if Owner needs additional time to contract for inspections required by NFPA 72.

F. Maintenance Test and Inspection: Perform tests and inspections listed for weekly, monthly, quarterly, and semiannual periods. Use forms developed for initial tests and inspections.

G. Annual Test and Inspection: One year after date of Substantial Completion, test fire-alarm system complying with the visual and testing inspection requirements in NFPA 72. Use forms developed for initial tests and inspections.

3.7 DEMONSTRATION

A. Train Owner's maintenance personnel to adjust, operate, and maintain fire-alarm system.

END OF SECTION 283112

	ZONED (DC LOOP) FIRE-ALARM SYSTEM
	283112 - 1



