

SECTION 10522PRIVATE 



FIRE EXTINGUISHERS, CABINETS, STAND PIPE CABINETS                                AND ACCESSORIES

1 PART 1 GENERAL


.1

SECTION INCLUDES



A.
Fire extinguishers.



B.
Cabinets.


.2

RELATED SECTIONS



A.
Section 04300 – Unit Masonry:  Roughed-in wall openings.


.3

REFERENCES



A.
ANSI/NFPA 10 ‑ Portable Fire Extinguishers.



B.
ANSI/UL 711 ‑ Rating and Fire Testing of Fire Extinguishers.

C. UL 299 ‑ Dry Chemical Fire Extinguishers.



D.
Reference to General Conditions.


.4

SUBMITTALS



A.
Submit under provisions of Section 01300.



B.
Shop Drawings: Indicate cabinet physical dimensions, rough‑in measurements for recessed cabinets.



C.
Product Data:  Provide extinguisher operational features, color and finish, anchorage details.



D.
Manufacturer's Installation Instructions: Indicate special criteria and wall opening coordination requirements.



E.
Manufacturer's Certificate: Certify that Products meet or exceed specified requirements.


.5

OPERATION AND MAINTENANCE DATA



A.
Submit under provisions of Section 01700.



B.
Maintenance Data: Include test, refill or recharge schedules and re‑certification requirements.


.6

QUALITY ASSURANCE



A.
Provide units conforming with ANSI/UL 711.


.7

REGULATORY REQUIREMENTS



A.
Conform to ANSI/NFPA 10 for requirements for extinguishers.


.8

ENVIRONMENTAL REQUIREMENTS



A.
Do not install extinguishers when ambient temperature may cause freezing of extinguisher ingredients.

2 PART 2 PRODUCTS


.1

MANUFACTURERS



A.
J.L. Industries.



B.
Larsen’s Manufacturing.



C.
Profile International.



D.
Substitutions: Under provisions of Section 01600.


.2

EXTINGUISHERS



A.
Dry Chemical Type:  UL 299,enameled steel  tank, with pressure gage; Class B:C, Size 10. UL Rated 4-A.


.3

CABINETS



A.
Metal:  Formed sheet steel, galvanized; 18 gage (1.2 mm) thick base metal.



B.
Configuration:  Semi‑recessed type, sized to accommodate accessories.



C.
Trim Type: Flat.



D.
Door: Aluminum  18  gage (1.2  mm) thick, reinforced for flatness and rigidity; latch access.



E.
Door Glazing:  Plastic, clear, 1/8 inch (3 mm) thick polycarbonate.



F.
Cabinet Mounting Hardware:
Appropriate to cabinet.


.4

ACCESSORIES



A.
Extinguisher Brackets: Formed steel, enamel finish.

B. Extinguisher Theft Alarm:  Battery operated alarm, 10 second delay for disarming, activated by opening cabinet door.



C.
Graphic Identification: “Fire Extinguisher”, silk-screened letters on glass.


.5

FABRICATION



A.
Form cabinet enclosure with right angle inside corners and seams.  Form perimeter trim.



B.
Pre‑drill for anchors.



C.
Hinge doors for 180 degree opening with continuous piano hinge. Provide roller type catch.



D.
Weld, fill, and grind components smooth.



E.
Glaze doors with resilient channel gasket glazing.


.6

FINISHES



A.
Extinguisher:  Steel, enamel to red color.



B.
Cabinet Exterior Trim and Door: Red baked enamel, color as selected.

C. Cabinet Interior: White enamel.

 .7

STAND PIPE CABINETS

Re-use existing cabinets.   Re-install hose connector to meet requirements of Fire Department.  Reroute standpipe piping to fit new walls.  Run above ceiling.

3 PART 3 EXECUTION


.1

EXAMINATION



A.
Verify wall openings under provisions of Section 01039. 



B.
Verify rough openings for cabinet are correctly sized and located.


.2

INSTALLATION



A.
Install in accordance with manufacturer's instructions.



B.
Secure rigidly in place.



C.
Place extinguishers in cabinets.


END OF SECTION
PAGE  
Error! Main Document Only.
Section 10522 Page 1 of 3      

