

SECTION 15510PRIVATE 


HYDRONIC PIPING

1 PART 1   GENERAL


.1

WORK INCLUDED



A.
Pipe and pipe fittings.



B.
Valves.



C.
Heating/Chilled water piping system.




.2

seq level2 \h \r0 

RELATED WORK



A.
Section 09900 ‑ Painting.



B.
Section 15060 ‑ Pipe and Pipe Fittings: Piping specialties.



C.
Section 15121 ‑ Expansion Compensation.



D.
Section 15140 ‑ Supports and Anchors.



E.
Section 15190 ‑ Mechanical Identification.



F.
Section 15242 ‑ Vibration Isolation.



G.
Section 15260 ‑ Piping Insulation.



H.
Section 15515 ‑ Hydronic Specialties.


.3

seq level2 \h \r0 

REFERENCES



A.
ANSI/ASME ‑ Boiler and Pressure Vessel Code.



B.
ANSI/ASME Sec 9 ‑ Welding and Brazing Qualifications.



C.
ANSI/ASME B16.3 ‑ Malleable Iron Threaded Fittings Class 150 and 300.



D.
ANSI/ASME B31.9 ‑ Building Services Piping.



E.
ANSI/ASTM D2466 ‑ Poly Vinyl Chloride PVC Plastic Pipe Fittings, Schedule 40.



F.
ANSI/AWS A5.8 ‑ Brazing Filler Metal.



G.
ANSI/AWS D1.1 ‑ Structural Welding Code.



H.
ANSI/AWWA C105 ‑ Polyethylene Encasement for Ductile Iron Piping for Water and Other Liquids.



I.
ANSI/AWWA C110 ‑ Ductile ‑ Iron and Gray ‑ Iron Fittings 3 in. through 48 in., for Water and Other Liquids.



J.
ANSI/AWWA C111 ‑ Rubber‑Gasket Joints for Ductile Iron and Gray‑Iron Pressure Pipe and Fittings.



K.
ANSI/AWWA C151 ‑ Ductile‑Iron Pipe, Centrifugally Cast in Metal Molds or Sand‑Lined Molds, for Water or Other Liquids.



L.
ASTM A53 ‑ Pipe, Steel, Black and Hot‑Dipped Zinc Coated, Welded and Seamless.



M.
ASTM A120 ‑ Pipe, Steel, Black and Hot‑Dipped Zinc Coated (Galvanized), Welded and Seamless, for Ordinary Uses.



N.
ASTM A234 ‑ Pipe Fittings of Wrought Carbon Steel and Alloy Steel for Moderate and Elevated Temperatures.



O.
ASTM B32 ‑ Solder Metal.



P.
ASTM B88 ‑ Seamless Copper Water Tube.



Q.
ASTM D1785 ‑ Poly (Vinyl Chloride) (PVC) Plastic Pipe, Schedules 40, 80, and 120.



R.
ASTM D2235 ‑ Solvent Cement for Acrylonitrile‑Butadiene-Styrene (ABS) Plastic Pipe and Fittings.



S.
ASTM D2241 ‑ Poly (Vinyl Chloride) (PVC) Plastic Pipe (SDR‑PR).



T.
ASTM D2310 ‑ Machine‑Made Reinforced Thermosetting Resin Pipe.



U.
ASTM D2466 ‑ Socket‑Type PVC Plastic Type Fittings, Schedule 40.



V.
ASTM D2467 ‑ Socket‑Type PVC Plastic Type Fittings, Schedule 80.



W.
ASTM D2680 ‑ Acrylonitrile‑Butadiene‑Styrene (ABS) 




Composite‑Sewer Piping.



X.
ASTM D2683 ‑ Socket‑Type Polyethylene Fittings for Outside Diameter‑Controlled Polyethylene Pipe and Tubing.



.4
seq level2 \h \r0 
REGULATORY REQUIREMENTS



A.
Conform to ANSI/ASME B31.9.


.5

seq level2 \h \r0 

QUALITY ASSURANCE



A.
Valves: Manufacturer's name and pressure rating marked on valve body.



B.
Welding Materials and Procedures: Conform to ANSI/ASME SEC 9 and applicable state labor regulations.



C.
Welders Certification: In accordance with ANSI/ASME SEC 9.


.6
seq level2 \h \r0 
SUBMITTALS



A.
Submit product data under provisions of Section 01300.



B.
Include data on pipe materials, pipe fittings, valves, and accessories.



C.
Include welders certification of compliance with ANSI/ASME SEC 9.


.6

seq level2 \h \r0 

DELIVERY, STORAGE, AND HANDLING



A.
Deliver products to site under provisions of Section 01600.



B.
Store and protect products under provisions of Section 01600. 



C.
Deliver and store valves in shipping containers with labelling in place.

2

seq level1 \h \r0 

seq level2 \h \r0  PART 2   PRODUCTS


.1seq level2 \h \r0 

seq level3 \h \r0 

Heating/CHILLED WATER PIPING, ABOVE GRADE



A.
Steel Pipe: ASTM A53 or A120, Schedule 40, wall for sizes        

12 inch (300 mm) and over,] black.




1.
Fittings: ANSI/ASTM B16.3, malleable iron or ASTM A234, forged steel welding type.




2.
Joints: Screwed for pipe 2 inch (50 mm) and under; ANSI/AWS D1.1 welded for pipe over 2 inch (50 mm).



B.seq level3 \h \r0 
Copper Tubing: ASTM B88, Type  K, hard drawn.




1.
Fittings: ANSI/ASME B16.23 cast brass or ANSI/ASME B16.29 solder wrought copper.




2.
Joints: ASTM B32, Solder, Grade 95TA


C.seq level3 \h \r0 
PVC Pipe: ASTM D1785, and Schedule 80 for sizes 8 inch (200 mm) and larger, or ASTM D2241, SDR 21 or 26.




1.
Fittings: ASTM D2466 or D2467, PVC.




2.
Joints: ASTM D2855, solvent weld.



D.seq level3 \h \r0 
RTR Pipe: ASTM D2310, fiberglass reinforced thermosetting resin plastic.





Not Used


.2seq level2 \h \r0 

seq level3 \h \r0 

EQUIPMENT DRAINS AND OVERFLOWS



A.
Steel Pipe: ASTM A53 or A120, Schedule 40 galvanized.




1.
Fittings: Galvanized cast iron, or ANSI/ASTM B16.3 malleable iron.




2.
Joints: Screwed, or grooved mechanical couplings.



B.seq level3 \h \r0 
Copper Tubing: ASTM B88, Type  K, hard drawn.




1.
Fittings: ANSI/ASME B16.23 cast brass, or ANSI/ASME B16.29 solder wrought copper.




2.
Joints: ASTM B32, solder, Grade 95TA.



C.seq level3 \h \r0 
PVC Pipe: ASTM D1785, [and Schedule 80 for sizes 8 inch (200 mm) and larger,] or ASTM D2241, SDR 21 or 26.




1.
Fittings: ASTM D2466 or D2467, PVC.




2.
Joints: ASTM D2855, solvent weld.



D.seq level3 \h \r0 
ABS Pipe: ASTM D2680 or D2751.




1.
Fittings: ASTM D2751.




2.
Joints: ASTM D2235, solvent weld.


.3
seq level2 \h \r0 

seq level3 \h \r0 
FLANGES, UNIONS, AND COUPLINGS



A.
Pipe Size 2 Inches (50 mm) and Under: 150 psig (1 034 kPa) malleable iron unions for threaded ferrous piping; bronze unions for copper pipe, soldered joints.



B.
Pipe Size Over 2 Inches (50 mm): 150 psig (1 034 kPa) forged steel slip‑on flanges for ferrous piping; bronze flanges for copper piping; 1/16 inch (1.6 mm) thick preformed neoprene bonded to asbestos.



C.
Grooved and Shouldered Pipe End Couplings: Malleable iron housing clamps to engage and lock, designed to permit some angular deflection, contraction, and expansion; C‑shape elastomer composition sealing gasket for operating temperature range from ‑30 degrees F (‑34 degrees C) to 230 degrees F (110 degrees C); steel bolts, nuts, and washers; galvanized couplings for galvanized pipe.


.4 seq level2 \h \r0 
GATE VALVES



A.
Up to 2 Inches (50 mm): Bronze body, bronze trim, non-rising stem, hand-wheel, inside screw, single wedge or disc, threaded ends.



B.
Over 2 Inches (50 mm): Iron body, bronze trim, non‑rising stem, hand-wheel, OS&Y, single wedge, flanged ends.


.5 seq level2 \h \r0 
GLOBE VALVES



A.
Up to 2 Inches (50 mm): Bronze body, bronze trim, rising stem and hand-wheel, inside screw, renewable composition disc, ends, with back seating capacity. 



B.
Over 2 Inches (50 mm): Iron body, bronze trim, rising stem, hand-wheel, OS&Y, plug‑type disc, flanged ends, renewable seat and disc.



.6 seq level2 \h \r0 
BALL VALVES



A.
Up to 2 Inches (50 mm): Bronze one piece body, stainless steel ball, Teflon seats and stuffing box ring, lever handle, and balancing stops.



B.
Over 2 Inches (50 mm): Cast steel body, chrome plated steel ball, Teflon seat and stuffing box seals, lever handle.

.7 seq level2 \h \r0 
BUTTERFLY VALVES



A.
Iron body, bronze disc, resilient replaceable seat for service to 250 degrees F (121 degrees C), wafer or lug ends, extended neck, 10 position lever handle.

3 PART 3   EXECUTION 


.1
seq level2 \h \r0 
INSTALLATION



A.
Route piping in orderly manner, plumb and parallel to building structure, and maintain gradient.



B.
Install piping to conserve building space, and not interfere with use of space and other work.



C.
Group piping whenever practical at common elevations.



D.
Install piping to allow for expansion and contraction without stressing pipe, joints, or connected equipment. Refer to Section 15121.



E.
Provide clearance for installation of insulation, and access to valves and fittings.



F.
Provide access where valves and fittings are not exposed. Coordinate size and location of access doors with Section 08305.



G.
Slope piping and arrange systems to drain at low points. Use eccentric reducers to maintain top of pipe level.



H.
Where pipe support members are welded to structural building framing, scrape, brush clean, and apply one coat of zinc rich primer to welding.



I.
Prepare pipe, fittings, supports, and accessories for finish painting.  Refer to Section 09900.



J.
Install valves with stems upright or horizontal, not inverted.


.2
seq level2 \h \r0 
APPLICATION



A.
Use grooved mechanical couplings and fasteners only in accessible locations.



B.
Install unions downstream of valves and at equipment or apparatus connections.



C.
Install brass male adapters each side of valves in copper piped system.  Sweat solder adapters to pipe.



D.
Install gate valves for shut‑off and to isolate equipment, part of systems, or vertical risers.



E.
Install butterfly valves for throttling, bypass, or manual flow control services.



F.
Provide spring loaded check valves on discharge of condenser water pumps.



G.
Use plug cocks for throttling service.  Use non‑lubricated plug cocks only when shut‑off or isolating valves are also provided.



H.
Use butterfly valves in heating water systems in heating, chilled and condenser water systems interchangeably with gate and globe valves.



I.
Use only butterfly valves in chilled and condenser water systems for throttling and isolation service.



J.
Use lug end butterfly valves to isolate equipment.



K.
Provide 3/4-inch ball drain valves at main shut‑off valves, low points of piping, bases of vertical risers, and at equipment.  Pipe to nearest drain.

END OF SECTION
PAGE  
Section 15510 Page 2 of 6

