## Pollutant Loads
Site Conditions |  | Annual Rainfall in inches
|  | 60 | inches
Existing Conditions
Green Space | 24255 | s.f. | 0.55682 | Acres |  | 100 | %
Proposed Land Cover
Roofs | 7678 | s.f. | 0.17626 | Acres |  | 31.6553 | %
Impervious Paving | 9130 | s.f. | 0.2096 | Acres |  | 37.6417 | %
Pervious Pavement | 4302 | s.f. | 0.09876 | Acres |  | 17.7898 | %
Lawns/Landscaping | 3145 | s.f. | 0.072199 | Acres |  | 12.9664 | %
Total | 24255 | s.f. | 0.55682 | Acres |  | 100.0532
Simple Method to Calculate Chemical Loads Annually
L=0.20 P Rv C A
L = Load of a pollutant in pounds per year;
P = Rainfall depth per year (inches);
Rv = Runoff coefficient, which expresses the fraction of rainfall which is converted into runoff. Rv = 0.05 + 0.009(I);
I = Site imperviousness (i.e., I = 75 if site is 75% impervious);
C = Flow-weighted mean concentration of the pollutant in urban runoff (mg/l);
A = Area of the development site (acres).
Pollutants | TSS | Total Suspended Solids |  | 75 | mg/l
| TP | Total Phosphorus |  | 0.26 | mg/l
| TN | Total Nitrogen |  | 2 | mg/l
| BOD | Biochemical oxygen demand |  | 14.1 | mg/l
Estimated Pre-Developed Pollutant Loads
| Rv | TSS (lbs/yr) | TP (lbs/yr) | TN (lbs/yr) | BOD (lbs/yr)
Lawns/Landscaping | 0.05 | 125.2841 | 0.086864 | 0.66818 | 4.7107
Estimated Post-Developed Pullutant Loads before adding BMPs
| Rv | TSS (lbs/yr) | TP (lbs/yr) | TN (lbs/yr) | BOD (lbs/yr)
Roofs | 0.3349 | 53.127 | 0.18417 | 1.4167 | 9.9879
Impervious Paving | 0.38878 | 73.3372 | 0.25424 | 1.9557 | 13.7874
Pervious Pavement | 0.21011 | 18.6753 | 0.064741 | 0.49801 | 3.511
Lawns/Landscaping | 0.05 | 3.249 | 0.011263 | 0.086639 | 0.61081
| Totals : | 148.3884 | 0.51441 | 3.957 | 27.897
Estimated Post-Developed Pullutant Loads with BMPs
| Rv | TSS (lbs/yr) | TP (lbs/yr) | TN (lbs/yr) | BOD (lbs/yr)
Roofs | 0.3349 | 10.6254 | 0.073669 | 0.70836
Impervious Paving | 0.38878 | 14.6674 | 0.10169 | 0.97783
Pervious Pavement | 0.21011 | 3.7351 | 0.025896 | 0.249
Lawns/Landscaping | 0.05 | 0.97469 | 0.0078842 | 0.060647
| Totals : | 30.0026 | 0.20914 | 1.9958 | 0
L = 0.226 * R * C * A
L = Annual load (lbs)
R = Annual runoff (inches)
C = Pollutant concentration (mg/l)
A = Area (acres)
0.226 = Unit conversion factor
Pollutants | Total Suspended Solids |  | TSS | 75 | mg/l
| Total Phosphorus |  | TP | 0.26 | mg/l
| Total Nitrogen |  | TN | 2 | mg/l
| Biochemical oxygen demand |  | BOD | 14.1 | mg/l
Estimated Pre-Developed Pollutant Loads
| TSS (lbs/yr) | TP (lbs/yr) | TN (lbs/yr) | BOD (lbs/yr)
Lawns/Landscaping | 566.2841 | 0.19631 | 1.5101 | 10.6461
Estimated Post-Developed Pullutant Loads w/o BMPs
| TSS (lbs/yr) | TP (lbs/yr) | TN (lbs/yr) | BOD (lbs/yr)
Roofs | 179.2591 | 0.62143 | 4.7802 | 33.7007
Impervious Paving | 213.1591 | 0.73895 | 5.6842 | 40.0739
Pervious Pavement | 100.4393 | 0.34819 | 2.6784 | 18.8826
Lawns/Landscaping | 73.4267 | 0.25455 | 1.958 | 13.8042
Totals | 566.2841 | 1.9631 | 15.1009 | 106.4614

## 10 Year event 1.25" Cap W-G (2)
PROJECT: | Josephine Condos
STORMWATER RUN-OFF CALCULATIONS
Formulas used:
[1] RATIONAL METHOD: Q=Aci
where: Q= | Peak discharge of watershed in cubic feet per second (cfs) due to maximum storm assumed.
A= | Area of watershed in acres.
c= | Coefficient of run-off [2].
i= | Intensity of rainfall in inches per hour based on concentration time. [3]
[4] TC=
where: TC= | Time of concentration= time required for rain falling at most remote point to reach discharge point.
c= | Site run-off coefficient based on conditions shown.
s= | Percent slope of overland flow.
PRIOR TO DEVELOPMENT
10 Year Frequency
Q1 = Aci
Watertight Surfaces |  |  | 0 | sqft | 0 | Acres
c(1) = | 0.9
Brick Pavers |  |  | 0 | sqft | 0 | Acres
c(2) = | 0.25
Green Space |  |  | 24255 | sqft | 0.55682 | Acres
c(3) = | 0.15
Summary |  |  | 24255 | sqft | 0.557 | Acres
c = | 0.15
Duration (D) = Time of concentration (TC)
where | L = | 191 | run-off length ft |  | Elev diff = | 1
| c = | 0.15 | run-off coef
| S = | 0.52356 | percent slope
therefore | TC = D = | 20.1248 | minutes
Expected rainfall intensity | i = | 5.99 | in/hr
Q1 = | 0.50046 | cfs
POST DEVELOPMENT
10 Year Frequency
Q2 = Aci
Watertight Surfaces |  |  | 16808 | sqft | 0.38586 | Acres
c(1) = | 0.9
Brick Pavers |  |  | 4302 | sqft | 0.09876 | Acres
c(2) = | 0.3
Green Space |  |  | 3145 | sqft | 0.072199 | Acres
c(3) = | 0.15
Summary |  |  | 24255 | sqft | 0.557 | Acres
c = | 0.69633
Duration (D) = Time of concentration (TC)
where | L = | 170 | run-off length ft |  | Elev diff = | 1
| c = | 0.69633 | run-off coef
| S = | 0.58824 | percent slope
therefore | TC = D = | 6.6122 | minutes
Expected rainfall intensity | i = | 7.67 | in/hr
Q2 = | 2.9749 | cfs
LANDSCAPE INFILTRATION
Lanscaping | Area | Soil Type | Cubic Feet Infiltration / HR |  | Gal Infiltraion / Hr
Turf | 776 s.f. | D | 17.46 cu ft / hr |  | 131 gph
Planting Area | 3,445 s.f. | A | 292.82 cu ft / hr |  | 2,190 gph
|  | Total | 310.28 cf/hr (0.0862 cfs) |  | 2,321 gph
CAPTURE REQUIREMENTS
Capture the 1st 1.25" of rainfall of a 10 year storm over a 24-hr period
Storage = 1.25"/12 x sqft of Watertight Surface |  |  | 1750.8333 | cuft or | 13096.2333 | Gallons
Draining a volume of this size using the Pre-Devlopement Run-Off Rate of 0.262 cfs would take =
1750.8 cuft / 0.262 cfs = 6682 seconds or 111.4 minutes or 1.86 hrs
Since the Landscaping Infiltration can handle 310.28 cu ft/hr the storage requirement can be reduced
by this amount: | 1750.8 - (310.28 cu ft / hr x 1.86 hrs) = 1173.7 cu ft of storage
CAPTURE REQUIREMENTS
Storage = 1.25"/12 x sqft of Watertight Surface |  |  | 1173.7 | cuft or | 8779.276 | Gallons
Storage using an Arch Conc Pipe = Equiv 42" Round Pipe with an area |  |  |  | 8.8 | Full Flow Area s.f.
Arch Pipe Length Required with 100% Storage Capacity = |  |  |  | 133.375
CALCULATE THE SIZE ORIFICE TO RESTRICT FLOW
[5] A=
where: A= | Discharge Area required
g= | Acceleration of gravity
c= | Discharge coefficient
h= | Hydraulic head
Q= | Flow volume from run-off
Q = | 0.50046 | cfs | h = | 1 | feet
c = | 0.62 | coefficient | A = | 0.10065 | sqft
g = | 32.16 | ft/sec/sec
| REQUIRED SIZE ORIFICE = |  | 4.2958 | inch inside diameter
References:
1. Chen, W.F. The Civil Engineering Handbook. 1995. Eq.# 31.1, pg. 1036
2. Seelye, Elwyn E. Data Book for Civil Engineers. Vol.1 1960. Tbl. B, pg. 18-02
3. Seelye, Elwyn E. Data Book for Civil Engineers. Vol.1 1960. Fig.B, pg. 18-01
4. Chen, W.F. The Civil Engineering Handbook. 1995. Tbl. 31.2 Regan Equation (n=0.013)
5. Chen, W.F. The Civil Engineering Handbook. 1995. Eq.# 28.32, pg. 969

## 10 Year event 1.25" Cap W-Green
PROJECT: | Josephine St. Condo's
STORMWATER RUN-OFF CALCULATIONS
Formulas used:
[1] RATIONAL METHOD: Q=Aci
where: Q= | Peak discharge of watershed in cubic feet per second (cfs) due to maximum storm assumed.
A= | Area of watershed in acres.
c= | Coefficient of run-off [2].
i= | Intensity of rainfall in inches per hour based on concentration time. [3]
[4] TC=
where: TC= | Time of concentration= time required for rain falling at most remote point to reach discharge point.
c= | Site run-off coefficient based on conditions shown.
s= | Percent slope of overland flow.
PRIOR TO DEVELOPMENT
10 Year Frequency
Q1 = Aci
Watertight Surfaces |  |  | 0 | sqft | 0 | Acres
c(1) = | 0.9
Brick Pavers |  |  | 0 | sqft | 0 | Acres
c(2) = | 0.25
Green Space |  |  | 24255 | sqft | 0.55682 | Acres
c(3) = | 0.15
Summary |  |  | 24255 | sqft | 0.55682 | Acres
c = | 0.15
Duration (D) = Time of concentration (TC)
where | L = | 191 | run-off length ft |  | Elev diff = | 1
| c = | 0.15 | run-off coef
| S = | 0.52356 | percent slope
therefore | TC = D = | 20.1248 | minutes
Expected rainfall intensity | i = | 5.99 | in/hr
Q1 = | 0.5003 | cfs
POST DEVELOPMENT
10 Year Frequency
Q2 = Aci
Watertight Surfaces |  |  | 16808 | sqft | 0.38586 | Acres
c(1) = | 0.9
Brick Pavers |  |  | 4302 | sqft | 0.09876 | Acres
c(2) = | 0.3
Green Space |  |  | 3145 | sqft | 0.072199 | Acres
c(3) = | 0.15
Summary |  |  | 24255 | sqft | 0.55682 | Acres
c = | 0.69633
Duration (D) = Time of concentration (TC)
where | L = | 170 | run-off length ft |  | Elev diff = | 1
| c = | 0.69633 | run-off coef
| S = | 0.58824 | percent slope
therefore | TC = D = | 6.6122 | minutes
Expected rainfall intensity | i = | 7.67 | in/hr
Q2 = | 2.9739 | cfs
LANDSCAPE INFILTRATION
Lanscaping | Area | Soil Type | Cubic Feet Infiltration / HR |  | Gal Infiltraion / Hr
Turf | 776 s.f. | D | 17.46 cu ft / hr |  | 131 gph
Planting Area | 3,445 s.f. | A | 292.82 cu ft / hr |  | 2,190 gph
|  | Total | 310.28 cf/hr (0.0862 cfs) |  | 2,321 gph
CAPTURE REQUIREMENTS
Capture the 1st 1.25" of rainfall of a 10 year storm over a 24-hr period
Storage = 1.25"/12 x sqft of Watertight Surface |  |  | 1750.8333 | cuft or | 13096.2333 | Gallons
Draining a volume of this size using the Pre-Devlopement Run-Off Rate of 0.262 cfs would take =
1750.8 cuft / 0.262 cfs = 6682 seconds or 111.4 minutes or 1.86 hrs
Since the Landscaping Infiltration can handle 310.28 cu ft/hr the storage requirement can be reduced
by this amount: | 1750.8 - (310.28 cu ft / hr x 1.86 hrs) = 1173.7 cu ft of storage
CAPTURE REQUIREMENTS
New Storage Volume = |  |  | 1173.7 | cuft or | 8779.276 | Gallons
Dimensions of Rectangular Storage = |  |  | WIDTH | 3.5 | feet
|  |  | LENGTH | 140 | feet
|  |  | DEPTH | 2.3953 | feet
Storage = 1.25"/12 x sqft of Watertight Surface |  |  | 1173.7 | cuft or | 8779.276 | Gallons
Storage using an Arch Conc Pipe = Equiv 48" Round Pipe with an area |  |  |  | 11.4 | Full Flow Area s.f.
Arch Pipe Length Required with 100% Storage Capacity = |  |  |  | 102.9561
CALCULATE THE SIZE ORIFICE TO RESTRICT FLOW
[5] A=
where: A= | Discharge Area required
g= | Acceleration of gravity
c= | Discharge coefficient
h= | Hydraulic head
Q= | Flow volume from run-off
Q = | 0.5003 | cfs | h = | 1 | feet
c = | 0.62 | coefficient | A = | 0.10062 | sqft
g = | 32.16 | ft/sec/sec
| REQUIRED SIZE ORIFICE = |  | 4.2951 | inch inside diameter
References:
1. Chen, W.F. The Civil Engineering Handbook. 1995. Eq.# 31.1, pg. 1036
2. Seelye, Elwyn E. Data Book for Civil Engineers. Vol.1 1960. Tbl. B, pg. 18-02
3. Seelye, Elwyn E. Data Book for Civil Engineers. Vol.1 1960. Fig.B, pg. 18-01
4. Chen, W.F. The Civil Engineering Handbook. 1995. Tbl. 31.2 Regan Equation (n=0.013)
5. Chen, W.F. The Civil Engineering Handbook. 1995. Eq.# 28.32, pg. 969

## 10 Year event 1.25" Capture
PROJECT: | Josephine St. Condo's
STORMWATER RUN-OFF CALCULATIONS
Formulas used:
[1] RATIONAL METHOD: Q=Aci
where: Q= | Peak discharge of watershed in cubic feet per second (cfs) due to maximum storm assumed.
A= | Area of watershed in acres.
c= | Coefficient of run-off [2].
i= | Intensity of rainfall in inches per hour based on concentration time. [3]
[4] TC=
where: TC= | Time of concentration= time required for rain falling at most remote point to reach discharge point.
c= | Site run-off coefficient based on conditions shown.
s= | Percent slope of overland flow.
PRIOR TO DEVELOPMENT
10 Year Frequency
Q1 = Aci
Watertight Surfaces |  |  | 0 | sqft | 0 | Acres
c(1) = | 0.9
Brick Pavers |  |  | 0 | sqft | 0 | Acres
c(2) = | 0.25
Green Space |  |  | 24255 | sqft | 0.55682 | Acres
c(3) = | 0.15
Summary |  |  | 24255 | sqft | 0.55682 | Acres
c = | 0.15
Duration (D) = Time of concentration (TC)
where | L = | 191 | run-off length ft |  | Elev diff = | 1
| c = | 0.15 | run-off coef
| S = | 0.52356 | percent slope
therefore | TC = D = | 20.1248 | minutes
Expected rainfall intensity | i = | 3.14 | in/hr
Q1 = | 0.26226 | cfs
POST DEVELOPMENT
10 Year Frequency
Q2 = Aci
Watertight Surfaces |  |  | 16808 | sqft | 0.38586 | Acres
c(1) = | 0.9
Brick Pavers |  |  | 4302 | sqft | 0.09876 | Acres
c(2) = | 0.3
Green Space |  |  | 3145 | sqft | 0.072199 | Acres
c(3) = | 0.15
Summary |  |  | 24255 | sqft | 0.55682 | Acres
c = | 0.69633
Duration (D) = Time of concentration (TC)
where | L = | 170 | run-off length ft |  | Elev diff = | 1.2
| c = | 0.69633 | run-off coef
| S = | 0.70588 | percent slope
therefore | TC = D = | 7.2433 | minutes
Expected rainfall intensity | i = | 3.14 | in/hr
Q2 = | 1.2175 | cfs
CAPTURE REQUIREMENTS
Capture the 1st 1.25" of rainfall |  | 1.25 | " OF A 10 YEAR STORM OVER 24-HR PERIOD
Storage = 1.25"/12 x sqft of Watertight Surface |  |  | 1750.8333 | cuft or | 13096.2333 | Gallons
Dimensions of Storage = |  |  | WIDTH | 3.5 | feet
|  |  | LENGTH | 140 | feet
|  |  | DEPTH | 3.5731 | feet
Storage = 1.25"/12 x sqft of Watertight Surface |  |  | 1750.8333 | cuft or | 13096.2333 | Gallons
Dimensions of Storage = Arch Conc Pipe = Equiv 48" Round Pipe |  |  |  | 11.4 | Full Flow Area s.f.
Arch Pipe Length Required with 100% Storage Capacity = |  |  |  | 153.5819
References:
1. Chen, W.F. The Civil Engineering Handbook. 1995. Eq.# 31.1, pg. 1036
2. Seelye, Elwyn E. Data Book for Civil Engineers. Vol.1 1960. Tbl. B, pg. 18-02
3. Seelye, Elwyn E. Data Book for Civil Engineers. Vol.1 1960. Fig.B, pg. 18-01
4. Chen, W.F. The Civil Engineering Handbook. 1995. Tbl. 31.2 Regan Equation (n=0.013)
5. Chen, W.F. The Civil Engineering Handbook. 1995. Eq.# 28.32, pg. 969

## 10 Year event 10% Reduction24hr
PROJECT: | Josephine St. Condo's
STORMWATER RUN-OFF CALCULATIONS
Formulas used:
[1] RATIONAL METHOD: Q=Aci
where: Q= | Peak discharge of watershed in cubic feet per second (cfs) due to maximum storm assumed.
A= | Area of watershed in acres.
c= | Coefficient of run-off [2].
i= | Intensity of rainfall in inches per hour based on concentration time. [3]
[4] TC=
where: TC= | Time of concentration= time required for rain falling at most remote point to reach discharge point.
c= | Site run-off coefficient based on conditions shown.
s= | Percent slope of overland flow.
PRIOR TO DEVELOPMENT
10 Year Frequency
Q1 = Aci
Watertight Surfaces |  |  | 0 | sqft | 0 | Acres
c(1) = | 0.9
Gravel Surface |  |  | 0 | sqft | 0 | Acres
c(2) = | 0.25
Green Space |  |  | 24255 | sqft | 0.55682 | Acres
c(3) = | 0.15
Summary |  |  | 24255 | sqft | 0.55682 | Acres
c = | 0.15
Duration (D) = Time of concentration (TC)
where | L = | 191 | run-off length ft |  | Elev diff = | 1
| c = | 0.15 | run-off coef
| S = | 0.52356 | percent slope
therefore | TC = D = | 20.1248 | minutes
Expected rainfall intensity | i = | 3.14 | in/hr
Q1 = | 0.26226 | cfs | 10% reduction |  | 0.026226 | cfs
POST DEVELOPMENT
10 Year Frequency
Q2 = Aci
Watertight Surfaces |  |  | 21110 | sqft | 0.48462 | Acres
c(1) = | 0.9
Gravel Surface |  |  | 0 | sqft | 0 | Acres
c(2) = | 0.25
Green Space |  |  | 3145 | sqft | 0.072199 | Acres
c(3) = | 0.15
Summary |  |  | 24255 | sqft | 0.55682 | Acres
c = | 0.80275
Duration (D) = Time of concentration (TC)
where | L = | 170 | run-off length ft |  | Elev diff = | 1.2
| c = | 0.80275 | run-off coef
| S = | 0.70588 | percent slope
therefore | TC = D = | 6.5525 | minutes
Expected rainfall intensity | i = | 3.14 | in/hr
Q2 = | 1.4035 | cfs
CAPTURE REQUIREMENTS
CAPTURE THE 1ST 1.25" |  | 1.25 | " OF A 10 YEAR STORM OVER 24-HR PERIOD
CAPTURE STORAGE |  | 2198.9583 | cuft or | 16448.2083 | Gallons
INFLOW FOR A 10 YEAR STORM OVER 24-HR PERIOD
Total Inflow rate = Q2 |  | 1.4035 | cfs
CAPTURE & DETENTION REQUIREMENTS FOR A 10 YEAR STORM OVER 24-HR PERIOD
Outflow rate = Q1 - 10% |  | 0.23604 | cfs
Storage rate = Inflow rate - outflow rate |  | 1.1675 | cfs
Capture and 24 hr Detention Storage |  | 100872.3183 | cuft or | 754524.9412 | Gallons
| Dimensions of Storage = |  | WIDTH | 42 | feet
|  |  | LENGTH | 156 | feet
|  |  | DEPTH | 15.3957 | feet
[5] A=
where: A= | Discharge Area required
g= | Acceleration of gravity
c= | Discharge coefficient
h= | Hydraulic head
Q= | Flow volume from run-off
Pipe Servicing Site Drainage
Outflow Q = | 0.23604 | cfs | h = | 0.25 | feet
c = | 0.62 | coefficient | A = | 0.094938 | sqft
g = | 32.16 | ft/sec/sec
REQUIRED CONDUIT = |  |  | 4.1721 | inch inside diameter
References:
1. Chen, W.F. The Civil Engineering Handbook. 1995. Eq.# 31.1, pg. 1036
2. Seelye, Elwyn E. Data Book for Civil Engineers. Vol.1 1960. Tbl. B, pg. 18-02
3. Seelye, Elwyn E. Data Book for Civil Engineers. Vol.1 1960. Fig.B, pg. 18-01
4. Chen, W.F. The Civil Engineering Handbook. 1995. Tbl. 31.2 Regan Equation (n=0.013)
5. Chen, W.F. The Civil Engineering Handbook. 1995. Eq.# 28.32, pg. 969

## 10 Year event NO Reduction24Hr
PROJECT: | Josephine St. Condo's
STORMWATER RUN-OFF CALCULATIONS
Formulas used:
[1] RATIONAL METHOD: Q=Aci
where: Q= | Peak discharge of watershed in cubic feet per second (cfs) due to maximum storm assumed.
A= | Area of watershed in acres.
c= | Coefficient of run-off [2].
i= | Intensity of rainfall in inches per hour based on concentration time. [3]
[4] TC=
where: TC= | Time of concentration= time required for rain falling at most remote point to reach discharge point.
c= | Site run-off coefficient based on conditions shown.
s= | Percent slope of overland flow.
PRIOR TO DEVELOPMENT
10 Year Frequency
Q1 = Aci
Watertight Surfaces |  |  | 0 | sqft | 0 | Acres
c(1) = | 0.9
Gravel Surface |  |  | 0 | sqft | 0 | Acres
c(2) = | 0.25
Green Space |  |  | 24255 | sqft | 0.55682 | Acres
c(3) = | 0.15
Summary |  |  | 24255 | sqft | 0.55682 | Acres
c = | 0.15
Duration (D) = Time of concentration (TC)
where | L = | 191 | run-off length ft |  | Elev diff = | 1
| c = | 0.15 | run-off coef
| S = | 0.52356 | percent slope
therefore | TC = D = | 20.1248 | minutes
Expected rainfall intensity | i = | 3.14 | in/hr
Q1 = | 0.26226 | cfs
POST DEVELOPMENT
10 Year Frequency
Q2 = Aci
Watertight Surfaces |  |  | 21110 | sqft | 0.48462 | Acres
c(1) = | 0.9
Gravel Surface |  |  | 0 | sqft | 0 | Acres
c(2) = | 0.25
Green Space |  |  | 3145 | sqft | 0.072199 | Acres
c(3) = | 0.15
Summary |  |  | 24255 | sqft | 0.55682 | Acres
c = | 0.80275
Duration (D) = Time of concentration (TC)
where | L = | 170 | run-off length ft |  | Elev diff = | 1.2
| c = | 0.80275 | run-off coef
| S = | 0.70588 | percent slope
therefore | TC = D = | 6.5525 | minutes
Expected rainfall intensity | i = | 3.14 | in/hr
Q2 = | 1.4035 | cfs
CAPTURE REQUIREMENTS
CAPTURE THE 1ST 1.25" |  | 1.25 | " OF A 10 YEAR STORM OVER 24-HR PERIOD
CAPTURE STORAGE |  | 2198.9583 | cuft or | 16448.2083 | Gallons
INFLOW FOR A 10 YEAR STORM OVER 24-HR PERIOD
Total Inflow rate = Q2 |  | 1.4035 | cfs
CAPTURE & DETENTION REQUIREMENTS FOR A 10 YEAR STORM OVER 24-HR PERIOD
Outflow rate = Q1 |  | 1.4035 | cfs
Storage rate = Inflow rate - outflow rate |  | 0 | cfs
Capture and 24 hr Detention Storage |  | 0 | cuft or | 0 | Gallons
| Dimensions of Storage = |  | WIDTH | 42 | feet
|  |  | LENGTH | 156 | feet
|  |  | DEPTH | 0 | feet
[5] A=
where: A= | Discharge Area required
g= | Acceleration of gravity
c= | Discharge coefficient
h= | Hydraulic head
Q= | Flow volume from run-off
Pipe Servicing Site Drainage
Outflow Q = | 1.4035 | cfs | h = | 0.25 | feet
c = | 0.62 | coefficient | A = | 0.56453 | sqft
g = | 32.16 | ft/sec/sec
REQUIRED CONDUIT = |  |  | 10.1738 | inch inside diameter
References:
1. Chen, W.F. The Civil Engineering Handbook. 1995. Eq.# 31.1, pg. 1036
2. Seelye, Elwyn E. Data Book for Civil Engineers. Vol.1 1960. Tbl. B, pg. 18-02
3. Seelye, Elwyn E. Data Book for Civil Engineers. Vol.1 1960. Fig.B, pg. 18-01
4. Chen, W.F. The Civil Engineering Handbook. 1995. Tbl. 31.2 Regan Equation (n=0.013)
5. Chen, W.F. The Civil Engineering Handbook. 1995. Eq.# 28.32, pg. 969

## 25 Year event
PROJECT: | New Condo's
STORMWATER RUN-OFF CALCULATIONS
Formulas used:
[1] RATIONAL METHOD: Q=Aci
where: Q= | Peak discharge of watershed in cubic feet per second (cfs) due to maximum storm assumed.
A= | Area of watershed in acres.
c= | Coefficient of run-off [2].
i= | Intensity of rainfall in inches per hour based on concentration time. [3]
[4] TC=
where: TC= | Time of concentration= time required for rain falling at most remote point to reach discharge point.
c= | Site run-off coefficient based on conditions shown.
s= | Percent slope of overland flow.
PRIOR DEVELOPMENT
25 Year Frequency
Q1 = Aci
Watertight Surfaces |  |  | 0 | sqft = | 0 | Acres
c(1) = | 0.9
Gravel Surface |  |  | 0 | sqft = | 0 | Acres
c(2) = | 0.25
Green Space |  |  | 24255 | sqft = | 0.55682 | Acres
c(3) = | 0.15
Summary |  |  | 24255 | sqft = | 0.55682 | Acres
c = | 0.15
Duration (D) = Time of concentration (TC)
where | L = | 191 | run-off length ft |  | Elev diff = | 1
| c = | 0.15 | run-off coef
| S = | 0.52356 | percent slope
therefore | TC = D = | 20.1248 | minutes
Expected rainfall intensity | i = | 3.64 | in/hr
Q1 = | 0.30402 | cfs |  | 10% reduction | 0.030402 | cfs
POST DEVELOPMENT
25 Year Frequency
Q2 = Aci
Watertight Surfaces |  |  | 21110 | sqft = | 0.48462 | Acres
c(1) = | 0.9
Gravel Surface |  |  | 0 | sqft = | 0 | Acres
c(2) = | 0.25
Green Space |  |  | 3145 | sqft = | 0.072199 | Acres
c(3) = | 0.15
Summary |  |  | 24255 | sqft = | 0.55682 | Acres
c = | 0.80275
Duration (D) = Time of concentration (TC)
where | L = | 170 | run-off length ft |  | Elev diff = | 1.2
| c = | 0.80275 | run-off coef
| S = | 0.70588 | percent slope
therefore | TC = D = | 6.5525 | minutes
Expected rainfall intensity | i = | 3.64 | in/hr
Q2 = | 1.627 | cfs
DETENTION REQUIREMENTS
Detention required | Q2-Q1 | 1.323 | cfs
ONE HOUR DETENTION |  | 4762.8347 | cuft
DETENTION DIMENSIONS |  |  | WIDTH | 60 | feet
|  |  | LENGTH | 156 | feet
|  |  | DEPTH | 0.50885 | feet
DISCHARGE END AREA REQUIREMENTS
10 Year Frequency
[5] A=
where: A= | Discharge Area required
g= | Acceleration of gravity
c= | Discharge coefficient
h= | Hydraulic head
Q= | Flow volume from run-off
Pipe Servicing Site Drainage
Q = | 0.030402 | cfs | h = | 3 | feet
c = | 0.62 | coefficient | A = | 0.00353 | sqft
g = | 32.16 | ft/sec/sec
REQUIRED CONDUIT = |  |  | 0.8045 | inch inside diameter
References:
1. Chen, W.F. The Civil Engineering Handbook. 1995. Eq.# 31.1, pg. 1036
2. Seelye, Elwyn E. Data Book for Civil Engineers. Vol.1 1960. Tbl. B, pg. 18-02
3. Seelye, Elwyn E. Data Book for Civil Engineers. Vol.1 1960. Fig.B, pg. 18-01
4. Chen, W.F. The Civil Engineering Handbook. 1995. Tbl. 31.2 Regan Equation (n=0.013)
5. Chen, W.F. The Civil Engineering Handbook. 1995. Eq.# 28.32, pg. 969

## Intensity calcs
ENTERED DATA = | [6 empty] | The runoff coefficient C
COMPUTED DATA= | [6 empty] | The fraction of rainfall which may be expected t become runoff
DATA FROM TABLES=
Business:
Table 1 | [6 empty] | downtown areas |  |  |  | 0.70 to 0.95
Rainfall Intensity (I) | [6 empty] | neighborhood areas |  |  |  | 0.50 to 0.70
Rainfall-Intensity-Duration-Frequency for Louisiana | [6 empty] | Residential:
Duration (t) minutes | 2 year | 10 year | 25 year | 50 year | 100 year |  | single-family areas |  |  |  | 0.30 to 0.50
5 | 6.9602 | 8.0588 | 9.0537 | 9.7926 | 10.6509 |  | multi units detached |  |  |  | 0.40 to 0.60
6 | 6.6866 | 7.8098 | 8.7827 | 9.5081 | 10.339 |  | multi units attached |  |  |  | 0.60 to 0.75
7 | 6.4347 | 7.5772 | 8.5293 | 9.2418 | 10.0475 |  | residential suuburban |  |  |  | 0.25 to 0.40
8 | 6.2021 | 7.3593 | 8.2918 | 8.9918 | 9.7744 |  | Apartment dwelling areas |  |  |  | 0.50 yo 0.70
9 | 5.9866 | 7.1549 | 8.0686 | 8.7567 | 9.5178 |  | Industrial:
10 | 5.7863 | 6.9626 | 7.8586 | 8.5352 | 9.2764 |  | light areas |  |  |  | 0.50 to 0.80
11 | 5.5996 | 6.7814 | 7.6605 | 8.326 | 9.0486 |  | heavy areas |  |  |  | 0.60 to 0.90
12 | 5.4252 | 6.6102 | 7.4734 | 8.1282 | 8.8335 |  | parks, cemeteries |  |  |  | 0.10 to 0.25
13 | 5.262 | 6.4484 | 7.2962 | 7.9407 | 8.6298 |  | playgrounds |  |  |  | .020 to 0.40
14 | 5.1087 | 6.295 | 7.1282 | 7.7628 | 8.4367 |  | unimproved areas |  |  |  | 0.10 to 0.30
15 | 4.9646 | 6.1495 | 6.9686 | 7.5937 | 8.2533
16 | 4.8288 | 6.0112 | 6.817 | 7.4328 | 8.0789
17 | 4.7006 | 5.8796 | 6.6725 | 7.2795 | 7.9128
18 | 4.5794 | 5.7542 | 6.5348 | 7.1331 | 7.7544 | Prior 10y TC = | 20.12
19 | 4.4647 | 5.6346 | 6.4033 | 6.9933 | 7.6032 |  | 6.01 | - | 5.88 | 0.13
20 | 4.3558 | 5.5203 | 6.2776 | 6.8596 | 7.4586 |  |  |  | x | 0.12
21 | 4.2524 | 5.4111 | 6.1573 | 6.7316 | 7.3203 |  |  |  |  | 0.0156
22 | 4.154 | 5.3065 | 6.0422 | 6.6089 | 7.1877 |  | Expected rainfall intensity @ TC i = |  |  | 5.99 | in/hr
23 | 4.0604 | 5.2063 | 5.9317 | 6.4911 | 7.0606
24 | 3.9711 | 5.1101 | 5.8257 | 6.3781 | 6.9386
25 | 3.8858 | 5.0178 | 5.7239 | 6.2694 | 6.8214 | Post 10y TC = | 6.61
26 | 3.8043 | 4.9291 | 5.626 | 6.1648 | 6.7086 |  | 7.81 | - | 7.58 | 0.23
27 | 3.7263 | 4.8438 | 5.5318 | 6.0642 | 6.6001 |  |  |  | x | 0.61
28 | 3.6517 | 4.7617 | 5.4411 | 5.9672 | 6.4955 |  |  |  |  | 0.1403
29 | 3.5801 | 4.6826 | 5.3536 | 5.8736 | 6.3948 |  | Expected rainfall intensity @ TC i = |  |  | 7.67 | in/hr
30 | 3.5114 | 4.6064 | 5.2693 | 5.7834 | 6.2975
31 | 3.4455 | 4.5329 | 5.1879 | 5.6962 | 6.2037
32 | 3.3821 | 4.4619 | 5.1093 | 5.612 | 6.113
33 | 3.3211 | 4.3933 | 5.0333 | 5.5305 | 6.0253
34 | 3.2624 | 4.327 | 4.9598 | 5.4517 | 5.9405
35 | 3.2059 | 4.2628 | 4.8887 | 5.3754 | 5.8584
36 | 3.1514 | 4.2008 | 4.8199 | 5.3015 | 5.7789
37 | 3.0988 | 4.1407 | 4.7531 | 5.2299 | 5.7018
38 | 3.048 | 4.0824 | 4.6885 | 5.1604 | 5.6271
39 | 2.999 | 4.026 | 4.6258 | 5.093 | 5.5546
40 | 2.9516 | 3.9712 | 4.5649 | 5.0276 | 5.4842
41 | 2.9057 | 3.9181 | 4.5058 | 4.964 | 5.4159
42 | 2.8613 | 3.8665 | 4.4485 | 4.9023 | 5.3495
43 | 2.8184 | 3.8164 | 4.3927 | 4.8423 | 5.285
44 | 2.7768 | 3.7677 | 4.3385 | 4.7839 | 5.2222
45 | 2.7364 | 3.7203 | 4.2857 | 4.7271 | 5.1612
46 | 2.6973 | 3.6743 | 4.2344 | 4.6718 | 5.1017
47 | 2.6593 | 3.6295 | 4.1845 | 4.618 | 5.0439
48 | 2.6225 | 3.5859 | 4.1359 | 4.5655 | 4.9875
49 | 2.5867 | 3.5434 | 4.0885 | 4.5144 | 4.9326
50 | 2.5519 | 3.502 | 4.0423 | 4.4646 | 4.879
51 | 2.5181 | 3.4617 | 3.9973 | 4.416 | 4.8268
52 | 2.4852 | 3.4224 | 3.9534 | 4.3686 | 4.7759
53 | 2.4532 | 3.384 | 3.9106 | 4.3224 | 4.7262
54 | 2.4221 | 3.3466 | 3.8688 | 4.2772 | 4.6776
55 | 2.3918 | 3.3101 | 3.828 | 4.2331 | 4.6303
56 | 2.3623 | 3.2745 | 3.7881 | 4.1901 | 4.584
57 | 2.3336 | 3.2397 | 3.7492 | 4.148 | 4.5387
58 | 2.3055 | 3.2057 | 3.7111 | 4.1068 | 4.4945
59 | 2.2782 | 3.1725 | 3.674 | 4.0666 | 4.4513
60 | 2.2516 | 3.14 | 3.6376 | 4.0273 | 4.409