## Sheet1
Potable Water System Calculations:
Assumptions:
Toilet uses 1.6 gallons per flush |  |  | 0.0035648 | ft3/s | 0.0035648 | ft3/s
3/4" Hose Bib uses 23 gpm |  |  | 0.051244 | ft3/s x 2 hose bibs | 0.10249 | ft3/s
The flush mechancism at toilet needs 20psi * 144 in2/1 ft2 = |  |  |  |  | 2880 | psf
Minimum water pressure at water main = 59.47 psi |  |  |  |  | 8566 | psf
type pipe SDR 26 with a manning roughness coefficient = |  |  |  |  | 0.012
The length of pipe used from the water meter to
[5 empty] | 250 | ft
Difference in elevation between main and the toilet mechanism = |  |  |  |  | 10 | ft
Caclulations:
Consider water usage at 1 toilet and two hose bibs simultaneously
1" Pipe Area= | 0.005454 | ft2
Q= | 0.10605 | ft3/s
V= | 19.4451 | ft/s
hf = f * L/D * v2/2g
hf = | 211.6216 | ft
p1/γ + z1 + v12/2g = p2/γ + z2 + v22/2g + hf
p2 = | 8344.3784 | psf > 2880 psf required at toilet
| 57.9471 | psi > 20 psi required at toilet
Re= VD/ν
Re= | 97342.1744 | > 10,000 turbulent flow