## Sheet1
Potable Water System Calculations:
Assumptions:
NFPA 24 - Fire Hydrants are required to be a minimum of a 6" lateral to the water main with a flow rate of 1000 GPM @ sustained 20psi. This water main shall utilize 8" main with 6" laterals
1000 gal/min * 1min/60sec * .1336gal/ft3 = |  |  |  | 2.2267 | ft3/s x 2 hydrants = |  | 4.4533 | ft3/s
8" * 1ft/12in = |  | 0.66667 | ft
20psi * 144 in2/1 ft2 = |  | 2880 | psf
8" C900 type pipe SDR 26 with a manning roughness coefficient = | [5 empty] | 0.012
Typical domestic water demand calculations are based on drought conditions @ 115 gal/capita*d @20 psi
115 gal/capita*d * 1day/86400sec * .1336gal/ft3 = |  |  |  |  | 1.778x10-4 | ft3/s*capita
Gramercy water supply to subdivision available pressure= 60psi
60psi * 144 in2/1 ft2 = |  | 8640 | psf
The longest run to a hydrant in the subdivision is from the 12" main at Central Canal to a hydrant located @ N. Montz Ave & East 7th =
[7 empty] | 1511.5 | ft
Difference in elevation between 12" main and the hydrant = | [6 empty] | -1.97 | ft
Caclulations:
Considering the entire population of the subdivision under drought conditions with only one 8" connection to the city water system is being used.
Consider water usage of 129 lots with 4 occupants per lot
| Use with 2 Fire Hydrants | [5 empty] | Use without Fire Hydrant
4.45339 ft3/s + ( 1.778x10-4 ft3/s*capita * 516 capita ) | [5 empty] | ( 1.778x10-4 ft3/s*capita * 516 capita )
Q= | 4.5451 | ft3/s |  |  |  | Q= | 0.091745 | ft3/s
V= | 13.0194 | ft/s |  |  |  | V= | 0.2628 | ft/s
hf = f * L/D * v2/2g
hf = | 71.6685 | ft |  |  |  | hf = | 0.029202 | ft
p1/γ + z1 + v12/2g = p2/γ + z2 + v22/2g + hf
p2 = | 8566.3615 | psf > 2880 psf required at hydrant |  |  |  | p2 = | 8640.6408 | psf
| 59.4886 | psi > 20 psi required at hydrant |  |  |  |  | 60.0044 | psi
Re= VD/ν
Re= | 521611.2188 | > 10,000 turbulent flow |  |  |  | Re= | 10528.9976 | > 10,000
Water Meter connection at property line
1" C900 type pipe SDR 26 with a manning roughness coefficient = | [5 empty] | 0.012
Typical domestic water demand calculations are based on drought conditions @ 115 gal/capita*d @20 psi
115 gal/capita*d * 1day/86400sec * .1336gal/ft3 = |  |  |  |  | 1.778x10-4 | ft3/s*capita
Each connection to water main for 2 pieces of property and each property has 4 people
Caclulations
1.778x10-4 ft3/s*capita * 8 capita )
Q= | 0.0014224 | ft3/s
V= | 0.2608 | ft/s
hf = f * L/D * v2/2g
hf = | 0.0045665 | ft
p1/γ + z1 + v12/2g = p2/γ + z2 + v22/2g + hf
p2 = | 8640.6654 | psf
| 60.0046 | psi
Re= VD/ν
Re= | 1306.0346 | < 2,000 laminar flow to meter(s)