SECTION 10191

CUBICLE CURTAINS

PART 1 GENERAL
1.01 SECTION INCLUDES
A. Surface mounted overhead metal curtain track and guides.
B. Curtains.

1.02 RELATED SECTIONS
A. Section 06114 - Wood Blocking and Curbing: Track supports above ceiling.
B. Section 09511 - Suspended Acoustical Ceilings: Suspended ceiling system to support track.
1.03 REFERENCES
A. ASTM E 84 - Standard Test Method for Surface Burning Characteristics of Building Materials;2001.

B. NFPA 701 - Standard Methods of Fire Tests for Flame-Resistant Textiles and Films; National Fire Protection Association; 1999.

1.04 DELIVERY, STORAGE, AND PROTECTION
	A. Accept curtain materials on site and inspect for damage.
PART 2 PRODUCTS
2.01 MANUFACTURERS
A. Cubicle Curtains:
1. A. R. Nelson Co: www.amelson.com.
2. General Cubicle Co., Inc: www.generalcubicle.com.
3. Imperial FastenerCo., Inc: www.imperialfastener.com. 4. Salsbury Industries.
5. Substitutions: See Section 01600 - Product Requirements.
2.02 TRACKS AND TRACK COMPONENTS
	A. Track: Extruded aluminum sections; one piece per cubicle track run; I-beam profile.
1. Structural Performance: Capable of supporting vertical test load of 50 lbs without visible deflection of track or damage to supports, safely supporting moving loads, and
sufficiently rigid to resist visible deflection and without permanent set.
2. Track End Stop, Tees, Y's, and Switches: To fit track section.
3. Track Bends: Minimum 12 inch radius; fabricated without deformation of track section or impeding movement of carriers.
	4. Finish on Exposed Surfaces: 6063 T-5 anodized finish.
B. Curtain Carriers: Nylon slider to accurately fit track; designed to eliminate bind when curtain is pulled; fitted to curtain to prevent accidental curtain removal; 2 carriers per foot of track
length. .
C. Wand: Plastic hollow section, attached to lead carrier, for pull-to-close action.
2.03 CURTAINS

A. All Curtain Materials:
	1. Flame spread index of 25, maximum; smoke developed index of 450, maximum; when
	tested in accordance with ASTM E 84.
2. Naturally flame resistant or flameproofed; capable of passing NFPA 701 test.
B. Curtain: Close weave cotton; anti-bacterial, self deodorizing, sanitized, and preshrunk.
C. Open Mesh Cloth: Open weave to permit air circulation; flameproof material, same color as curtain.

D. Curtain Fabric Manufacturer: Design Tex Group, 200 Varick St. NY, NY,.1 0014 - 800.221.1540
	- www.dtex.com
E. Curtain Fabrication:
	1. Manufacture curtains of one piece, sized 10 percent wider than track length. Terminate
	curtain 15 inches from floor. .
	2. Include open mesh cloth at top 24 inches of curtain for room air circulation.
	3. Curtain Heading: Triple thickness 2 inches wide, with stitched button holes for carriers 6
	inches on center, double fold bottom hem 2 inches wide with lead weights included. Lock
	stitch seams in two rows. Turn seam edges and lock stitch.

PART 3 EXECUTION
3.01 EXAMINATION
A. Verify that surfaces and supports above ceiling are ready to receive work of this Section.
3.02 INSTALLATION
A. Install curtain track to be secure, rigid, and true to ceiling line.
B. Install end cap and stop device.
C. Install curtains on carriers ensuring smooth operation.
3.03 SCHEDULES
	A. Pre-OP, Recovery Lounge, Recovery, Treatment, Patient Rooms and other designated areas:
refer to plans for location.

END OF SECTION

;: