File: STD 4-03

	No comment

File: STD4-04
 
  	16.4.2.1

	16.4.2.3.3  Splices shall be manufactured by Raychem Corporation, G&W, or 3M.

File: STD 4-05

	No comment

File: STD 4-07
	
	No comment

File: STD 4-10

	16.10.4.1 Change 
	“Conductor		#2/0 uncoated copper

	to read:

	“Conductor		uncoated copper size as noted on plans”

	16.10.4.2  This section is about multi-conductor cable.  Please delete this section.

File: STD 4-11

	16.11.2	Conduit  The specs are written around rigid aluminum conduit.  Should EMT or Galvanized steel conduit be allowed?   

File: STD 4-12

	No comment

File: STD 4-17

	16.17.3.2.1  Three Sources: Cutler-Hammer, Square D, G.E.

	Note: on section 16.17.3.5.
 	The primary section of the transformer will not include a switch or fusing.  	(The switching and 	protective devices are located in the pad mounted switchgear)  
	The primary side will be a terminal compartment.  Please replace section with:

16.17.3.5	Primary Section
		
		The high voltage primary incoming section shall be an outdoor tamper proof metal enclosure designed for bottom entry. 

Note on section 16.17:  This section is written around an industrial type transformer.  I found some information on a pad mounted transformer  in the Cutler-Hammer book which is more of a commercial type trans former.  This section is alright for now but will need some re-write.

File: STD 4-18	

This specification is written around a panelboard.  We need to re-write specs around a
 	switchboard.  I will get back to you with more details.

File: STD 4-27 
	
	16.27.1	General
	change “The 15 KV switchgear shall be metal-enclosed or metal-clad” to read  
 	“The 15 KV switchgear shall be Outdoor pad mounted”  
	
It looks like this specification is written around a metal enclosed switchgear with automatic transfer capability.  Let’s re-write this one when we get the specifications from S&C.

File: STD 4-29 LIGHTNING ARRESTERS
 
 	Rocky said that he did not want a lightning arrester.  Let’s not include this section.

File: STD 4-41

	This section is good for now, but needs work.