360R-2

ACI COMMITTEE REPORT

4.7—Inspection and site testing of slab support

4.8—Special slab-on-ground support problems

Chapter 5—Loads, p. 360R-18

5.1—Introduction

5.2—Vehicular loads

5.3—Concentrated loads

5.4—Distributed loads

5.5—Line and strip loads

5.6—Unusual loads

5.7—Construction loads

5.8—Environmental factors

5.9—Factors of safety

Chapter 6—Joints, p. 360R-22

6.1—Introduction

6.2—Load-transfer mechanisms

6.3—Sawcut contraction joints

6.4—Joint protection

6.5—Joint filling and sealing

Chapter 7—Design of unreinforced concrete slabs,

p. 360R-31

7.1—Introduction

7.2—Thickness design methods

7.3—Shear transfer at joints

7.4—Maximum joint spacing

Chapter 8—Design of slabs reinforced for

crack-width control, p. 360R-34

8.1—Introduction

8.2—Thickness design methods

8.3—Reinforcement for crack-width control only

Chapter 9—Design of shrinkage-compensating

concrete slabs, p. 360R-34

9.1—Introduction

9.2—Thickness determination

9.3—Reinforcement

9.4—Other considerations

Chapter 10—Design of post-tensioned

slabs-on-ground, p. 360R-38

10.1—Introduction

10.2—Applicable design procedures

10.3—Slabs post-tensioned for crack control

10.4—Industrial slabs with post-tensioned reinforcement

for structural support

Chapter 11—Fiber-reinforced concrete

slabs-on-ground, p. 360R-40

11.1—Introduction

11.2—Synthetic fiber reinforcement

11.3—Steel fiber reinforcement

Chapter 12—Structural slabs-on-ground

supporting building code loads, p. 360R-44

12.1—Introduction

12.2—Design considerations

Chapter 13—Design of slabs for refrigerated

facilities, p. 360R-44

13.1—Introduction

13.2—Design and specification considerations

13.3—Temperature drawdown

Chapter 14—Reducing effects of slab shrinkage

and curling, p. 360R-45

14.1—Introduction

14.2—Drying and thermal shrinkage

14.3—Curling and warping

14.4—Factors that affect shrinkage and curling

14.5—Compressive strength and shrinkage

14.6—Compressive strength and abrasion resistance

14.7—Removing restraints to shrinkage

14.8—Base and vapor retarders/barriers

14.9—Distributed reinforcement to reduce curling and

number of joints

14.10—Thickened edges to reduce curling

14.11—Relation between curing and curling

14.12—Warping stresses in relation to joint spacing

14.13—Warping stresses and deformation

14.14—Effect of eliminating sawcut contraction joints with

post-tensioning or shrinkage-compensating concrete

14.15—Summary and conclusions

Chapter 15—References, p. 360R-53

15.1—Referenced standards and reports

15.2—Cited references

Appendix 1—Design examples using Portland

Cement Association method, p. 360R-58

A1.1—Introduction

A1.2—The PCA thickness design for single-axle load

A1.3—The PCA thickness design for slab with post loading

A1.4—Other PCA design information

Appendix 2—Slab thickness design by Wire

Reinforcement Institute method, p. 360R-60

A2.1—Introduction

A2.2—The WRI thickness selection for single-axle wheel

load

A2.3—The WRI thickness selection for aisle moment due

to uniform loading

Appendix 3—Design examples using Corps of

Engineers’ charts, p. 360R-63

A3.1—Introduction

A3.2—Vehicle wheel loading

A3.3—Heavy lift truck loading

Appendix 4—Slab design using post-tensioning,

p. 360R-63

A4.1—Design example: Post-tensioning to minimize cracking

A4.2—Design example: Equivalent tensile stress design

Appendix 5—Design example using shrinkage-

compensating concrete, p. 360R-65

A5.1—Introduction

DESIGN OF SLABS-ON-GROUND

360R-3

A5.2—Example selecting the optimum amount of reinforce-

ment to maximize the compressive stress in the

concrete where the slab thickness, the joint

spacing, and prism expansion are known

Appendix 6—Design examples for steel FRC slabs-

on-ground using yield line method, p. 360R-66

A6.1—Introduction

A6.2—Assumptions and design criteria

Appendix 7—Construction document information,

p. 360R-67

A7.1—Introduction

A7.2—Example design criteria

A7.3—Typical details

Conversion factors, p. 360R-72

CHAPTER 1—INTRODUCTION

1.1—Purpose and scope

This guide presents information on the design of slabs-on-

ground. Design is the decision-making process of planning,

sizing, detailing, and developing specifications preceding

construction of slabs-on-ground. Information on other

aspects, such as materials, construction methods, placement

of concrete, and finishing techniques is included only where

needed in making design decisions.

In the context of this guide, slab-on-ground is defined as:

a slab, supported by ground, whose main purpose is to

support the applied loads by bearing on the ground. The slab

is of uniform or variable thickness and it may include stiffening

elements such as ribs or beams. The slab may be unreinforced

or reinforced with nonprestressed reinforcement, fibers, or post-

tensioned tendons. The reinforcement may be provided to limit

crack widths resulting from shrinkage and temperature

restraint and the applied loads. Post-tensioning tendons may

be provided to minimize cracking due to shrinkage and

temperature restraint, resist the applied loads, and accommodate

movements due to expansive soil volume changes.

This guide covers the design of slabs-on-ground for loads

from material stored directly on the slab, storage rack loads,

and static and dynamic loads associated with equipment and

vehicles. Other loads, such as roof loads transferred through

dual-purpose rack systems, are also mentioned.

This guide discusses soil-support systems, shrinkage and

temperature effects; cracking, curling or warping; and other

concerns affecting slab design. Although the same general

principles are applicable, this guide does not specifically

address the design of roadway pavements, airport pavements,

parking lots, or mat foundations.

1.2—Work of ACI Committee 360 and other

relevant committees

There are several ACI committees listed below that

provide relevant information concerning slabs-on-ground

design and construction or similar slab types that are not

addressed in this guide such as pavements, parking lots, or

mat foundations. These committees provide documents

where more detailed information for topics discussed in this

guide can be found.

1.2.1 ACI Committee 117 develops and reports information

on tolerances for concrete construction through liaison with

other ACI committees.

1.2.2 ACI Committee 223 develops recommendations on

the use of shrinkage-compensating concrete.

1.2.3 ACI Committee 301 develops and maintains specifi-

cations for concrete construction.

1.2.4 ACI Committee 302 develops and reports information

on materials and procedures for the construction of concrete

floors. ACI 302.1R provides guidelines and recommendations

on materials and slab construction. ACI 302.2R provides

guidelines for concrete slabs that receive moisture-sensitive

flooring materials.

1.2.5 ACI Committee 318 develops and maintains

building code requirements for structural concrete.

1.2.6 ACI Committee 325 develops and reports information

on concrete pavements.

1.2.7 ACI Committee 330 develops and reports information

on concrete parking lots and paving sites. Parking lots and

paving sites have unique considerations that are covered in

ACI 330R.

1.2.8 ACI Committee 332 develops and reports information

on concrete in residential construction.

1.2.9 ACI Committee 336 develops and reports information

on footings, mats, and drilled piers. The design procedures

for combined footings and mat foundations are given in ACI

336.2R. Mat foundations are typically more rigid and more

heavily reinforced than common slabs-on-ground.

1.2.10 ACI Committee 360 develops and reports information

on the design of slabs-on-ground, with the exception of high-

ways, parking lots, airport pavements, and mat foundations.

1.2.11 ACI Committee 544 develops and reports information

on concrete reinforced with short, discontinuous, randomly-

dispersed fibers. ACI 544.3R is a guide for specifying, propor-

tioning, and production of fiber-reinforced concrete (FRC).

1.3—Work of non-ACI organizations

Numerous contributions of slabs-on-ground design and

construction information used in this guide come from

organizations and individuals outside the American

Concrete Institute. The U.S. Army Corps of Engineers

(USACE), the National Academy of Science, and the

Department of Housing and Urban Development (HUD)

have developed guidelines for floor slab design and

construction. The Portland Cement Association (PCA), Wire

Reinforcement Institute (WRI), Concrete Reinforcing Steel

Institute (CRSI), Post-Tensioning Institute (PTI), as well as

several universities and consulting engineers have studied

slabs-on-ground and developed recommendations for their

design and construction. In addition, periodicals such as

Concrete International and Concrete Construction have

continuously disseminated information about slabs-on-ground.

1.4—Design theories for slabs-on-ground

1.4.1 Introduction—Stresses in slabs-on-ground result

from applied loads and volume changes of the soil and

concrete. The magnitude of these stresses depends on factors

such as the degree of slab continuity, subgrade strength and

360R-4

ACI COMMITTEE REPORT

uniformity, construction method, construction quality, and magnitude and position of the loads. In most cases, the effects of these factors are evaluated by making simplified analysis assumptions with respect to material properties and soil-structure interaction. The following sections briefly review some of the design theories of soil-supported concrete slabs.

1.4.2 Review of classical design theories—Design methods for slabs-on-ground are based on theories originally developed for airport and highway pavements. Westergaard developed one of the first rigorous theories of structural behavior of rigid pavement (Westergaard 1923, 1925, 1926). This theory considers a homogeneous, isotropic, and elastic slab resting on an ideal subgrade that exerts, at all points, a vertical reactive pressure proportional to slab deflection; known as a Winkler subgrade (Winkler 1867). The subgrade acts as a linear spring with a proportionality constant k with units of pressure (lb/in.2 [kPa]) per unit deformation (in. [m]). The units are commonly abbreviated as lb/in.3 (kN/m3). This constant is defined as the modulus of subgrade reaction. In the 1930s, the structural behaviors of concrete pavement slabs were investigated at the Arlington Virginia Experimental Farm and at the Iowa State Engineering Experiment

Station. Good agreement occurred between experiential

stresses and those computed by the Westergaard’s theory, as

long as the slab remained continuously supported by the

subgrade. Corrections were required only for the Westergaard

corner formula to account for the effects of slab curling and

loss of contact with the subgrade. Although choosing the

modulus of subgrade reaction was essential for good agreement

with respect to stresses, there remained ambiguity in the

methods used to determine the correction coefficient.

In the 1930s, experimental information showed that the

behavior of many subgrades may be close to that of an elastic

and isotropic solid. Two characteristic constants—the

modulus of soil deformation and Poisson’s ratio—are typically

used to evaluate the deformation response of such solids.

Based on the concept of the subgrade as an elastic and

isotropic solid, and assuming that the slab is of infinite extent

but of finite thickness, Burmister proposed the layered-solid

theory of structural behavior for rigid pavements (Burmister

1943). He suggested basing the design on a criterion of

limited deformation under load. Design procedures for rigid

pavements based on this theory are not sufficiently developed

for use in engineering practice. The lack of analogous solutions

for slabs of finite extent, for example, edge and corner cases,

is a particular deficiency. Other approaches based on the

assumption of a thin elastic slab of infinite extent resting on

an elastic, isotropic solid have been developed. The

preceding theories are limited to behavior in the linear range

where deflections are proportional to applied loads. Lösberg

(Lösberg 1978; Pichumani 1973) later proposed a strength

theory based on the yield-line concept for ground-supported

slabs, but the use of ultimate strength for slab-on-ground

design is not common.

All existing design theories are grouped according to

models that simulate slab and the subgrade behavior. Three

models used for slab analysis are:

1. Elastic-isotropic solid;

2. Thin elastic slab; and

3. Thin elastic-plastic slab.

Two models used for subgrade are:

1. Elastic-isotropic solid; and

2. Winkler (1867).

The Winkler subgrade models the soil as linear springs so

that the reaction is proportional to the slab deflection.

Existing design theories are based on various combinations

of these models. The methods in this guide are generally

graphical, plotted from computer-generated solutions of

selected models. Design theories need not be limited to these

combinations. The elastic-isotropic model provides close

prediction for the response of real soils, but the Winkler

model is widely used for design and a number of investigators

have reported good agreement between observed responses

to the Winkler-based predictions.

1.4.3 Finite-element method—The classical differential

equation of a thin elastic plate resting on an elastic subgrade

is often used to represent the slab-on-ground. Solving the

governing equations by conventional methods is feasible for

simplified models where slab and subgrade are assumed to

be continuous and homogeneous. In reality, a slab-on-

ground usually contains discontinuities, such as joints and

cracks, and the subgrade support may not be uniform. Thus,

the use of this approach is limited.

The finite-element method can be used to analyze slabs-

on-ground, particularly those with discontinuities. Various

models have been proposed to represent the slab (Spears and

Panarese 1983; Pichumani 1973). Typically, these models

use combinations of elements, such as elastic blocks, rigid

blocks, and torsion bars, to represent the slab. The subgrade

is typically modeled by linear springs (Winkler subgrade)

placed under the nodal joints. Whereas the finite-element

method offers good potential for complex problems, graphical

solutions and simplified design equations have been tradi-

tionally used for design. The evolution of modern computer

software has made modeling with finite elements more

feasible in the design office setting.

1.5—Construction document information

Listed below is the minimum information that should be

addressed in the construction documents prepared by the

designer. Refer to ACI 302.1R for information related to the

installation and construction for some of these items.

• Slab-on-ground design criteria;

• Base and subbase materials, preparation requirements,

and vapor retarder/barrier, when required;

• Concrete thickness;

• Concrete compressive strength, or flexural strength,

or both;

• Concrete mixture proportion requirements, ultimate

dry shrinkage strain, or both;

• Joint locations and details;

• Reinforcement (type, size, and location), when required;

• Surface treatment, when required;

• Surface finish;

• Tolerances (base, subbase, slab thickness, and floor

flatness and levelness);

• Concrete curing;

• Joint filling material and installation;

• Special embedments;

• Testing requirements; and

• Preconstruction meeting, quality assurance, and quality

control.

1.5.1 Slab-on-ground design criteria—It is helpful that

when the slab-on-ground design criteria are well established,

that it be shown on the drawings. This information is especially

useful when future modifications are made to the slab or its

use. Design issues, such as the slab contributing to wind or

seismic resistance or building foundation uplift forces,

would not be readily apparent unless noted on the drawings.

Because it is not readily apparent when a slab is used as a

horizontal diaphragm, it should be noted on the drawings.

Removing or cutting a slab that is designed to resist uplift or

horizontal forces could seriously impair the building’s stability.

The design criteria should include some of the following:

• Geotechnical soil properties used for the different

loading types;

• Uniform storage loading;

• Lift-truck and vehicle loadings;

• Rack loadings;

• Line loads;

• Equipment loads;

• When the slab is used to resist wind or seismic foundation

uplift forces; and

• When the slab is used as a horizontal diaphragm and to

resist horizontal forces or both due to tilt-walls,

masonry walls, tops of retaining walls, and metal

building system columns.

Refer to Appendix 7 for an example of design criteria.

1.5.2 Floor flatness and levelness tolerances—Tolerances

for floor uses should conform to ACI 117. For additional

information, including how to specify floor flatness and

levelness requirements, refer to ACI 117 commentary and

ACI 302.1R.

When using slabs in offices, areas of pedestrian traffic,

wide aisle warehousing, and manufacturing, where the

movement is intended to be random in any direction, then a

random traffic tolerance system, such as FF/FL, should be

designated. The subject areas should be shown on the

construction documents and tolerances specified.

In defined traffic areas such as narrow aisle or very narrow

aisle warehousing and manufacturing, where vehicle paths

are restrained by rail, wire, laser, or telemetry guidance

systems, a tolerance system such as F-min should be imple-

mented (Fudala 2008), with subject areas shown on the

construction documents, and tolerances specified. Table 1.1

provides typical defined traffic values for different rack

heights that have been used successfully. Narrow aisle and

very narrow aisle systems, however, use specialized equipment

and the manufacturers should be consulted for F-min

recommendations.

Table 1.1—Defined traffic values

Rack height, ft (m)

Longitudinal* F-min Transverse† F-min

0 to 25 (0 to 7.6)

26 to 30 (7.9 to 9.1)

31 to 35 (9.4 to 10.7)

36 to 40 (11 to 12.2)

41 to 45 (12.5 to 13.7)

46 to 50 (14 to 15.2)

51 to 65 (15.5 to 19.8)

66 to 90 (20.1 to 27.4)

50

55

60

65

70

75

90

100

*Longitudinal value between the front and rear axle.

†Transverse value between loaded wheel tracks.

60

65

70

75

80

85

100

125

1.6—Further research

There are many areas that need additional research. Some

of these areas are:

• Developing concrete mixture proportions that have low

shrinkage characteristics and are workable, finishable,

and provide a serviceable surface;

• Flexural stress in slabs with curl and applied loads and

how curling stresses change over time due to creep;

• Base restraint due to shrinkage and other volume

changes and how this restraint changes over time;

• Crack widths for different amounts of reinforcement

for slabs-on-ground;

• Provide guidance on acceptable joint and crack widths

for different slab usages;

• Provide dowel recommendations based on loadings (lift

truck, rack post, and uniform storage) rather than slab

thickness;

• Provide plate dowel spacing recommendations for plate

dowel geometries;

• Provide design guidance for slabs with macrosynthetic

fibers;

• Provide design aids for slabs with rack uplift loads due

to seismic and other uplift loadings;

• Provide design aids for slabs with non-uniform rack

post loads;

• Develop a standardized method for testing and specifying

slab surface abrasion resistance;

• Soil properties and how they may change over time

under load repetitions, wide area long-term loadings, or

both; and

• Recommended joint spacing for fiber-reinforced concrete.

CHAPTER 2—DEFINITIONS

2.1—Definitions

ACI provides a comprehensive list of definitions through

an online resource. “ACI Concrete Terminology,” http://

terminology.concrete.org. Definitions provided herein

complement that resource.

curling or warping—out-of-plane deformation of the

corners, edges, and surface of a pavement, slab, or wall panel

from its original shape.

slab-on-ground––slab, supported by ground, whose main

purpose is to support the applied loads by bearing on the

ground.

CHAPTER 3—SLAB TYPES

3.1—Introduction

Chapter 3 identifies and briefly discusses the common

types of slab-on-ground construction. The term “slab-on-

ground” is preferred but “slab-on-grade” is often used. Slab-

on-ground includes interior slabs subject to loadings as

described in Chapter 5. These include industrial, commercial,

residential, and related applications. Although the term

might include parking lot and roadway pavements, this guide

does not specifically address them.

An important responsibility of the slab designer is to

discuss the requirements of the floor slab with the owner.

Discussions should include the advantages and disadvantages

of the different slab types and how they relate to the owner’s

requirements. It is important for this discussion to occur so

the owner has reasonable expectations of the slab perfor-

mance and required future maintenance for the slab type

selected. Some of the more important expectations that

should be discussed for the prospective slab type are:

• Cracking potential;

• Crack widths for slabs designed with reinforcement to

limit crack widths;

• Use of doweled joints versus aggregate interlock;

• Possible future repairs including joint deterioration;

• Joint maintenance requirements and the owner's

responsibility for this maintenance;

• Floor flatness and levelness requirements to meet the

owner’s needs;

• Changes to the flatness and levelness over time, especially

in low-humidity environments;

• Advantages and disadvantages of slab placement with

the watertight roofing system in place versus placing

the slab in the open;

• Level of moisture vapor resistance required; and

• Advantages and disadvantages of using the building

floor slab for tilt-wall construction form and temporary

bracing.

3.2—Slab types

There are four basic design choices for slab-on-ground

construction:

1. Unreinforced concrete slab.

2. Slabs reinforced to limit crack widths due to shrinkage

and temperature restraint and applied loads. These slabs

consist of:

a. Nonprestressed steel bar, wire reinforcement, or

fiber reinforcement, all with closely spaced joints; and

b. Continuously reinforced, free-of-sawcut, contraction

joints.

3. Slabs reinforced to prevent cracking due to shrinkage

and temperature restraint and applied loads. These slabs

consist of:

a. Shrinkage-compensating concrete; and

b. Post-tensioned.

4. Structural slabs designed in accordance with ACI 318:

a. Plain concrete; and

b. Reinforced concrete.

3.2.1 Unreinforced concrete slab—The thickness is

determined as

a

concrete slab without reinforcement;

however, it may have joints strengthened with steel dowels.

It is designed to remain uncracked between joints when

loaded and restraint to concrete volumetric changes.

Unreinforced concrete slabs do not contain macrosynthetic

fibers, wire reinforcement, steel fibers, plain or deformed

bars, post-tensioning, or any other type of steel reinforcement.

Type I or II portland cement (ASTM C150/C150M) is

normally used. Drying shrinkage effects and uniform

subgrade support on slab cracking are critical to the perfor-

mance of unreinforced concrete slabs. Refer to Chapter 7 for

unreinforced slab design methods.

3.2.2 Slabs reinforced for crack-width control—Thickness

design can be the same as for unreinforced concrete slabs,

and they are designed to remain uncracked when loaded. For

slabs constructed with portland cement, shrinkage crack

widths (when cracking occurs) between joints are controlled

by a nominal quantity of distributed reinforcement. Slabs

reinforcement can consist of bars, welded wire reinforcement

sheets, steel fibers, or macrosynthetic fibers. Bar and wire

reinforcement should be stiff enough to be accurately located

in the upper 1/3 of the slab.

Bars or welded wire reinforcement are used to provide

flexural strength at a cracked section. In this case, and for

slabs of insufficient thickness to carry the applied loads as an

unreinforced slab, the reinforcement required for flexural

strength should be sized by reinforced concrete theory as

described in ACI 318. Using the methods in ACI 318 with

high steel reinforcement stresses, however, may lead to

unacceptable crack widths. Building codes do not support

the use of fiber reinforcement to provide flexural strength in

cracked sections for vertical or lateral forces from other

portions of a structure.

Other than post-tensioning or the reinforcement in a

shrinkage-compensating slab, reinforcement does not

prevent concrete cracking. Typically, the most economical

way to increase flexural strength is to increase the slab thickness.

Chapters 7, 8, and 11 contain design methods for slabs

reinforced for crack-width control.

3.2.3 Slabs reinforced to prevent cracking—Post-

tensioned slabs and shrinkage-compensating slabs are typically

designed not to crack, but some incidental minor cracking

may occur. For shrinkage-compensating slabs, the slab is

designed unreinforced, and the reinforcement is designed to

prestress the expanding slab to offset the stresses caused by

the shrinkage and temperature restraint. For post-tensioned

slabs, the reinforcement is typically designed to compensate

for shrinkage and temperature restraint stress and applied loads.

Shrinkage-compensating concrete slabs are produced

either with a separate component admixture or with ASTM

C845 Type K expansive cement. This concrete does shrink,

but first expands to an amount intended to be slightly greater

than its drying shrinkage. To limit the initial slab expansion

and to prestress the concrete, reinforcement is distributed in

the upper 1/3 of the slab. Such reinforcement should be rigid

and positively positioned. The slab should be isolated from

fixed portions of the structure, such as columns and perimeter foundations, with a compressible material that allows the

initial slab expansion.

Refer to Chapters 9 and 10 for design methods for slabs

reinforced to prevent cracking.

3.2.4 Structural slabs—Structural plain and reinforced

slabs that transmit vertical loads or lateral forces from other

portions of the structure to the soil should be designed in

accordance with ACI 318. Using the methods in ACI 318

with high steel reinforcement stresses, however, may lead to

unacceptable crack widths.

3.3—General comparison of slab types

To assist with selecting the most appropriate slab type

for the particular project, Table 3.1 provides general

advantages and disadvantages for the slab types discussed

in Section 3.2.

3.4—Design and construction variables

Design and construction of slabs-on-ground involves both

technical and human factors. Technical factors include loadings,

soil-support systems, joint types and spacings, design method,

slab type, concrete mixture, development of maintenance

procedures, and the construction process. Human factors

include the workers’ abilities, feedback to evaluate the

construction process, and conformance with proper main-

tenance procedures for cracking, curling, and shrinkage.

These and other factors should be considered when

designing a slab (Westergaard 1926).

3.5—Conclusion

No single slab design method is recommended for all

applications. Rather, from the number of identifiable construc-

tion concepts and design methods, a combination should be

selected based on the requirements of the specific application.

CHAPTER 4—SOIL SUPPORT SYSTEMS FOR

SLABS-ON-GROUND

4.1—Introduction

The design of slabs-on-ground to resist moments and

shears caused by applied loads depends on the interaction

between the concrete slab and the supporting materials.

Properties and dimensions of the slab and the supporting

materials are important in the design of a slab-on-ground.

The support system should be of acceptable uniform strength

and not easily susceptible to the effects of climatic changes.

Slab-on-ground failures can occur because of an improper

support system. Issues related to the support system of the

slab-on-ground include:

• Geotechnical engineering reports providing soil properties;

• Subgrade classification;

• Modulus of subgrade reaction;

• Design of the slab support system;

• Site preparation; and

• Inspection and testing of the slab support system.

This chapter is limited to aspects of the support system

necessary for proper slab-on-ground performance.

The slab support system consists of a subgrade, usually a

base, and sometimes a subbase, as illustrated in Fig. 4.1.

Crushed rock, gravels, or coarse sands have high strength,

low compressibility, and high permeability, are commonly

used as base courses. Crushed rock, gravels, sands, select

soils, and stabilized soils are commonly used as subbases

and may be used as base materials. Soils in the subgrade are

generally the ultimate supporting materials, but bedrock,

competent or weathered, may also be encountered. When the

existing soil has uniform strength and other necessary prop-

erties to support the slab, the slab may be placed directly on

the existing subgrade. The existing grade, however, is

frequently not at the desired elevation or slope and some cut

and fill is required. To improve surface drainage or to elevate

the floor level, controlled fill using on-site or imported soils

is required on some sites.

4.2—Geotechnical engineering reports

4.2.1 Introduction—Geotechnical engineering investigations

supply subsurface site information primarily for design and

construction of the building foundation elements and to meet

building code requirements. Within the geotechnical

engineering report, slab-on-ground support is frequently

discussed, and subgrade drainage and preparation recommen-

dations are given. Even when slab support is not discussed in

detail, information given within these reports, such as boring

or test pit logs, field and laboratory test results, and discussions

of subsurface conditions, are useful in evaluating subgrade

conditions relative to slab-on-ground design and construction.

4.2.2 Boring or test pit logs—Descriptions given on boring

or test pit logs provide information on the texture of the soils

and their moisture condition and relative density, when

noncohesive; or consistency, when cohesive. These logs

present field test results, such as the standard penetration test

(ASTM D1586) in blows per 6 in. (150 mm) interval values.

The log notes the location of the water table at the time of

boring and depths to shallow bedrock. The Atterberg limits, and laboratory test results, such as the moisture content and

dry density of cohesive soils, are often included on the

boring logs or in the geotechnical report. Also, the soil is

classified as discussed in Section 4.3.

4.2.3 Report evaluations and recommendations—Evalua-

tions and recommendations relative to the existing subgrade

material, its compaction, and supporting capability can be

included in the report and should be evaluated against the

design requirements. The geotechnical engineer may

provide suggestions for subbase and base course materials.

In some cases, local materials that are peculiar to that area,

such as crushed sea shells, mine tailings, bottom ash, and

other waste products, can be economically used. The local

geotechnical engineer is generally knowledgeable about

using these materials in the project area. The expected

performance characteristics of the slab-on-ground should be

made known to the geotechnical engineer before the subsurface

investigation to obtain the best evaluation and recommendations.

For example, some of the information that should be

provided to the geotechnical engineer includes:

• Facility use and proposed floor elevation;

• Type and magnitude of anticipated loads;

• Environmental conditions of the building space;

• Floor levelness and flatness criteria; and

• Floor-covering requirements.

It may be beneficial for the geotechnical engineer to visit

local buildings or other facilities of the client that have

similar use. Coordination between the geotechnical engineer

and the slab-on-ground designer from the beginning of the

project can lead to an adequate and economical slabs-on-ground.

4.3—Subgrade classification

Soil supporting the slab-on-ground may meet the criteria

for a subbase or even a base material, but should be identified

and classified to estimate its suitability as a subgrade. The

Unified Soil Classification System is predominantly used in

the U.S. and is referred to in this guide. Table 4.1 provides

information on classification groups of this system and

important criteria for each soil group. Visual procedures

(ASTM D2488) can be used, but laboratory test results

(ASTM D2487) provide classifications that are more reliable.

For example, use the plasticity chart of Table 4.2 to classify

the fine-grained soils.

The following tests and test methods are useful for soil

classification:

• Moisture content: ASTM D2216;

• Specific gravity: ASTM D854;

• Liquid and plastic limits: ASTM D4318; and

• Expansion Index: ASTM D4829.

The standard Proctor compaction test (ASTM D698) and

modified Proctor compaction test (ASTM D1557) are not

strictly classification tests. Their moisture-density relationships

are useful in assessing a soil subgrade or subbase. A more

detailed listing of the ASTM standards appears in Chapter 15.

4.4—Modulus of subgrade reaction

4.4.1 Introduction—Design methods listed in Chapter 3,

including Westergaard’s pioneering work on rigid pavement

analysis (Westergaard 1923, 1926), employ the modulus of

subgrade reaction as a single property to represent the design

support strength. This modulus, also called the modulus of

soil reaction or Winkler foundation, is a spring constant that

assumes a linear response between load and deformation

from the subgrade.

Actually, there is no single k value for a subgrade because

the relationship between load and soil deformation is

nonlinear and is not a fundamental soil property. Figure 4.2

depicts a typical nonlinear relationship between a normal

compressive load and the resulting deformation for an area.

The type of soil structure, density, moisture content, and

prior loading determine the load-deformation relationship.

The relationship also depends on the width and shape of the

loaded area, depth of the subgrade, and position under the

slab. In addition, time may be a significant factor because

any deeper compressible soils may settle due to consolidation,

and near-surface soils may settle due to shrinkage from

alternate wetting and drying. Nevertheless, the procedures

for static nonrepetitive plate load tests outlined in ASTM

D1196 have been used to estimate the subgrade modulus.

4.4.2 Plate load field tests—Determining the modulus of

subgrade reaction on representative subgrade in place with a

30 in. (760 mm) diameter bearing plate, which is recommended

by ASTM D1196, is time-consuming and expensive. It takes

several days to plan and execute a load-testing program.

Large loads may be needed to obtain significant settlement

of the plates. Adjustments should be made for nonrecoverable

deformation and any plate deflections. Because the load-

deformation results are nonlinear, either an arbitrary load or

deformation should be assumed to calculate k (Fig. 4.2).

Several tests over the project area are required to obtain

representative k values, which generally result in a range of

k values. A correction is generally necessary to account for

future saturation of cohesive soil subgrades, and this requires sampling and laboratory tests. It is usually impractical to

conduct field tests on subgrade soils at their expected range

of densities and moisture contents. It is also impractical to

test the various possible types and thicknesses of base

courses and subbases on a representative subgrade. It is difficult

to test during adverse climatic conditions. Smaller plates,

such as 12 in. (300 mm) diameter, have been used, but the

diameter of the plate influences the results, and this is difficult

to take into account when reporting a k value.

Typically, these tests are made directly on an unconfined

natural or compacted subgrade or on a layer of compacted

subbase or base course over a subgrade. The physical character-

istics of the base course and subgrade material are necessary

to properly interpret the plate bearing test results. At a

minimum, data should include gradations, moisture

contents, densities, and Atterberg limit of the materials in the

supporting system. Before initiating a plate load field test, it

is advisable to consult a geotechnical engineer familiar with

site conditions to estimate price and time required and the

probable results.

4.4.3 American Association of State Highway Transportation

Officials (AASHTO) approach—For rigid pavements,

AASHTO developed a design procedure using the following

theoretical relationship between k values from plate bearing

tests and MR, the resilient modulus of the subgrade

k (lb/in.3) = MR (psi)/19.4 (in.-lb units)

k (kN/m3) = MR (kPa) × 2.03 (SI units)

The resilient modulus is a measure of the assumed elastic

property of soil considering its nonlinear characteristics. It is

defined as the ratio of the repeated axial deviator stress to the

recoverable axial strain and is widely recognized as a method

for characterizing pavement materials. The AASHTO Test

Method T 307 describes the methods for determining MR.

The value of MR can be evaluated using a correlation with

the older and more common California bearing ratio (CBR)

test value (ASTM D1883) by the following empirical rela-

tionship (Heukelom and Klomp 1962)

MR (psi) = 1500 × CBR (in.-lb units)

MR (kPa) = 10,342 × CBR (SI units)

This approximate relationship has been used extensively

for fine-grained soils having a soaked, saturated 96-hour

CBR value of 10 or less (Heukelom and Klomp 1962).

Correlations of MR with clay content, Atterberg limits, and

moisture content have also been developed.

The effective k value used for design, as recommended by

AASHTO for rigid pavements, depends on several different

factors besides the soil resilient modulus, including subbase

types and thicknesses, loss of support due to voids, and depth

to a rigid foundation. Tables and graphs in the “Guide for the

Design of Pavement Structures” (AASHTO 1993) may be

used to obtain an effective k for design of slabs-on-ground.

The k values obtained from measured CBR and MR data

using the AASHTO relationships can yield unrealistically

Fig. 4.2—Plate load-deformation diagram.

high values. It is recommended that the nomograph relation-

ships contained in Fig. 4.3 be used to validate the results of

correlated k values derived from AASHTO correlations.

4.4.4 Other approaches—The Corps of Engineers (COE)

developed empirical relations between soil classification type,

CBR, and k values, as illustrated by Fig. 4.3. These relationships

are usually quite conservative. All of these test methods and

procedures have been developed for pavements, not for slab-

on-ground floors for buildings. Nevertheless, correlations

such as these are widely used to approximate the subgrade

support values for slab-on-ground design and construction.

4.4.5 Influence of moisture content—The moisture content

of a fine-grained soil affects the modulus of subgrade reaction k

at the time of testing and throughout the slab service life.

Nearly all soils exhibit a decrease in k with an increase in

saturation, but the amount of reduction depends chiefly on

the texture of the soil, its density, and the activity of clay

minerals present. In general, the higher the moisture content,

the lower the supporting strength, but the relationship is

unique for each type of soil. The more uniform the moisture

content and dry density, the more uniform the support.

Therefore, good site surface drainage and drainage of the

subgrade is very important. Experience demonstrates that

high water tables and broken water or drain lines cause slab-

on-ground failures.

To evaluate the influence of moisture, test procedures

(such as CBR), unconfined compression, and triaxial shear

can be followed. Moisture and dry density ranges chosen for

testing should match those anticipated in the field. Laboratory

tests are more practical than field tests.

4.4.6 Influence of soil material on modulus of subgrade

reaction—Soils found at a building site are capable of

providing a range of subgrade support, as illustrated in Fig. 4.3.

Clay soils, such as CL and CH materials, provide the lowest

subgrade support. Well-graded, noncohesive soils, such as

SW and GW material, provide the greatest support. An

increase in density by compaction can improve a soil’s

strength, but to a limited extent. Using stabilization methods

will also have a limited range of effectiveness. Drainage

conditions can change the support strength of most soils, but this can be most significant for clays and silts. Frost action

can also reduce the support strength of soils containing silt.

Thus, the correlation between soil classification and supporting

strength is useful for estimating the range of capability, but

should be adjusted for expected site conditions.

4.4.7 Uniformity of support—The design charts of PCA,

WRI, and COE indicate the influence that the modulus of

subgrade reaction has on the required slab thickness. These

design aids assume continuous slab contact with the base and

a uniform subgrade modulus. Continuous intimate contact is

not achieved in practice because of differences in composition,

thickness, moisture content, slab curling, and subgrade

density. By following the joint recommendations in Fig. 6.6,

the curling stresses will be sufficiently low that the PCA,

WRI, and COE methods will provide reasonable solutions.

Cycles of load and climatic fluctuations of moisture may

increase or decrease k, but such change is usually not

uniform. Differences in subgrade support due to cuts and

fills or irregular depths to shallow bedrock are common.

Poor compaction control or variations in borrow material can

cause fills to provide nonuniform support. Attempts to

produce high subgrade moduli by compaction or stabilization

may yield nonuniform support unless strict quality-control

standards are implemented. Uniform high k values are difficult

to achieve. After slab installation, densification of noncohesive

soils, sand, and silts by vibration may yield nonuniform

support. The shrinking and swelling action of cohesive soils

(GC, SC, CL, and CH) causes cracks in concrete slabs, even

when design and construction precautions are taken. Lack of

uniform support can cause slab cracks. On some projects, a

well-constructed subgrade has been compromised by utility

trenches that were poorly backfilled. The importance of

providing uniform support cannot be overemphasized.

Inspection and testing of controlled fills should be mandatory.

4.4.8 Influence of size of loaded area—The k value, when

derived from the plate load test, only provides information

relative to the upper 30 to 60 in. (760 to 1520 mm) of the

subsurface profile. This may be sufficient for the analyses of

floor slabs subjected to relatively small concentrated loads,

but it is not sufficient for floor slabs subjected to large, heavy

loads. For example, a fully loaded warehouse bay measuring

25 x 25 ft (7.6 x 7.6 m) can load and consolidate soils 30 ft

(9.1 m) or more when fills were used to develop the site. Slab

settlement is not uncommon where fills were used to

produce dock height floors or promote area drainage. The

degree of settlement under such loading conditions typically

indicates an equivalent k value of only 20 to 30% of that

measured by a plate load test.

To properly consider the effect of heavy distributed loads

on slab performance, a more comprehensive evaluation of

subsurface conditions should be conducted. Such an evaluation

may include the performance of soil test borings, laboratory

tests of subgrade materials, or one of a variety of in-place

testing techniques. Such information can be used to develop

soil-support values that account for long-term consolidation

settlements under sustained heavy distributed loads.

4.4.9 Influence of time—Time of load application and

elapsed time are important. Short, transient loads such as lift

trucks, produce smaller deformations than sustained loads;

therefore, a higher k value can be used for rolling loads. With

the passage of time, the subgrade and subbase is subject to

load cycling. Applications of surface loads may increase the

stiffness of the subgrade and subbase, and a higher k value

will result. Unfortunately, this may also produce nonuniform

support because the areas of load application will not usually

be uniform.

Subgrade moisture change over time may also affect the

soil-support system. Stability through changes of climate,

such as protracted dry or wet weather conditions or cycles of

freezing and thawing, should be considered.

4.5—Design of slab-support system

4.5.1 General—After the subgrade soils have been classified,

the general range of their k values can be approximated from

Fig. 4.3. Adjustments may be made on the basis of local

experience, expected seasonal changes, and expected

construction conditions.

With this information, a decision can be made whether to

use the existing subgrade, improve it by compaction or stabi-

lization, use a subbase and a base course, or vary the thickness

of these layers. Initially, a wide range of subgrade conditions

may exist across the site. The soil-support system is rarely

uniform and some soil work is generally required to produce

a more uniform surface to support the slab. The extent of this

work, such as the degree of compaction or the addition of a base

course, is generally limited by economics. Selection of crushed

rock or soils in the well-graded gravel (GW) and poorly-graded

gravel (GP) groups may appear costly as a base material, but the

selection of these materials has distinct advantages. They

improve the modulus of subgrade reaction, produce more

uniform support, and provide an all-weather working surface to

speed construction during inclement weather.

4.5.2 Economics and simplified design—Designing a slab-

support system requires identification of the subgrade material

and the conditions to which it will be exposed. This knowledge

is essential to estimate the modulus of subgrade and the

potential volume change. With knowledge of soil classification

and some local experience, the engineer can select an

appropriate k value and design for the specific soil conditions.

The slab thickness calculation is insensitive to small changes

in k, therefore the exact k value need not be known. Significant

variations do not significantly change the design thickness.

For small projects, it may be advantageous to assume a

relatively low k factor and add an appropriate thickness of

subbase and base course material to enhance performance of

the slab rather than performing an expensive plate load test.

Basing design on assumed conditions increases the risk of

slab failure, but there are occasions when a simplified design

approach is justified. These decisions are a matter of

engineering judgment and economics.

4.5.3 Bearing support—Calculated bearing pressures under

loaded slabs-on-ground are typically significantly lower and are

not critical to typical designs as compared with the allowable

foundation contact pressures for building elements controlled

by ACI 318. Providing uniform support conditions is extremely

important for serviceable slab performance.

4.6—Site preparation

4.6.1 Introduction—Initially, the top layer of soil should

be stripped of all organic material, debris, and frozen material.

Normally, to produce a uniform support, strip and till the

surface, and recompact it before placing the subbase. Hard

and soft pockets of soil should be located by proof-rolling or

other means. Remove them and replace with compacted soil

to provide a uniform subgrade for the base, subbase, or concrete

slab. Refer to ACI 302.1R for additional information.

The site should be graded to provide good surface drainage

throughout the construction period and for the lifetime of the

structure. Groundwater may have to be intercepted and

routed around the site.

Combinations of base and subbase materials and thick-

nesses can be used to increase the subgrade strength. Carefully

examine sinkholes, expansive soils, highly compressible

materials, or other subgrade problems, as they can influence

slab performance.

4.6.2 Proof-rolling—As discussed in ACI 302.1R, proof-

rolling usually refers to driving a loaded vehicle in a grid

pattern over the subgrade in an effort to locate soft and

compressible areas at or near the surface. This should be a

part of the quality assurance process for the soil-support

system and should be documented in the project specifications.

The wheel load should be sized to avoid bearing failure, but

be large enough to stress at least the upper foot of subgrade.

Three cycles of the wheel load over the same track are

usually specified. These repeated applications may expose

weak areas by rutting or pumping behavior of the surface

soils. Rutting normally indicates excess moisture at the

surface. Pumping of the soils under the wheels of the loaded

vehicle indicates the subgrade soils are likely wet of the

optimum moisture and unable to achieve and maintain

compaction. Areas of poor support should be removed and

replaced with compacted material to provide a more uniform

subgrade. After repairs, proof-rolling can be repeated. There

are no standards for proof-rolling, and quantitative assessment

cannot be made from its use. Guidelines for proof-rolling are

given in ACI 302.1R. When a thick layer of dry and dense

material, such as a base or subbase course, exists over the

surface, or the subgrade surface has become hard due to

drying and construction traffic, proof-rolling may not detect

any soft or compressible areas under the surface. Some projects

employ proof-rolling three times after:

• Stripping (before any fill is placed);

• Installing the fill; and

• Placing the base course.

Locating suspected deeper soft areas or buried debris may

require borings, test pits, resistivity, or other procedures.

Proof-rolling should be scheduled so remedial work does not

interfere with the construction schedule.

4.6.3 Subgrade stabilization—A number of methods can

improve the performance of a soil subgrade. Generally, for

slabs-on-ground, the soil is densified by using compaction

equipment such as a sheepsfoot, rubber tire, or vibratory

rollers. Chemical stabilization may also be appropriate.

Weak subgrade material can be stabilized by adding

chemicals that combine with the soil, as shown in Table 4.3.

Generally, portland cement, lime, or fly ash is mixed into the

soil substrata with water and the mixture is recompacted.

Lime and fly ash are also used to lower the plasticity index

of subgrade and subbase materials. For silty soils, portland

cement may be effective. A geotechnical engineer should

plan, supervise, and analyze the soil conditions before chemical

stabilization is used.

Depending on the situation and soil conditions, certain

compactors are more effective than others. Generally, granular

soils are most responsive to vibratory equipment, and cohesive

soils respond best to sheepsfoot and rubber-tired rollers, but

there are exceptions. The depth of compacted lifts varies

with soil type and compaction equipment, but in most cases,

the depth of compacted lifts should be 6 to 9 in. (150 to 230 mm).

The dry density achieved after compaction is normally

measured and compared with maximum dry density values

obtained from laboratory compaction tests. Maximum dry

density and optimum moisture content values vary with

texture and plasticity. Refer to Fig. 4.4, which illustrates

standard Proctor tests (ASTM D698) on eight different soils.

Because the modified Proctor test (ASTM D1557) uses a

higher level of energy, the maximum dry density will be

higher and the optimum moisture content will be lower than

the standard Proctor test values. Furthermore, the difference

will vary with the texture and plasticity of the soil (Fig. 4.5).

Specifications frequently limit only the minimum field

density, such as 95% of the standard Proctor maximum

density or 90% of the modified Proctor maximum dry

density. To achieve a more uniform subgrade modulus, a

range of density should be specified. For example, 100 ± 5%

of the standard Proctor maximum density, or 95 ± 5% of the

modified Proctor maximum dry density. The range specified,

however, should be compatible with the soil type, soil

uniformity, contractor’s operation, and project needs.

Specifying a lower density range for clay soils having a

plasticity index of 20 or higher, for example, 92 ± 4% of the

standard Proctor maximum dry density is often used to

control volume changes. Frequently, moisture content within

± 3% of the optimum moisture content of the appropriate test

is also specified. Higher moisture contents, from optimum

moisture content to 4% above it, are frequently used to

minimize volume changes.

4.6.4 Subbase and base materials—For many slabs-on-

ground, the existing subgrade provides adequate support.

Generally, the materials listed in Fig. 4.3 that yield a standard

modulus of subgrade reaction above 100 lb/in.3 (27145 kN/

m3) can be used (Fig. 4.3). Highly compressible organic mate-

rials (OL) should be avoided, as well as high-plasticity clays

(CH), as they may cause heave or swell problems. Much of the

variation in support strength is the result of compaction and

moisture content; for example, the k value for lean clay (CL)

ranged from 70 to 250 lb/in.3 (19000 to 120000 kN/m3).

The subbase material has better qualities than the

subgrade, and may serve as a construction working surface

and part of the floor support system. The subbase is generally

omitted where the subgrades are of high quality. The use of

a subbase with a base course usually represents an economical

alternative for construction on a poor subgrade with an expensive base course material. The subbase may be

composed of:

• Stabilized subgrade soil;

• A fill of higher quality soil;

•Sand;

• Crushed rock;

• Reclaimed crushed concrete or asphalt pavement; or

• Local material with properties that satisfy project

requirements.

Base material should be a clean, densely-graded, granular

material with a balanced fine content. It should produce an

easily constructed, low-friction surface while minimizing

wicking of moisture from below. These densely-graded crushed

products are commonly referred to as “crusher-run” materials.

The following material sources have proven to be adequate:

1. The local Department of Transportation (DOT)

approved road base material with 100% passing the 1-1/2 in.

Fig. 4.5—Standard and modified Proctor curves.

(37.5 mm) sieve, 15% to 55% passing the No. 4 (4.75 mm)

sieve, and less than 12% passing the No. 200 sieve (75 μm).

2. Material satisfying the requirements of ASTM D1241,

Gradation “A,” “C,” or “D” (with the modified allowance of

less than 12% passing the No. 200 sieve [75 μm]).

Material passing the No. 200 sieve (75 μm) should be

clean, granular fill with less than 3% clay or friable particles.

These materials are easily compacted and have high

strengths and low compressibilities. When they have little or

no fines (material passing a 200 mesh [75 μm] sieve), they

are easily drained and act as a capillary break. Their effect on the slab support and the overall k value depends on the type

and thickness of the base material (Fig. 4.6). Data for specific

designs should be based on laboratory analysis and site-testing

results. When using an open-graded, crushed rock, the surface

may have to be filled in, “choked off” with sand or fine

gravels, and compacted to provide a smooth, planar surface to

reduce the restraint due to linear concrete shrinkage.

4.6.5 Stabilization of base and subbase—Base and subbase

materials are often densified by mechanical compaction to

improve the k value. Consider the relative price of alterna-

tives such as chemical stabilization of the subgrade, use of

high-quality base courses, or using a thicker slab.

Measure the mechanical compaction of clay and silt as a

percent of standard Proctor density (ASTM D698) or modified

Proctor density (ASTM D1557). Minimum dry densities

typically specified for these materials range from 90 to 95%

of the maximum dry densities of the standard and modified

tests, respectively.

4.6.6 Grading tolerance—Usually, compliance with the

initial rough and fine grading tolerance is based on a rod and

level survey using a grid pattern of no more than 20 ft (6.1 m).

Grading tolerances specified for a project should be consis-

tent with the recommendations of ACI 117. When a

minimum slab thickness has been specified, however, then

the slab designer will need to take exception to ACI 117 slab

and base tolerances requirements in the construction documents.

Specifying a minimum acceptable slab thickness significantly

increases the effort to minimize the base and slab tolerances.

It may also increase the concrete thickness overages needed

to ensure a slab minimum thickness.

4.6.7 Vapor retarder/barrier—All concrete is permeable

to some degree. Water and water vapor can move through

slabs-on-ground (Brewer 1965; Neville 1996). This can

adversely affect the storage of moisture-sensitive products

on the slab, humidity control within the building, and a

variety of flooring materials from coatings to carpets. For

storage facilities, anticipated stored goods, and methods of

storage should be discussed with the owner. Emitting vapor

can become trapped and condensed beneath products such as

cardboard stored in direct contact with the slab. Because this

moisture can damage stored products, the slab designer should

consider positive moisture protection such as a vapor retarder.

Products that are not stored in direct contact with the slab, but

are sensitive to moisture, may require humidity control. For

slabs to receive moisture-sensitive floor coverings, product

manufacturers specify a maximum moisture emission rate

from the slab surface, generally in the range of 3 to 5 lb/1000 ft2

(12 to 21 N/100 m2)/24 hours or a maximum relative

humidity, generally 75 to 80% at a depth of 40% of the slab

thickness. The use and the location of vapor retarders/barriers

require careful consideration. Figure 4.7 provides guidance.

Excess water in the slab not taken up by chemical action

evaporates through the slab top until reaching equilibrium

with ambient humidity. Additionally, moisture can transpire

from the subgrade and through the slab. When the base material

under the slab is saturated and subjected to a hydrostatic

head, as for a basement slab below a water table, liquid water

may flow through cracks or joints in the concrete. When

hydrostatic forces can occur, include them in the slab design

considerations. The amount of flow depends on the amount

of head and width, length, and spacing of the joints and

cracks in the concrete. When the base material is saturated or

near saturation and there is no head, moisture may transmit

into the slab by capillary action of the interconnected voids

in the concrete. Positive subgrade drainage is necessary

where water would otherwise reach the slab base. Further, an

open-graded stone is frequently used as a base course to form

a break against capillary rise of moisture in the subgrade.

Vapor retarders/barriers can substantially reduce vapor

transmission through slabs, but some water vapor will

transpire through the slab when the vapor pressure above the

slab is less than that below the slab.

Climate-control systems may lower the relative humidity

above the slab and result in water vapor movement through

the slab. The vapor pressure is a function of temperature and

relative humidity. The vapor drive is from high to low vapor

pressure. The temperature of the soil base is usually lower

than that of the space above the slab. The relative humidity

of the subgrade is typically 100%.

Water in the subgrade under slabs-on-ground can change

due to seasonal fluctuations of shallow water tables, capillary

rise in the subgrade soils, poor subsurface drainage, ponding

of storm water adjacent to the slab-on-ground, overwatering

plants and lawns adjacent to the slab-on-ground, or from

broken pipes in the subgrade. Because there are a variety of

moisture sources, there is likely a nonuniform distribution of

moisture beneath the slab-on-ground. Tests can be made to

try to ascertain the moisture problem before a covering is

placed. ASTM D4263 may detect moisture coming from the

slab but does not yield a rate of moisture movement. A quanti-

tative test method, ASTM F1869, uses a desiccant calcium

chloride beneath an impermeable dome over a small slab

area to calculate the moisture emission rate. These test

results may be misleading when the ambient air conditions

do not represent in-service conditions. ASTM F1869 requires an ambient air temperature of 75°F ± 10°F (24°C ± 6°C) and

a relative humidity of 50% ± 10% for 48 hours before and

during the test. This test measures moisture in the top 1/2 in.

(13 mm) of the slab, and cannot detect moisture below 3/4 in.

(19 mm). To better quantify moisture in slabs, ASTM F2170

was developed for the use of relative humidity probes.

Subgrade drainage and selecting subgrade materials have

a great influence on vapor retarders/barriers performance.

Protecting vapor retarders/barriers from damage during

construction can significantly influence their effectiveness.

Vapor retarders/barriers have been reported to affect the

concrete behavior in the slab by increasing finishing time,

promoting cracking, increasing slab curling, and reducing

strength. These problems, however, may be less costly than

performance failures related to excessive moisture transmission

through the slab.

4.7—Inspection and site testing of slab support

Inspection and testing are required to control the quality of

the subgrade and subbase construction and determine

conformance to project specifications. Before construction

begins, the subgrade soils and subbase or base-course

materials should be sampled, tested in the laboratory, and the

results evaluated.

In general, perform the following tests for soils and soil-

aggregate mixtures:

• Particle size (ASTM D422);

• Plasticity (ASTM D4318); and

• Laboratory compaction tests (ASTM D698 or D1557).

For cohesionless and free-draining soils and aggregates

gradation, perform the following:

• Maximum relative density (ASTM D4253);

• Minimum relative density (ASTM D4254); and

• Calculation of relative density.

After compaction, the in-place density can be determined

in the field by:

• Drive cylinder (ASTM D2937);

• Sand cone (ASTM D1556);

• Water balloon (ASTM D2167); and

• Nuclear densometer (ASTM D2922 and D3017).

The sand cone test is the most accepted method, but the

nondestructive nuclear density method is advantageous

because it takes minutes to conduct, the results are available

at the end of the field test, and it is widely used and accepted.

This allows field density and moisture contents to be used to

control construction. To check questionable results or to

confirm calibrations, however, the sand cone method is

generally specified. To check the nuclear gauge against the

sand cone and provide an adjustment factor, conduct a series

of calibration tests. Check the moisture readings against field

moisture tests (ASTM D566). Testing frequency is relative

to the uniformity of the materials used and the quality of

compaction required. Work that does not conform to the

project specifications should be corrected and retested. The

subgrade should be tested in advance of installing the

remainder of the slab-on-ground system. Minimum testing

requirements should be established for each project. These

should provide a reasonable test interval for each lift. These

tests are relatively inexpensive and easy to perform.

4.8—Special slab-on-ground support problems

Because of their low shear strength and high compressibility,

avoid placing slabs on topsoil. Project specifications generally

require stripping topsoil from the building site.

Expansive soils are defined as fine-grained soils, as shown

in Tables 4.1 and 4.2. Soils with a plasticity index of 15 or

higher may have a potential for volume change that should

be considered. A geotechnical engineer should examine the

soil data and recommend appropriate options. Potential

problems can be minimized by proper slab designs, stabi-

lizing the soil, and preventing moisture migration through

the slab. Failure to manage problems can, and often will,

result in slab failure.

Frost action may be critical to silts, clays, and some fine

sands. These soils can experience large volume changes and

consequently heave due to the growth of ice lenses during

freezing cycles and lose support due to saturation upon thawing.

Three conditions are present when this problem occurs:

1. Freezing temperature in the soil;

2. Water table close to the frost level providing water for

the formation of ice lenses; and

3. A soil that will transmit water from the water table into the

frost zone by capillary action.

Possible remedies include lowering the water table,

providing a barrier, or using a subbase or subgrade soil that

is not frost-susceptible. Properly designed insulation can be

beneficial. Volume changes due to frost action occur at

building perimeters, under freezer areas, and under ice-skating

rink floors (NCHRP 1974).

CHAPTER 5—LOADS

5.1—Introduction

Chapter 5 describes loadings, the variables that control load

effects, and provides guidance for factors of safety for concrete

slabs-on-ground. Concrete slabs are typically subjected to

some combinations of the following loads and effects:

• Vehicle wheel loads;

• Concentrated loads;

• Distributed loads;

• Line and strip loads;

• Unusual loads;

• Construction loads; and

• Environmental effects.

Slabs should be designed for the most critical combination of

these loadings, considering variables that produce the

maximum stress. Figure 5.1 presents the PCA guide for

selecting the most critical or controlling design considerations

for various loads (Packard 1976). Because a number of factors,

such as slab thickness, concrete strength, subgrade stiffness,

and loading are relevant, cases where several design consider-

ations that may control should be investigated thoroughly.

Other potential load conditions, such as loadings that

change during the life of the structure and those encountered

during construction (Wray 1986), should also be considered.

For example, material-handling systems today make

improved use of the building’s volume. Stacked pallets, once

considered uniform loads, may now be stored in narrow-

aisle pallet racks that produce concentrated loads. The envi-

ronmental exposure of the slab-on-ground is also a concern.

These effects include subgrade volume changes (shrink and

swell soils), buildings with equipment to reduce humidity,

and temperature changes. Thermal effects may be minimized

by constructing the slab after the building is enclosed, but

many slabs are placed before building enclosure. Therefore,

construction sequence is important in determining whether

transient environmental factors should be considered in the

design. Finally, thermal effects due to in-service conditions

should be considered.

5.2—Vehicular loads

Most vehicular traffic on industrial floors consists of lift

trucks and distribution trucks with payload capacities as high

as 70,000 lb (310 kN). The payload and much of a truck’s

weight are generally carried by the wheels of the loaded axle

for the standard (counterbalanced) lift truck. The Industrial

Truck Association (ITA) (1985) has compiled representative

load and geometry data for lift truck capacities up to 20,000 lb

(89 kN) (Table 5.1). Vehicle variables affecting the thickness

selection and design of slabs-on-ground include:

• Maximum axle load;

• Distance between loaded wheels;

• Tire contact area; and

• Load repetitions during service life.

The axle load, wheel spacing, and contact area are functions

of the lift truck or vehicle specifications. When vehicle

details are unknown or when the lift truck strength is

expected to change in the future, the values in Table 5.1 may

be used for design. The number of load repetitions, which

may be used to help establish a factor of safety, is a function

of the facility’s usage. Knowledge of load repetitions and

traffic patterns helps the designer to quantify fatigue.

Consider whether these values are predictable or constant

during the slab’s service life. Often, the slab is designed for

an unlimited number of repetitions.

The contact area between tire and slab is used in the analysis

for lift truck with pneumatic or composition tires (Wray

1986). The contact area of a single tire can be approximated

by dividing the tire load by the tire pressure (Packard 1976).

This calculation is somewhat conservative because the effect

of tension in the tire wall is not included. Assumed pressures

are variable; however, pneumatic non-steel-cord tire pressures

range from 85 to 100 psi (0.6 to 0.7 MPa), whereas steel-cord

tire pressures range from 90 to 120 psi (0.6 to 0.8 MPa). The

ITA found that the standard solid and cushion solid rubber

tires have floor contact areas based on internal pressures

between 180 and 250 psi (1.2 to 1.7 MPa) (Goodyear Tire

and Rubber Co. 1983). Polyurethane tire pressures

exceeding 1000 psi (6.9 MPa) have been measured.

Dual tires have an effective contact area greater than the

actual contact area of the two individual tires. Charts are

available to determine this effective contact area (Packard

1976). A conservative estimate of this effective contact area

can be made by using the contact area of the two tires and the

areas between the contact area. When it is not known

whether the vehicle has dual wheels or what the wheel

spacings are, then a single equivalent wheel load and contact

area can be used conservatively.

An important consideration for the serviceability of a slab

subject to vehicular loads is the design of construction and

sawcut contraction joints. Joints should be stiff enough and

have sufficient shear transferability to limit differential

movement such that the joint filler can perform properly and

resists edge spalling as a vehicle travels across the joint.

Refer to Chapter 6 for more information and joint details.

5.3—Concentrated loads

Warehousing improvements in efficiency and storage

densities have trended toward increased rack post loads.

These changes include narrower aisles, higher pallet or

material stacking, and using automated stacking equipment.

Pallet storage racks may be higher than 80 ft (24 m) and may

produce concentrated post loads of 40,000 lb (180 kN) or

more. For the higher rack loads, racks that cover a large plan

area (which affects deeper soil layers), and racks with long-

term loading, consider the effect of the long-term soil settlement

in the design of the slab. Cracking can also be caused by

early installation of rack systems that may restrain the slab’s

shrinkage and thermal movement and prevent joint activation.

The racks may restrain the slab with the rack system bracing or

by the increase in base friction from additional storage loads.

The concentrated load variables that affect slab-on-ground

design include:

• Maximum or representative post load;

• Duration of load;

• Spacings between posts and aisle width;

• Location of the concentrated load relative to slab joint

location and the amount of shear transfer across the

slab joint; and

• Area of contact between post base plate and slab.

Material-handling systems are major parts of the building

layout and should be well defined early in the project. Rack

data can be obtained from the manufacturer. It is not

uncommon to specify a larger base plate than is normally

supplied to reduce the flexural stress caused by the concen-

trated load. The base plate should be sized to distribute the

load nearly uniformly over the plate area.

5.4—Distributed loads

In many warehouse and industrial buildings, materials are

stored directly on the slab-on-ground. Flexural stresses in the

slab are usually less than those produced by concentrated

loads. The design should prevent negative moment cracks or

limit crack widths for the reinforced slabs in the aisles and

prevent excessive settlement. For higher load intensities,

distributed loads that cover a large plan area (which affect

deeper soil layers) and long-term uniform loads, consider the

effect of the differential soil settlement in the slab design.

The effect of a lift truck operating in aisles between

uniformly loaded areas is not normally combined with the

uniform load into one loading case, as the moments

produced generally offset one another. The individual cases

are always considered in the design.

For distributed loads, the variables affecting the design of

slabs-on-ground are:

• Maximum load intensity;

• Load duration;

• Width and length of loaded area;

• Aisle width; and

• Presence of a joint located in and parallel to an aisle.

Load intensity and layout may not be constant during the

service life of a slab. Therefore, the slab should be designed

for the most critical case. For a given modulus of subgrade

reaction and slab thickness, there is a critical aisle width that

maximizes the center aisle moment (Packard 1976).

5.5—Line and strip loads

A line or strip load is a uniform load distributed over a

relatively narrow area. Consider a load to be a line or strip

load when its width is less than 1/3 of the radius of relative

slab stiffness (Section 7.2). When the width approximates

this limit, review the slab for stresses produced by line loading

and uniform load. When the results are within 15% of one

another, consider the load as uniform. Partition loads, bearing

walls, and roll storage are examples of this load type. For

higher load intensities and long-term loading, consider the

effect of differential soil settlement in the design of the slab.

The variables for line and strip loads are similar to those

for distributed loadings and include:

• Maximum load intensity;

• Load duration;

• Width, length of loaded area, and when the line or strip

loads intersect;

• Aisle width;

• Presence of a joint in and parallel to an aisle;

• Presence of parallel joints on each side of an aisle; and

• The amount of shear transfer across the slab joint,

which is especially important when the line load crosses

perpendicular to a joint or is directly adjacent and

parallel to a joint.

5.6—Unusual loads

Loading conditions that do not conform to the previously

discussed load types may also occur. They may differ in the

following manner:

• Configuration of loaded area;

• Load distributed to more than one axle; and

• More than two or four wheels per axle.

The load variables are similar to those for the load types

previously discussed in Chapter 5.

5.7—Construction loads

During the building construction, various equipment types

may be located on the newly placed slab-on-ground. The

most common construction loads are:

• Pickup trucks;

• Scissor lifts;

• Concrete trucks;

• Dump trucks;

• Hoisting equipment and cranes used for steel erection;

• Tilt wall erection and bracing loads; and

• Setting equipment.

In addition, the slab may be subjected to loads such as

scaffolding and material pallets. Because these loads can

exceed design limits, anticipate the construction load case,

particularly relative to early-age concrete strength. Also,

consider limiting construction loads near the free edges or slab

corners. The controlling load variables for construction loads

are the same as for vehicle loads, concentrated loads, and

uniform loads.

For construction trucks, the maximum axle load and other

variables can usually be determined by referencing to local

transportation laws or AASHTO standards. Off-road

construction equipment may exceed these limits, but in most

cases, construction equipment will not exceed the local DOT

legal limits. For design, reference the values shown in Fig. 5.2.

Design codes are mostly silent on the subject of temporary

construction loads during erection (Subrizi et al. 2004). In

tilt-up construction, the slab-on-ground is often used as part

of the temporary construction bracing. The Tilt-Up Concrete

Association (TCA) has developed a temporary bracing

guideline (TCA 2005) that provides some guidance for the

slab’s design. When the slab designer considers these tilt-up

wall bracing loads during the initial design of the slab, then

often a more economical bracing solution is achieved for the

project (Kelly 2007). Kelly (2007) also provides some

solutions when the bracing loads are considered after the

slab has been constructed along with some design guidance

for the slab’s flexural strength.

5.8—Environmental factors

Overall slab design should consider flexural stresses

produced by thermal changes, reduction in humidity, expansive

soils, and moisture changes in the slab, which will affect

curling due to the different shrinkage rates between the top

and bottom of the slab. These effects are of particular impor-

tance for exterior slabs and for slabs constructed before the

building is enclosed. Curling caused by these changes

produces flexural stresses due to the slab lifting off the

subgrade. Generally, the restraint stresses can be ignored in

short slabs because a smooth, planar subgrade does not signifi-

cantly restrain the short slab movement due to uniform thermal

expansion, contraction, or drying shrinkage. When the joint

spacing recommendations given in Fig. 6.6 are followed, then

these stresses will be sufficiently low. Built-in restraints such

as foundation elements, edge walls, and pits should be

avoided. Reinforcement should be provided at such restraints

to limit slab crack widths. Chapter 14 discusses thermal and

moisture effects. Chapter 10 discusses expansive soils.

5.9—Factors of safety

Unique serviceability requirements distinguish slabs-on-

ground from other structural elements. Some of these

serviceability requirements can:

• Minimize cracking and curling;

• Increase surface durability;

• Optimize joint locations and joint types for joint stability,

which is the differential deflection of the adjacent slab

panels edges as wheel loads cross the joint; and

• Maximize long-term flatness and levelness.

Because building codes primarily provide guidance to

prevent catastrophic failures that affect public safety, the

factors of safety for serviceability, inherent in building codes,

are not directly addressed as are those for strength. When the

slab-on-ground is part of the structural system used to transmit

vertical loads or lateral forces from other portions of the

structure to the soil, such as a rack-supported roof, then

requirements of ACI 318 should be used for that load case.

The designer selects the factor of safety to minimize the

likelihood of serviceability failure. Some items the designer

should consider in selecting the factor of safety are:

• Consequences of serviceability failure, including lost

productivity, lost beneficial use, and the costs for

repairing areas in an active facility. For example, mini-

mizing cracking and limiting crack widths for facilities

such as pharmaceutical and food processing;

• Concrete mixture proportion and its shrinkage charac-

teristics (test and minimize shrinkage to reduce linear

drying shrinkage and curling);

• Humidity-controlled environment that increases linear

drying shrinkage and slab curling;

• Subgrade smoothness and planeness to minimize

restraint during linear drying shrinkage;

• Spacing and joint types;

• Geotechnical investigation to determine the shallow

and deep properties of the soil;

• Number of load repetitions and traffic patterns to allow

consideration of fatigue cracking;

• Impact effects;

• Storage racks installed at an early stage, which restrain

linear drying shrinkage; and

• Compounding factors of safety that may produce an

overly conservative design. Inclusion of cumulative

factors of safety in the modulus of subgrade reaction,

applied loads, compressive or flexural strength of the

concrete, or number of load repetitions, may produce a

very conservative and, consequently, expensive construc-

tion. The factor of safety is normally accounted for only

in the allowable flexural stress in the concrete slab.

Table 5.2 shows some commonly used factors of safety for

various types of slab loadings. Most range from 1.7 to 2.0,

but some loading conditions use factors as low as 1.4.

A moving vehicle subjects the slab-on-ground to the effect

of fatigue. Fatigue strength is expressed as the percentage of

the static tensile strength that can be supported for a given

number of load repetitions. As the ratio of the actual flexural

stress to the modulus of rupture decreases, the slab can

withstand more load repetitions before failure. For stress

ratios less than 0.45, concrete can be subjected to unlimited

load repetitions (PCA 2001). Table 5.3 shows various load

repetitions for a range of stress ratios. The factor of safety is

the inverse of the stress ratio.

CHAPTER 6—JOINTS

6.1—Introduction

Joints are used in slab-on-ground construction to limit the

frequency and width of random cracks caused by concrete

volume changes. Generally, when limiting the number of

joints or increasing the joint spacing can be accomplished

without increasing the number of random cracks, floor

maintenance will be reduced. The designer should provide

the layout of joints and joint details. When the joint layout

and joint details are not provided before project bid, the

designer should provide a detailed joint layout along with the

joint details before the slab preconstruction meeting or

commencing construction.

Every effort should be made to avoid connecting the slab

to any other element of the structure. Restraint from any

Allowable load

repetitions

832

630

477

361

274

207

157

119

90

68

52

39

30

22

17

13

10

7

6

4

3

2

2

1

1

1

1

0

0

source, whether internal or external, will increase the potential

for random cracking.

Three types of joints are commonly used in concrete slabs-

on-ground and are discussed in detail in this chapter:

1. Isolation joints.

2. Sawcut contraction joints.

3. Construction joints.

Refer to Fig. 6.1 for appropriate locations for isolation joints

and sawcut contraction joints. With the designer’s approval,

construction joint details and sawcut contraction joint details

can be interchanged. Joints in topping slabs should be located

directly over joints in the base slab and, when the topping is

bonded, no additional joints are required. The bonded topping

slab should be designed for the shrinkage restraint due to the

bond to the existing slab, and the bond should be sufficient to

resist the upward tension force due to curling. For a thin,

unreinforced, unbonded topping slab, consider additional

joints between the existing joints in the bottom slab to help

minimize the curling stress in the topping slab. The topping

slab can have high curling stresses due to the bottom slab

being a hard base for the topping slab. Also, any cracks in the

base slab that are not stable should be repaired to ensure they

will not reflect through into the topping slab.

6.1.1 Isolation joints—Isolation joints should be used

wherever complete freedom of vertical and horizontal

movement is required between the floor and adjoining

building elements. Isolation joints should be used at junctions

with walls (not requiring lateral restraint from the slab),

columns, equipment foundations, footings, or other points of

restraint such as drains, manholes, sumps, and stairways.

Isolation joints are formed by inserting preformed joint

filler between the floor and the adjacent element. Where the

isolation joint will restrain shrinkage, flexible closed cell

foam plank should be used with a thickness that accommodates

the anticipated shrinkage movement. The joint material

should extend the full depth or slightly below the bottom of

the slab to ensure complete separation and not protrude

above it. Where the joint filler will be objectionably visible,

or where there are wet conditions or hygienic or dust-

control requirements, the top of the preformed filler can be

removed and the joint caulked with an elastomeric sealant.

Listed as follows are three methods of producing a relatively

uniform joint sealant depth:

1. Use a saw to score both sides of the preformed filler at

the depth to be removed. Insert the scored filler in the proper

location. After the concrete hardens, use a screwdriver or

similar tool to remove the top section.

2. Cut a strip of wood equal to the desired depth of the joint

sealant. Nail the wood strip to the preformed filler and install

the assembly in the proper location. Remove the wood strip

after the concrete has hardened.

3. Use premolded joint filler with a removable top portion.

Refer to Fig. 6.2 and 6.3 for typical isolation joints around

columns. Figure 6.4 shows an isolation joint at an equipment

foundation. Refer to ACI 223 for guidance on isolation joints

for slabs using shrinkage-compensating concrete.

6.1.2 Construction joints—Construction joints are placed

in a slab to define the extent of the individual placements, generally in conformity with a predetermined joint layout.

When concreting is interrupted long enough for the placed

concrete to harden, the construction documents should

provide a detail to address this unplanned event. A contingency

plan for this unplanned event should also be discussed in the

slab preconstruction meeting. For specialty floors such as

defined traffic slabs, unplanned joints can have a significant

effect on the long-term floor flatness and levelness when not

detailed appropriately.

In areas not subjected to wheel traffic or when differential

curling movement is not a concern, a butt joint or keyed joint

may be adequate. In areas subjected to wheeled traffic, heavy

loads, or both, joints with load transfer devices are recom-

mended (Fig. 6.5). A keyed joint is not recommended for

load transfer in areas subjected to wheel traffic because the

male and female key components lose contact when the joint

opens due to drying shrinkage. This can eventually cause a

breakdown of the concrete joint edges and failure of the top

side portion of the key.

Construction joints are commonly formed using bulkheads.

These bulkheads should be placed to ensure specified

concrete slab thickness and elevation at the slab edge.

Provide the necessary support to keep the bulkheads straight,

true, and rigid during the entire placing and finishing operations.

When positive load transfer is required, provisions should be

made along the bulkhead to ensure proper alignment of the

load-transfer device during placing and finishing operations.

Proper alignment can be achieved by rigidly attaching

alignment devices to the bulkhead or by accurately slotting

or drilling the bulkhead to accept a load-transfer device.

These methods should allow the load-transfer device to be installed at the joint face while maintaining proper alignment

during placing and finishing operations. The load-transfer

devices should be parallel to the top surface, each other, and

perpendicular to the joint face. Depending on the method used,

the load-transfer device can be inserted before or after the bulk-

head is removed. When incorporating alignment or installation

devices into the bulkhead, which remain in the slab, the device

should be manufactured with a thin rigid material that is a tight

fit with the load-transfer device to minimize vertical deflection

due to load. Load-transfer devices in direct contact with the

concrete will be the most effective load-transfer mechanism for

controlling vertical joint deflection.

All construction joints should be internally vibrated at

frequent intervals to properly consolidate the concrete at the joint

and around the load-transfer devices. Vibratory screeds, laser-

guided screeds, and hand-rodding techniques do not provide

sufficient internal vibration around the load-transfer devices.

6.1.3 Sawcut contraction joints—Sawcut contraction joints

are used to limit random, out-of-joint floor slab cracking.

Joints are usually located on column lines, with intermediate

joints located at equal spaces between column lines (Fig. 6.1).  Consider the following when selecting spacing of sawcut

contraction joints:

• Slab design method;

• Slab thickness;

• Type, amount, and location of reinforcement;

• Shrinkage potential of the concrete, including cement

type and quantity; aggregate type, size, gradation,

quantity, and quality; water-cementitious material ratio;

type of admixtures; and concrete temperature;

• Base friction;

• Floor slab restraints;

• Layout of foundations, racks, pits, equipment pads,

trenches, and similar floor discontinuities; and

• Environmental factors such as temperature, wind, and

humidity.

Establishing slab joint spacing, thickness, and reinforcement

requirements is the responsibility of the designer. The specified joint spacing will be a principal factor dictating both the amount

and the character of random cracking to be experienced, so joint

spacing should always be carefully selected. For unreinforced

slabs-on-ground and for slabs reinforced only for limiting

crack widths, other than continuously reinforced with

more than 0.5% of steel by cross-sectional area, Fig. 6.6  provides recommendations for joint spacing. The spacings

are based on shrinkage values for specimens that have been

moist-cured 7 days and then placed in air storage per ASTM

C157/C157M. Use the appropriate prism size for the

concrete mixture being placed. The procedures in ACI 209R

can be used along with the ASTM C157/C157M test infor-

mation to predict the ultimate drying shrinkage. Using only

a few days of laboratory drying shrinkage data and the proce-

dures from ACI 209R to predict the ultimate drying shrinkage

may lead to unreliable values. Using 28-day laboratory

shrinkage values (7 days of curing and then 21 days of air

storage) and the procedures in ACI 209R to predict the ultimate

drying shrinkage, however, have provided useful results.

Sawcut contraction joints should be continuous across

intersecting joints, not staggered or offset. The aspect ratio

of slab panels that are unreinforced, reinforced only for

crack-width control, or made with shrinkage-compensating

concrete should be a maximum of 1.5 to 1; however, a ratio

of 1 to 1 is preferred. L- and T-shaped panels should be

avoided. Floors around loading docks have a tendency to

crack due to their configuration and restraints. Figure 6.7

shows two options that minimize slab cracking at reentrant

corners of loading docks. In Option 1, the loading dock pit

wall is placed integral with the slab and, therefore, most of

the shrinkage movement is forced to the construction joint

shown in the figure. To minimize the opening width of this

construction joint, place the joint at 1/2 of the typical slab joint

spacing. In Option 2, create a slip surface at the top of the pit

wall that will help equalize the shrinkage movement on each

side of the slab panel so the typical slab joint spacing can be

used. By using a construction joint as shown in Option 2, there

is less likelihood of cracking at the dock pit corners.

Plastic or metal inserts are not recommended for creating

a contraction joint in any exposed floor surface subject to

wheel traffic.

Contraction joints in industrial and commercial floors are

usually formed by sawing a continuous slot in the slab to

form a weakened plane so a crack will form below (Fig. 6.8).

When using load-transfer assemblies at sawcut contraction

joints, the concrete around these assemblies should be internally

vibrated. This properly consolidates the concrete around the

load-transfer assemblies. Section 6.3 provides further details

on sawcutting of joints.

6.2—Load-transfer mechanisms

Use load-transfer devices at construction and contraction

joints (Fig. 6.5) when positive load transfer is required,

unless a sufficient amount of post-tensioning force is

provided across the construction joint to transfer the shear.

Load-transfer devices force concrete on both sides of a joint

to deflect approximately equally when subjected to a load.

This can help prevent damage to an exposed edge when

subjecting the joint to wheel traffic.

For dowels to be effective, they should be smooth, aligned,

and supported so they remain parallel in both the horizontal

and vertical planes during the placing and finishing operation.

All dowels should have flat, square, and deburred end edges

that will not restrain concrete shrinkage. Properly aligned,

smooth dowels allow the joint to open freely as concrete

shrinks. ACI 117 provides tolerances for the installation of

slab-on-ground round dowels.

Plate dowels are now commonly used in construction and

contraction joints. Manufacturers offer various plate dowel

geometries and associated installation devices. Plate dowels

can minimize shrinkage restraint by using a tapered shape,

formed void, or by having compressible material on the

vertical faces with a thin bond breaker on the top and bottom

dowel surfaces (Fig. 6.9 and 6.10) (Schrader 1987, 1991;

PTI 2000; Ringo and Anderson 1992; Metzger 1996; Walker

and Holland 1998; American Concrete Paving Association

1992). When a formed void on the vertical sides is

constructed by a stay-in-place device, then that stay-in-place

device should be of a rigid material and fit tightly with the

dowel surface to minimize vertical deflection at the joint.

The tapered shape along with a thin bond breaker on all sides

allows a void space to develop along the vertical sides of the dowel to eliminate restraint as the slab shrinks from the joint.

Similarly, a formed void or the compressible material will

also eliminate the restraint as the slab shrinks from the joint.

Dowel baskets (Fig. 6.11 and 6.12) should be used to

maintain alignment of dowels in sawcut contraction joints,

and alignment installation devices should be used in

construction joints. Plate dowels in contraction joint basket

assemblies with the compressible material or tapered shape

allow for some horizontal misalignment with the sawcut

contraction joint. In corrosive environments, the designer

should consider corrosion protection for the dowels. Plate

and square dowel systems that minimize horizontal restraint

as shown in Fig. 6.9, 6.10, and 6.12 can be placed close to the

intersection of joints, but no closer than 6 in. (150 mm).

Other dowels should be placed no closer than 12 in. (300

mm) from the intersection of any joints because the maximum

movement caused by horizontal dry shrinkage occurs at this

point, and the corner of the slab may consequently crack.

Table 6.1 provides recommended dowel sizes and spacing

for round and square shapes. Because of the various plate

dowel geometries and installation devices available from the

different manufacturers, the manufacturers should be

consulted for their recommended plate dowel size and spacing.

A less effective load-transfer mechanism than those just

discussed is aggregate interlock. Aggregate interlock

depends on the irregular face of the cracked concrete at joints

for load transfer. Designers that choose aggregate interlock

as the load-transfer mechanism at joints are cautioned that,

for unreinforced concrete slabs, the joint spacings in Fig. 6.6

are intended to minimize the potential for midpanel out-of-

joint random cracking, and are independent of load transfer

requirements at joints. Not all joints activate uniformly. This

results in some joint opening widths that are larger than might

normally be anticipated (Walker and Holland 2007b). These

wide joints are often called the “dominant joints.” The domi-

nant joint behavior is made worse by the ever-increasing use

of vapor retarders/barriers placed below the floor slab, which

reduces base friction and makes the dominant joints more

noticeable and problematic. Where aggregate interlock is

anticipated as the only load-transfer mechanism in a slab-on-

ground, joint spacing should be the thoughtful result of an

evaluation of the anticipated, activated, joint-opening widths

and the type of wheel loadings on the slab. Furthermore,

when the designer cannot be sure of positive long-term shear

transfer at the joints through aggregate interlock, then positive  load-transfer devices should be used at all joints subject to

wheel traffic.

With respect to this issue, PCA implemented a test program

to examine the effectiveness of aggregate interlock as a load-

transfer mechanism (Colley and Humphrey 1967). The

program tested 7 and 9 in. (180 and 230 mm) thick slabs. The

test slabs were constructed using 1-1/2 in. (38 mm) maximum-

size aggregate, fully supported on various base materials, and

loaded using repetitive applications of 9000 lb (40 kN) on 16 in.

(440 mm) diameter pads centered 9 in. (230 mm) from the

joints. Among the findings were the following:

• Joint effectiveness for 7 in. (180 mm) thick slabs is

reduced to 60% at an opening width of 0.025 in. (0.6 mm);

• Joint effectiveness for 9 in. (230 mm) thick slabs is

reduced to 60% at an opening width of 0.035 in. (0.9 mm);

• Three values of foundation-bearing support were used.

The values used were k = 89, 145, and 452 lb/in.3

(24,200, 39,400, and 123,000 kN/m3). Joint effectiveness

was increased with increases in foundation bearing

value k; and

• Joint effectiveness increased with increased aggregate particle angularity.

Using the opening width of a joint or crack as an acceptance

criterion has been used with limited success in predicting its

service life. There are a number of difficulties in using the

opening width. These include:

• How to measure the width, because a crack edge may not have well-defined boundaries due to spalling or other factors;

• The crack width will change with temperature;

• The crack or joint opening width will vary along the length;

• The crack is wider at the top than at the bottom, due to curling; and

• The joint effectiveness relates to factors other than the

opening width. These include load magnitude, slab

thickness, soil support system stiffness, degree of

curling, aggregate size and angularity.

A more reliable and definable method to evaluate the

performance of a joint having a load-transfer mechanism, a

joint using aggregate interlock, or a crack that has developed, is

by measuring the joint or crack stability. The joint or crack

stability is the differential deflection of the adjacent slab

panel or crack edges when a service load crosses the joint or

crack. Joint or crack stability can be easily measured. It is

commonly done by using a leveled straightedge and gauge—

for example, a tri-square or dial indicator—to measure the

vertical distance from the upper straightedge to slab surface

at 12 in. (300 mm) spacing (6 in. [150 mm] each side of the

joint) to determine the amount of vertical movement under

the bottom of the straightedge as it occurs (Type I Apparatus,

ASTM E1155) or by using a device with an inclinometer

having 12 in. (300 mm) contact point spacing located 6 in.

[150 mm] on each side of the joint that gives a visual readout

of the vertical movement as it occurs (Type II Apparatus,

ASTM E1155). Joint or crack stability measurements below

0.010 in. (0.25 mm) for joints or cracks subjected to lift truck

wheel traffic with small hard wheels will have good service

life (Tarr 2004; Walker and Holland 2007a). For lift truck

traffic with large, cushioned rubber wheels, a joint or crack

stability measurement of 0.020 in. (0.51 mm) should have

good service life (Walker and Holland 1999, 2007a). These

joint stability values assume the joint is properly filled full

depth with semi-rigid joint filler and that the joint filler is

properly maintained. For joint or crack stability values above

0.060 in. (1.5 mm), the joint or crack would be considered

unstable (Tarr 2004), have a much reduced service life, and

most likely should be repaired.

Another load-transfer mechanism is enhanced aggregate

interlock. Enhanced aggregate interlock depends on a combina-

tion of the effect of a small amount of deformed reinforcement

continued through the joint and the irregular face of the cracked

concrete at joints for load transfer. The continuation of a small

percentage of deformed reinforcement (0.1% of the slab cross-

sectional area) through sawcut contraction joints in combination

with joint spacings (Fig. 6.6), has been used successfully by

some designers to provide load-transfer capability without

using dowels. A slab design that uses this small amount of

deformed reinforcement to enhance aggregate interlock at

the joints should conform to the following:

• Space joints as shown in Fig. 6.6;

• Place the reinforcement above mid-depth but low

enough that the sawcut will not cut the reinforcement;

• Place a construction or sawcut contraction joint with a

load-transfer device at a maximum of 125 ft (38 m).

This forces activation at these joints when the other

joints with the deformed reinforcement do not activate;

• Use an early-entry saw to cut all sawcut contraction

joints; and

• The slab should be a uniform thickness.

As a general rule, the continuation of larger percentages of

deformed reinforcing bars should not be used across sawcut

contraction joints or construction joints because they restrain

joints from opening as the slab shrinks during drying, and

this increases the probability of out-of-joint random

cracking. The restraint provided by the reinforcement varies

with the quantity of reinforcement in the slab, expressed as a

percentage of the cross-sectional area of the slab. Park and

Paulay (1975) offer a method of calculating the reduction in

unrestrained internal shrinkage strain that can be attributed

to the presence of reinforcement. Table 6.2 provides the

calculated reduction in strain that can be attributed to the

presence of various percentages of reinforcement located at

midheight of a slab using the following values:

Es

= modulus of elasticity of steel: 29,000,000 psi

(2,000,000 MPa);

Ec

Ct

= modulus of elasticity of concrete: 2,900,000 psi

(20,000 MPa);

= creep coefficient: 2.0; and

= unrestrained shrinkage strain: 0.000500.

This table suggests that the reduction in strain that could

be anticipated from 0.1% reinforcement at midheight of the

slab is less than 3%. This percentage is relatively minor

when compared with the potential impact of variations in the esh

restraint stresses due to the different coefficients of subgrade

friction (Fig. 14.3) and curling stresses.

Plate, square, and round smooth dowels for slab-on-

ground installation should meet the requirements of ASTM

A36/A36M or A615/A615M. The designer should specify

the diameter or cross-sectional area, length, shape, treatment

for corrosion resistance, and specific location of dowels, as

well as the method of installation, support, and debonding.

Refer to Table 6.1, Fig. 6.5, and Fig. 6.9 through 6.12.

For long post-tensioned floor strips and floors using

shrinkage-compensating concrete with long joint spacing,

take care to accommodate significant slab movements. In

most instances, post-tensioned slab joints are associated with

a jacking gap. Delay the filling of jacking gaps as long as

possible to accommodate shrinkage and creep. In traffic areas,

armor plating of the joint edges is recommended (Fig 6.13).

Figure 6.14 shows a doweled joint detail at a jacking gap in

a post-tensioned slab (PTI 1996, 2004).

6.3—Sawcut contraction joints

Three types of tools are commonly used for sawcutting

joints: conventional wet-cut (water-injection) saws;

conventional dry-cut saws; and early-entry dry-cut saws.

Timing of the sawing operations varies with manufacturer and

equipment. The goal of sawcutting is to create a weakened

plane as soon as the joint can be cut, preferably without

creating spalling at the joint, so the floor slab will crack at

the sawcut instead of randomly and create the desired

visual effect.

Conventional wet-cut saws are gasoline-powered. With

the appropriate blades, they are capable of cutting joints up

to 12 in. (300 mm) depth or more. Dry-cut tools can use

electrical or gasoline power. They provide the benefit of being

generally lighter than wet-cut equipment. Most early-entry dry-

cut saws cut to a maximum depth of 1-1/4 in. (32 mm), but

some cut to a maximum depth of 4 in. (100 mm). Timing of

the early-entry process allows joint sawcutting before

significant concrete tensile stresses develop. This increases

the probability of cracks forming at the joint when sufficient

concrete stresses develop. Care should be taken to ensure

that the early-entry saw does not ride up over hard or large

coarse aggregate. The highest coarse aggregate should be notched by the saw to ensure proper function of the sawcut

contraction joint.

Early-entry dry-cut saws use a skid plate that helps prevent

spalling. Timely changing of skid plates in accordance with

manufacturer’s recommendations is necessary to effectively

control spalling. Typically, joints produced using conven-

tional processes are made within 4 to 12 hours after the slab

has been finished in an area—4 hours in hot weather to 12 hours

in cold weather. For early-entry dry-cut saws, the waiting

period will typically vary from 1 hour in hot weather to 4 hours

in cold weather after completing the finishing of the slab in

that joint location. Longer waiting periods may be necessary

for all types of sawing for floors reinforced with steel fiber

or where embedded mineral-aggregate hardeners with long-

slivered particles are used. In all instances, sawing should be

completed before slab concrete cooling occurs subsequent to

the peak heat of hydration.

The minimum depth of sawcut using a wet conventional

saw should be the greater of at least 1/4 of the slab depth or

1 in. (25 mm). The minimum depth of sawcut using an early-

entry dry-cut saw should be 1 in. (25 mm) for slab depths up

to 9 in. (230 mm). This recommendation assumes that the

early-entry dry-cut saw is used within the time constraints

noted previously. Some slab designers require cutting the

slab the following day to 1/4 of the slab depth to deepen the

1 in. (25 mm) early-entry sawcut and ensure the joint activates.

Restricted joint activation using a 1 in. (25 mm) sawcut is a

particular concern with doweled joints because dowels may

restrain slab movement. For this situation, plate or square

dowels cushioned on the vertical sides by compressible

material or tapered plate dowels are available in dowel

basket assemblies and can reduce this restraint (Fig. 6.12).

For slabs containing steel fibers, the sawcut using a wet

conventional saw should be 1/3 of the slab depth. When

timely cutting is done with an early-entry saw, the depth can

be the same as for unreinforced (plain) concrete for lower

fiber concentrations and preferably 1-1/4 in. (32 mm)

minimum for higher fiber concentrations up to a 9 in. (230 mm)

thick slab. The sawing should be done shortly after the final set,

but timing of the sawing is critical so as not to pull up the

steel fiber. New, clean saw blades are recommended for crisp

sawcuts. Attempt a 5 ft (1.5 m) long cut and evaluate it for

spalling or raveling before cutting the entire slab section.

When fibers are pulled up, delay the sawing and repeat the

procedure until sawing reveals no fibers. Regardless of the

process chosen, sawcutting should be performed before

concrete starts to cool, as soon as the concrete surface is firm

enough not to permit dislodging or spalling of steel fibers

close to the floor surface to be torn or damaged by the blade,

and before random drying-shrinkage cracks can form in the

concrete slab. Shrinkage stresses build in the concrete as it

sets and cools. When sawing is unduly delayed, the concrete

can crack randomly before it is sawed. Additionally, delays

can generate cracks that run off from the saw blade toward the

edge of the slab at an obtuse or skewed angle to the sawcut.

6.4—Joint protection

Joints should be protected to ensure long-term perfor-

mance. Regardless of the materials chosen for protection, the

joint needs to have adequate load transfer and the surfaces of

adjacent slabs should remain in the same plane.

For wheel traffic, there are two ways to protect a joint: fill

the joint with a material to restore surface continuity or

armor the edges with steel plates (Fig. 6.13). Certain types of

semirigid epoxy or polyurea are the only materials known to

the committee that can fill joints and provide sufficient

shoulder support to the edges of the concrete and prevent

joint breakdown. Such joint materials should be 100% solids

and have a minimum Shore A hardness of 80 when measured

in accordance with ASTM D2240. Refer to Section 6.5 for

more details on joint filling and sealing.

For large slab placements where sawcut contraction joints

are not used and the joint width at the construction joints may

open significantly, such as post-tensioned slabs, steel-fiber

joint-free slabs, or slabs cast with shrinkage-compensating

concrete, it is recommended that the joints be protected with

back-to-back steel bars (Fig. 6.13 and 6.14). It is critical that

the top surfaces of the bars used to armor the joint are hori-

zontally level with the top of the slab. Milling may be

required to produce a flat surface when conventional bar

stock material is used. Angles have been used to armor

joints with limited success. Milling the top surface of the

angle to correct camber, sweep, and out-of-square is not

practical. Installing and maintaining the top angle leg hori-

zontal during concrete placing and finishing operations is

difficult while consolidating the concrete under the angle

leg bearing area. Steel-armored joints less than 3/8 in. (9 mm)

wide can be sealed with an elastomeric sealant as described

in ACI 504R.

Armored joints equal or greater than 3/8 in. (9 mm) wide

should be filled full depth with semi-rigid epoxy or polyurea

joint filler or joint filler that contains an integral sand

extender. This should provide a smooth transition for wheel

traffic and minimize damage to tire tread.

Unstable construction and sawcut contraction joints will

not retain any type of joint filler. Joints are unstable when

there is horizontal movement due to continued shrinkage or

temperature changes, or vertical movement due to inadequate

load transfer. Regardless of the integrity of initial construction,

the continued movement of a filled, curled, undoweled joint

under traffic may prematurely fatigue the filler and concrete

interface and cause failure. Joint edge protection provided by

supportive filler increases when load-transfer provisions are

incorporated in the joint design.

6.5—Joint filling and sealing

Where there are wet conditions, hygienic and dust control

requirements, and the slab is not exposed to wheel traffic,

contraction and construction joints can be filled with joint

filler or an elastomeric joint sealant. Joints exposed to wheel

traffic should be treated as discussed in Section 6.4.

Isolation or other joints are sometimes sealed with an

elastomeric sealant to minimize moisture, dirt, or debris

accumulation. Elastomeric sealants should not be used in

interior joints subjected to vehicular traffic unless protected

with steel armored edges. Refer to ACI 504R for more

information on elastomeric sealants.

6.5.1 Time of filling and sealing—Concrete slabs-on-ground

continue to shrink for years; most shrinkage takes place

within the first year. It is advisable to defer joint filling and

sealing as long as possible to minimize the effects of

shrinkage-related joint opening on the filler or sealant.

Ideally, when the building is equipped with an HVAC

system, it should be run for two weeks before joint filling.

This is especially important where using joint filler in traffic-

bearing joints because such materials have minimal

extensibility. When the joint is filled before most of the

shrinkage has occurred, expect separation between the joint

edge and the joint filler or within the joint filler itself. These

slight openings can subsequently be filled with a low-

viscosity compatible material.

When construction schedule dictates that joints be filled

early or when it is decided to fill the joints early to minimize

the damage to the joints due to construction traffic, then the

construction documents should have provisions to require

that the contractor return at a pre-established date, typically

between 6 months and 1 year, to repair the joint filler

separations using the same manufacturer’s product. Early

filling results in greater separation and requires more

substantial correction. This separation does not indicate a

failure of the filler or installation. The construction documents

should identify the parties responsible for this repair and

address payment requirements.

For cold-storage and freezer-room floors, joint fillers

specifically developed for cold temperature applications

should be installed only after the room has been held at its

planned operating temperature for at least 48 hours. For freezer rooms with operating temperatures below 0°F (–18°C),

the operating temperature should be maintained for 14 days

before starting filling joints.

There should be an understanding among all parties as to

when the joints will be filled and whether provisions should

be made for refilling the joints at a later time when additional

concrete shrinkage has taken place.

6.5.2 Installation—Elastomeric sealants should be

installed over a preformed joint filler, backer rod, or other

bond breaker as described in ACI 504R. Semirigid epoxy

and polyurea joint fillers should be installed full sawcut

depth to bottom of sawcut so that the sawcut ledge provides

support for the filler material. Joints should be suitably

cleaned to provide optimum contact between the filler or

sealant and bare concrete. Remove dirt, debris, saw cuttings,

curing compounds, and sealers. Vacuuming is recommended

rather than blowing the joint out with compressed air. Cured

epoxy and polyurea fillers should be flush with the floor

surface to protect the joint edges and recreate an interruption-

free floor surface. Installing the joint filler flush with the top

of the slab can best be achieved by overfilling the joint and

shaving the top of the filler level with the slab surface after

the material has hardened.

CHAPTER 7—DESIGN OF UNREINFORCED

CONCRETE SLABS

7.1—Introduction

The thickness of unreinforced concrete slabs is determined

using an allowable concrete flexural tensile stress. Although

the effects of any welded wire reinforcement, plain or

deformed bars, post tensioning, fibers, or any other type of

reinforcement are not considered, joints may be reinforced

for load transfer across the joint. Slabs are normally designed

to remain uncracked due to applied loads with a factor of

safety of 1.4 to 2.0 relative to the modulus of rupture.

It is important to note that, as set forth in ACI 318,

slabs-on-ground are not considered structural members

unless they are used to transmit vertical or horizontal loads

from other elements of the building’s structure (Chapter 12).

Consequently, cracking, joint instability, and surface character

problems are considered slab serviceability issues and not

relevant to the general integrity of the building structure.

Concrete floor slabs employing portland cement, regardless

of slump, will begin to experience a reduction in volume as

soon as they are placed. This continues as long as water,

heat, or both, are released into the surroundings. Because the

drying and cooling rates at the top and bottom of the slab are

dissimilar, the shrinkage will vary with the depth. This

distorts the as-cast shape and reduces volume. Resistance to

this distortion introduces internal concrete stresses that,

when unrelieved, may cause cracks.

Controlling the effects of drying shrinkage is critical to the

performance of unreinforced concrete slabs. Two principal

objectives of unreinforced slab-on-ground design are to

avoid the formation of random, out-of-joint cracks and to

maintain adequate joint stability. The slab’s anticipated live

loading governs its thickness and cross-joint shear transfer requirements, whereas shrinkage considerations dictate the

maximum joint spacing.

Current design and construction procedures are based

upon limiting cracking and curling, due to restrained

shrinkage, to acceptable levels, but not eliminating them.

ACI 302.1R suggests that cracking in up to 3% of the slab

panels in a normally jointed floor is a realistic expectation.

Refer to ACI 224R for further discussion of cracking in

reinforced and unreinforced concrete slabs.

In jointed, unreinforced slabs-on-ground, the design

intends to cause shrinkage cracks to occur beneath sawcut

contraction joints. In industrial construction, this can result

in a floor slab that is susceptible to relative movement of the

joint edges and joint maintenance problems when exposed to

wheel traffic. When the designer cannot be sure of positive

long-term shear transfer at the joints through aggregate

interlock, then positive load-transfer devices should be used

at all joints subject to wheel traffic. Refer to Section 6.2 for

additional information.

7.2—Thickness design methods

When the slab is loaded uniformly over its entire area and

supported by uniform subgrade, stresses will be due solely to

restrained volumetric changes; however, most slabs are

subjected to nonuniform loading. In warehouses, the necessity

for maintaining clear aisles for access to stored materials results

in alternating loaded and unloaded areas. Rack post and lift

truck wheel loads present a more complex loading pattern.

As noted in Chapter 1, the analysis of slabs supporting

concentrated loads is based largely on the work of Westergaard

(1923, 1925, 1926). Three separate cases, differentiated on the

basis of the location of the load with respect to the edge of

the slab, might be considered (Winter et al. 1964). These

cases are provided to illustrate the effect of load location,

particularly at free corners or edges. Most of the generally

used structural design methods discussed do not provide for

loading at free edges and corners. The designer should

carefully consider such loading.

Case 1: Wheel load close to corner of large slab—With a

load applied at the corner of a slab, the critical stress in the

concrete is tension at the top surface of the slab. An approx-

imate solution assumes a point load acting at the corner of

the slab (Fig. 7.1). At short distances from the corner, the

upward reaction of the soil has little effect, and the slab is

considered to act as a cantilever. At a distance x from the

corner, the bending moment is Px; it is assumed to be uniformly distributed across the slab section width at right

angles to the bisector of the corner angle. For a 90-degree

corner, the section width is 2x, and the bending moment per

unit width of slab is

Px

2x

P

2

------ = ---

When h is the thickness of the slab, the tensile stress at the

top surface is

ft == -------=----------

M

S

-----

P/2

h2/6

3P

h2

(7-1)

This equation provides reasonably close results only in the

immediate vicinity of the slab corner, and only when the load

is applied over a small contact area.

In an analysis that considers the reaction of the subgrade,

and that considers the load to be applied over a contact area

of radius a (Fig. 7.1), Westergaard derives the expression for

critical tension at the top of the slab, occurring at a distance

2

a1L from the corner of the slab

ft = -------1 – ----------

3P

h2

⎛⎞

⎝⎠

a 2

L

0.6

(7-2)

where ft is concrete tensile stress, psi (Pa); a is the radius of

load contact area, in. (m); P is the load on the slab-on-

ground, lb (N); h is the slab thickness, in. (m); and in which

L is the radius of relative stiffness [in. (m)], equal to

L = 4 ----------------------------

Eh3

12 1 ν2

(–)k

where E is elastic modulus of concrete, psi (Pa); ν is

Poisson’s ratio for concrete—approximately 0.15; and k is

modulus of subgrade reaction, lb/in.3 (N/m3).

The value of L reflects the relative stiffness of the slab and

the subgrade. It will be large for a stiff slab on a soft base,

and small for a flexible slab on a stiff base.

Case 2: Wheel load considerable distance from edges of

slab—When the load is applied some distance from the

edges of the slab at approximately four times the relative

stiffness (4L), the critical stress in the concrete will be in

tension at the bottom surface. This tension is greatest directly

under the center of the loaded area, and is given by the

expression

fb 0.316 P

h2-----

=

[log(h)3 41.6a2 h2

– log(–)–log(k) 6.48+

+ 0.675h

](7-4)

Case 3: Wheel load at edge of slab, but removed considerable

distance from corner—When the load is applied at a point

along an edge of the slab, the critical tensile stress is at the

bottom of the concrete, directly under the load, and is equal to

(7-3)

where

Mc

fb 0.572 P

h2-----

=

[log(h)3 41.6a2 h2

– log(–)–log(k) 5.77+

+ 0.675h

](7-5)

For Eq. (7-4) and (7-5), use P in pounds (lb), h in inches

(in.), and k in pounds per cubic inch (lb/in.3), then fb will be in

pounds per square inch (lb/in.2). The logarithms are base 10.

If the flexural tensile stress, as given by the previous

equations, exceeds the allowable concrete flexural tensile

stress, it is necessary to increase slab thickness, increase

concrete flexural strength, or provide reinforcement. Such

reinforcement is usually designed to provide for all the

tension indicated by the analysis of the assumed homogeneous,

elastic slab.

Case 4: Loads distributed over partial areas—In addition

to concentrated loads, uniform loads distributed over partial

areas of slabs may produce the critical design condition.

Again, in warehouses, heavy loads alternate with clear

aisles. With such a loading pattern, cracking is likely to

occur along the centerline of the aisles.

In an analysis based on such loading, Rice (1957) derived

an expression for the critical negative moment in the slab Mc

that occurs at the center of the aisle

Mc = []

w –λa

2λ2--------e

sin(λa)

(7-6)

= slab moment at the center of the aisle, in.-lb/in.

(m-N/m);

λ =, in.–1 (m–1);

E = elastic modulus of concrete, psi (Pa);

I

4 k 4EI⁄

= moment of inertia, in.4 (m4);

a

k

= half-aisle width, in. (m);

= modulus of subgrade reaction, lb/in.3 (N/m3);

w = uniform load, psi (N/m2); and

e

= base of natural logarithms.

Recognizing that the aisle width cannot always be

predicted exactly, Rice suggests that a “critical aisle width”

be used. This width is such as to maximize the above for

bending moment (Westergaard 1926).

Generally accepted thickness design methods for unre-

inforced slabs-on-ground are the:

• PCA method (Section 7.2.1);

• WRI method (Section 7.2.2); and

• COE method (Section 7.2.3).

Each of these methods, described in Chapter 1, seek to

avoid live load-induced cracks through the provision of

adequate slab cross section by using an adequate factor of

safety against rupture. The PCA and WRI methods only

address live loads imposed on the slab’s interior, whereas the

COE method only considers live loads imposed on the slab’s

edges or joints. All three methods assume that the slab

remains in full contact with the ground at all locations.

Curl-induced stresses are not considered. Design examples

in Appendixes l, 2, and 3 show how to use all three methods.

7.2.1 Portland Cement Association design method—The

PCA method is based on Pickett’s analysis (Ringo 1986).

The variables used are flexural strength, working stress,